## Costs
Emerging Technology Costs & Incremental Cost
Summary of Incremental Costs
Upgrade Type | Incremental cost per ton refrigeration ($) | Number of data points for cost calculation | Incremental cost per ton refrigeration (%) | Number of data points for percentage calculation
Distributed refrigeration system | 638.2979 | 1 | 15% | 1
Secondary loop system | 1496.2006 | 2 | 16.67% | 3
CO2 Cascade Systems | 1515.1515 | 1 | 10% | 2
CO2 Transcritical systems | 2232.1429 | 1 | 36.25% | 2
All upgrade technologies considered | 1470.4482 | 5 | 19.48% | 8
Emerging Technology Incremental Cost Data
Upgrade Type | Incremental Cost | Description |  | Notes | Source
CO2 transcritical | 50% - 55% | A 62 ton transcritial system at Hannaford supermarket in Turner, Maine. First in the U.S., and began operation in 2013. |  | 40% incremental cost for refrigeration equipment, an additional 10%-15% for the required piping and disply cases. | Case Study: Transcritical CO2 Supermarket Refrigeration Systems, DOE Better Buildings, 2015
Secondary loop | $147,000 (35%) | A 94 ton secondary loop system with R507 primary and propylene glycol and potassium formate secondary loop and evaporative condensers |  | Baseline central DX system used R22 or R404A with air-cooled condensers. Extra costs associated due to condenser type difference. Incremental cost includes both equipment and installation costs. Equipment: $70,000; Installation: $77,000 | Dev. And Demo. Of an Advanced Supermarket Refrigeration HVAC System
Secondary loop | 15% | R404A or R507 primary and propylene glycol or potassium formate secondary loop |  | Study states that maintenance cost for secondary system should be less | IEA Annex 26 Report
Secondary loop | 0% | A 23 ton secondary loop system with R717 (ammonia) primary and HFE-7100 secondary loop |  | Study considers total cost of system (cases, piping, refrigerant, brine, labor, compressor rack or chiller) | IEA Annex 26 Report
Distributed | $60,000 (15%) | A 94 ton distributed system with secondary loop and evaporative coolint tower for heat rejection. |  | Incremental cost includes both equipment and installation costs. Equipment: $53,000; Installation: $7,000 | Dev. And Demo. Of an Advanced Supermarket Refrigeration HVAC System
CO2 cascade | 10% | A 26 ton system with propane as high temperature refrigerant and CO2 as low temperature refrigerant |  | Cascade plant. Medium refrigeration load (30 kW freezing load; 60 kW cooling load) Propane (high temperature refrigerant). CO2 (low temperature level) | IEA Annex 26 Report
CO2 cascade | 10% | A 71 ton cascade system with R404A high temperature refrigerant and CO2 low temperature refrigerant |  | Incremental cost takes into account reduced refirgerant charge (R404A) compared to DX system. Includes Denmarks tax on Danish tax on R404A. | IEA Annex 26 Report
CO2 cascade | 50000 | A 33 ton system using R404A in the top side, and two CO2 loops serving refrigeration loads (CO2 DX, CO2 pump-recirculated) |  | System includes both CO2 direct expansion and a secondary recirculated loop of CO2. | PG&E Supermarket Refrigeration Codes and Standards Enhancement Initiative (2011)
Secondary loop | 150000 | A 105 ton system using R404A in top cycle (two separate medium and low temp top cycles), CO2 secondary pump-recirculated secondary loops used for loads. |  |  | PG&E Supermarket Refrigeration Codes and Standards Enhancement Initiative (2011)
CO2 transcritical | 250000 | A 112 ton transcritical CO2 system with dry gas cooler. |  | Incremental cost includes equipment and installation. | "Food Retail Panel Discussion" Ahold USA, Accelerate America July-Aug 2015 article
CO2 transcritical | 20% | A 364 ton transcritical CO2 system with 4 CO2 compressor racks. Each rack includes 3 low temperature compressors and 5 to 6 medium temperature compressors. |  | Incremental cost includes equipment only. | "In Love with CO2" Angelo Caputo's Fresh Market, Accelerate America June 2015 article
Note: All projects in the above table are new construction. The baseline for all projects is central DX, as shown in the "System Graphics" tab.

## Definitions and Features
Advanced Compressors for Commercial Refrigeration
Description of Each Emerging Technology Studied
Advanced Refrigeration Types | Definition of System |  | Baseline
Distributed refrigeration systems | Multiple parallel compressors installed in cabinets with small compressors are located in close proximity to the refrigerated loads. Cabinets are dedicated to a single load. Heat rejection is performed with an air-cooled condenser located on the roof or glycol loop and fluid cooler. Scroll compressors are typically used for this system type. Compared to central DX systems the refrigerant charge is reduced and suction temperatures closely match the evaporator temperature. |  | Central DX
CO2 transcritical systems | Systems use R-744 (CO2) directly as a refrigerant, often have multiple stages and operate at high pressures. These system require specialized equipment and high grade materials rated for the high pressures involved. This reduced the operations and maintenance costs involved with decreased component failures due to high quality components. Heat rejection occurs above the CO2 critical pressure with a gas cooler instead of a condenser. Cooling occurs below the critical pressure of CO2. The naturally high discharge pressures allow for greater heat reclaim options for space heat than standard centralized DX systems. |  | Central DX
Secondary loop systems | Two fluids are used in a secondary loop system; the primary fluid, typically a traditional HFC refrigerant, is used to cool the secondary fluid that is pumped to the loads to remove heat. |  | Central DX
CO2 cascade systems | Two refrigeration systems with a heat exchange serving as an evaporator for the top system and condenser for the lower system. R-744 (CO2) is used in the lower system a direct expansion refrigerant serving low temperature loads. |  | Central DX
Distributed Refrigeration Systems
Manufacturer | Product Name | Notes | Website
Hussmann | Protocol | Indoor distributed cabinets with 2-8 scroll compressors enclosed. Horizontal or vertical configurations available. | http://www.hussmann.com/en/Products/Refrigeration-Systems/Protocol/Pages/default.aspx
Hussmann | Protochill | Protocol distributed cabinets with integrated secondary loop for medium temperature applications. | http://www.hussmann.com/en/Products/Refrigeration-Systems/Protocol/Pages/default.aspx
Zero-Zone | Edge | Exterior and interior units, with scroll or reciprocating compressors. | http://www.zero-zone.com/commercial-refrigeration-systems.php?ID=81
Hillphoenix | ParaTemp | Exterior units for roof or behind store, includes a self-contained parallel condenser. | http://www.hillphoenix.com/refrigeration-systems/distributed-systems/paratemp/
Hillphoenix | AdaptaPac | Modular system for small footprint retail refrigeration and convenience stores. Each unit contains up to 3 bays with up to 4 scroll or hermetic reciprocating compressors per bay. | http://www.hillphoenix.com/refrigeration-systems/distributed-systems/adaptapac/
Hillphoenix | InviroPac | Indoor distributed cabinets. Up to 8 reciprocating or scroll compressors for horizontal configurations. Up to 4 reciprocating or scroll compressors for vertical configurations. | http://www.hillphoenix.com/refrigeration-systems/distributed-systems/inviropac/
Hillphoenix | WeatherPac | Larger external distributed system for larger stores, installed on roof above loads. Variety of compressor options. | http://www.hillphoenix.com/refrigeration-systems/distributed-systems/weatherpac/
CO2 Transcritical Systems
Manufacturer | Product Name | Notes | Website
Hussmann | Purity | Multiple CO2 compressor racks, various options including heat recovery, mechanical sub-cooling, and adiabatic gas coolers. | http://www.hussmann.com/en/Products/Refrigeration-Systems/Purity/Pages/default.aspx
Hillphoenix | Advansor | Parallel CO2 reciprocating compressor racks which can serve both medium and low temperature loads. System comes standard with electronic expansion valves standard. Heat recovery option available. | http://www.hillphoenix.com/refrigeration-systems/second-nature/
Hillphoenix | Advansor Flux | Packaged multiple compressor CO2 transcritical booster system. System is compact for use as a CO2 transcritical distributed system in large stores, or a central system in smaller stores. | http://www.hillphoenix.com/advansorflex-co2-booster-system/
Secondary Loop Systems
Manufacturer | Product Name | Notes | Website
Hussmann | TerraChill | Liquid CO2 secondary fluid, both medium and low temperature loads. | http://www.hussmann.com/en/Products/Refrigeration-Systems/Central-Secondary/Pages/default.aspx
Hussmann | Pump Station | Propylene glycol 30-35% mixture secondary fluid, medium temperature loads. | http://www.hussmann.com/en/Products/Refrigeration-Systems/Central-Secondary/Pages/default.aspx
Zero-Zone | Coldloop | Glycol or CO2 secondary fluid. | http://www.zero-zone.com/commercial-refrigeration-systems.php?ID=69
Hillphoenix | Second Nature Low-Temp CO2 (SNLT2) | Liquid CO2 secondary fluid, low temperature loads. | http://www.hillphoenix.com/refrigeration-systems/second-nature/
Hillphoenix | Second Nature Medium-Temp CO2 (SNMT2) | Liquid CO2 secondary fluid, medium temperature loads. | http://www.hillphoenix.com/refrigeration-systems/second-nature/
CO2 cascade systems
Manufacturer | Product Name | Notes | Website
Hillphoenix | SNLTX2 | Upper system is a traditional medium temperature DX; lower system is a low temperature CO2 subcritical DX system. | http://www.hillphoenix.com/refrigeration-systems/second-nature/
Zero-zone | Coldloop | Low temperature loads served by CO2 DX system; medium temperatures served by a CO2 secondary fluid loop; CO2 is cooled with an R-407A upper refrigeration system. | http://www.zero-zone.com/commercial-refrigeration-systems.php?ID=84

## Baseline costs
Baseline Costs
Baseline Cost Data
Equipment | System Size (tons) | Full Cost | Cost per Ton | Source | Notes
Centralized DX | 47.25 | 183195 | 3877.1429 | Efficiency Maine project report 1 | 1
Centralized DX | 15.6733 | 93578 | 5970.5232 | Efficiency Maine project report 2 | 1
Centralized DX | 27.4283 | 156000 | 5687.5494 | Efficiency Maine project report 3 | 1
Centralized DX | 24.6531 | 107957 | 4379.0466 | Efficiency Maine project report 4 | 1
Centralized DX | 39.85 | 157600 | 3954.8306 | Efficiency Maine project report 5 | 1
Centralized DX | 36.4667 | 160000 | 4387.5686 | Efficiency Maine project report 6 | 1
Centralized DX | 10.3667 | 92722 | 8944.2444 | Efficiency Maine project report 7 | 1
Centralized DX | 94 | 420000 | 4468.0851 | Estimated from Dev. And Demo. Of an Advanced Supermarket Refrigeration HVAC System Report | 2
Centralized DX | 94 | 400000 | 4255.3191 | Estimated from Dev. And Demo. Of an Advanced Supermarket Refrigeration HVAC System Report | 2
| Average baseline cost per ton |  | 5102.7011
Notes
1 | For new construction projects, centralized DX was installed in place of standalone condenser units.
2 | Estimated cost based on incremental cost information provided in study reviews

## System Graphics
System Graphics of Baseline and Emerging Technologies
Source: | IEA Annex 26: Advanced Supermarket Refrigeration/Heat Recovery Systems
Oak Ridge National Laboratory, 2003
Central DX "multiplex" system (considered the baseline for all emerging technolgies) |  | Distributed DX System | Secondary Loop System