## Current Product List- Dec 2017
DISCLAIMER- Some of the performance values reported as part of the Cold-Climate ASHP Specification are NOT derived from industry standard test procedures or third-party tested/verified (i.e. performance values at 5°F). Performance in some instances may be represented by manufacturer’s engineering data.
Products added to list since during current month
Products in grey are the ones not found in the AHRI database as of June 12, 2017.
General Information | [14 empty] | Condition 1 Performance - (47°F/70°F) | [9 empty] | Condition 2 Performance - (17°F/70°F) | [9 empty] | Condition 3 Performance - (5°F/70°F)* | [10 empty] | Pan Heater Data |  |  | OPTIONAL Condition 4 Performance - (X°F/70°F)*
[15 empty] | Capacity (btu/hr) |  |  | Input Power (kW) |  |  | COP |  |  |  | Capacity (btu/hr) |  |  | Input Power (kW) |  |  | COP |  |  |  | Capacity (btu/hr) |  |  | Input Power (kW) |  |  | COP | [8 empty] | Capacity (btu/hr) |  |  | Input Power (kW) |  | COP
Updated: December 11, 2017
Manufacturer | Brand (if applicable) | Model Name | AHRI Certificate No. | Outdoor Unit Model | Indoor Unit Model(s) | AHRI Type | HSPF (Region IV): | SEER | EER (@ 95°F) | Cooling Capacity (Btuh) | ENERGY STAR Certified | Ductless or Centrally Ducted | If Ductless, Multi-zone or Single-zone? | Ductless Indoor Type | Minimum Capacity 47°F | Rated Capacity 47°F | Maximum Capacity 47°F | Input Power at Min. Capcaity 47°F | Rated Input Power 47°F | Input Power at Max. Capacity 47°F | COP at Min. Capacity 47°F | COP at Rated Capacity 47°F | COP at Max. Capacity 47°F |  | Minimum Capacity 17°F | Rated Capacity 17°F | Maximum Capacity 17°F | Input Power at Min. Capacity 17°F | Input Power at Rated Capacity 17°F | Input Power at Max. Capacity 17°F | COP at Min. Capacity 17°F | COP at Rated Capacity 17°F | COP at Max. Capacity 17°F |  | Minimum Capacity 5°F |  | Maximum Capacity 5°F | Input Power at Min. Capacity 5°F |  | Input Power at Max. Capacity 5°F | COP at Min. Capacity 5°F |  | COP at Max. Capacity 5°F | Maintenance Capacity (Max 5°F/Max 47°F) | Maintenance Capacity (Max 5°F/Max 17°F) | Integrated or Accessory (provide model #) | Input Power (W) | What determines when heater operates? | Outdoor Dry Bulb (°F) | Minimum Capactity X°F |  | Maximum Capacity X°F | Input Power at Min. Capacity X°F | Input Power at Max. Capacity X°F | COP at Min. Capacity X°F | COP at Max. Capacity X°F | Condition 2 minus Condition 3
Amana Heating and air Conditioning | Amana | AVZC20 | 10324704 | AVZC200241A* | CA*F3642*6D*+MBVC1200**-1A*+TX | HRCU-A-CB | 10 | 21 | 13 | 23400 | Yes | Centrally Ducted | N/A | N/A | 5507 | 23600 | 23600 | 0.328 | 1.87 | 1.87 | 4.9206 | 3.6987 | 3.6987 |  | 3943 | 13915 | 15200 | 0.338 | 1.487 | 1.82 | 3.4189 | 2.7425 | 2.4476 |  | 1650 |  | 11400 | 0.296 |  | 1.6 | 1.63 |  | 2.09 | 48.31% | 75% | N/A |  |  | N/A | [7 empty] | 3800
Amana Heating and air Conditioning | Amana | AVZC20 | 10324705 | AVZC200361A* | CA*F3743*6D*+MBVC1600**-1A*+TX | HRCU-A-CB | 10 | 21 | 14 | 35400 | Yes | Centrally Ducted | N/A | N/A | 13438 | 35000 | 35000 | 0.721 | 2.48 | 2.48 | 5.46 | 4.14 | 4.14 |  | 8580 | 18365 | 28800 | 0.722 | 2.092 | 3.72 | 3.48 | 2.57 | 2.27 |  | 5135 |  | 22100 | 0.722 |  | 3.48 | 2.08 |  | 1.86 | 63.14% | 76.74% | N/A |  |  | N/A | [7 empty] | 6700
Amana Heating and air Conditioning | Amana | AVZC20 | 10324706 | AVZC200481A* | CA*F4961*6D*+MBVC2000**-1A*+TX | HRCU-A-CB | 10 | 20 | 13 | 46500 | Yes | Centrally Ducted | N/A | N/A | 13274 | 45500 | 45500 | 0.796 | 3.42 | 3.42 | 4.8872 | 3.899 | 3.899 |  | 8394 | 28254 | 34000 | 0.766 | 2.926 | 4.15 | 3.21 | 2.83 | 2.4 |  | 5390 |  | 26000 | 0.722 |  | 3.87 | 2.19 |  | 1.97 | 57.14% | 76.47% | N/A |  |  | N/A | [7 empty] | 8000
Amana Heating and air Conditioning | Amana | AVZC20 | 10324707 | AVZC200601A* | CA*F4961*6D*+MBVC2000**-1A*+TX | HRCU-A-CB | 10 | 20 | 12.5 | 52500 | Yes | Centrally Ducted | N/A | N/A | 15848 | 50000 | 50000 | 0.891 | 3.76 | 3.76 | 5.2128 | 3.8972 | 3.8972 |  | 9302 | 32293 | 34000 | 0.92 | 3.466 | 4.07 | 2.96 | 2.73 | 2.45 |  | 5407 |  | 26000 | 0.901 |  | 3.85 | 1.76 |  | 1.98 | 52% | 76.47% | N/A |  |  | N/A | [7 empty] | 8000
American Standard | American Standard | AccuComfort Platinum 20 | 6749789 | 4A6V0024A1 | *AM8C0B30V21 | HRCU-A-CB | 10 | 19.25 | 13.75 | 24200 | Yes | Centrally Ducted | N/A | N/A | 7800 | 20200 | 21900 | 0.5 | 1.64 | 1.56 | 4.58 | 3.61 | 4.12 |  | 11430 | 16800 | 16800 | 1.18 | 1.97 | 1.91 | 2.84 | 2.5 | 2.58 |  | 11176 |  | 13000 | 1.58 |  | 1.84 | 2.08 |  | 2.08 | 59.36% | 77.38% | N/A |  |  | N/A | [7 empty] | 3800
American Standard | American Standard | AccuComfort Platinum 20 | 6749791 | 4A6V0048A1 | *AM8C0C48V41 | HRCU-A-CB | 10 | 19.25 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 11800 | 42500 | 42600 | 0.74 | 4.15 | 3.65 | 4.68 | 3 | 3.42 |  | 21530 | 34000 | 34400 | 2.61 | 4.74 | 4.66 | 2.42 | 2.1 | 2.16 |  | 22446 |  | 26720 | 3.72 |  | 4.44 | 1.76 |  | 1.76 | 62.72% | 77.67% | N/A |  |  | N/A |  | z | [5 empty] | 7680
American Standard | American Standard | AccuComfort Platinum 18 | 6750232 | 4A6V8036A1 | *AM8C0C36V31 | HRCU-A-CB | 10 | 18 | 13 | 35000 | Yes | Centrally Ducted | N/A | N/A | 8200 | 32200 | 32200 | 0.47 | 3.04 | 2.6 | 5.12 | 3.1 | 3.62 |  | 15710 | 25200 | 25400 | 1.85 | 3.36 | 3.33 | 2.48 | 2.2 | 2.24 |  | 16488 |  | 19680 | 2.66 |  | 3.18 | 1.82 |  | 1.82 | 61.12% | 77.48% | N/A |  |  | N/A |  | z | [5 empty] | 5720
American Standard | American Standard | AccuComfort Platinum 18 | 6750233 | 4A6V8048A1 | *AM8C0C48V41 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 11800 | 41000 | 43000 | 0.74 | 3.88 | 3.64 | 4.68 | 3.1 | 3.46 |  | 21860 | 34400 | 34800 | 2.57 | 4.58 | 4.61 | 2.5 | 2.2 | 2.22 |  | 22792 |  | 27080 | 3.66 |  | 4.38 | 1.82 |  | 1.82 | 62.98% | 77.82% | N/A |  |  | N/A |  | z | [5 empty] | 7720
American Standard | American Standard | AccuComfort Platinum 18 | 6750455 | 4A6V8024A1 | *AM8C0B30V21 | HRCU-A-CB | 10 | 18 | 13 | 23800 | Yes | Centrally Ducted | N/A | N/A | 7800 | 20000 | 21900 | 0.5 | 1.63 | 1.56 | 4.58 | 3.6 | 4.12 |  | 11430 | 16800 | 16800 | 1.18 | 1.97 | 1.91 | 2.84 | 2.5 | 2.58 |  | 11176 |  | 13000 | 1.58 |  | 1.84 | 2.08 |  | 2.08 | 59.36% | 77.38% | N/A |  |  | N/A |  | z | [5 empty] | 3800
American Standard | American Standard | AccuComfort Platinum 18 | 6750457 | 4A6V8049A1 | *AM8C0C48V41 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 11800 | 41500 | 42600 | 0.74 | 4.05 | 3.65 | 4.68 | 3 | 3.42 |  | 21530 | 34000 | 34400 | 2.61 | 4.74 | 4.66 | 2.42 | 2.1 | 2.16 |  | 22446 |  | 26720 | 3.72 |  | 4.44 | 1.76 |  | 1.76 | 62.72% | 77.67% | N/A |  |  | N/A |  | z | [5 empty] | 7680
American Standard | American Standard | AccuComfort Platinum 20 | 6796524 | 4A6V0036A1 | *UD2C080ACV4 4TXCC007CC3 | HRCU-A-CB | 10 | 20 | 13 | 34600 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32000 | 33100 | 0.49 | 2.93 | 2.57 | 4.96 | 3.2 | 3.78 |  | 15710 | 25800 | 25900 | 1.88 | 3.44 | 3.35 | 2.44 | 2.2 | 2.26 |  | 16488 |  | 19800 | 2.7 |  | 3.22 | 1.78 |  | 1.8 | 59.82% | 76.45% | N/A |  |  | N/A |  | z | [5 empty] | 6100
American Standard | American Standard | AccuComfort Platinum 20 | 6796526 | 4A6V0036A1 | *UD2C100ACV5 4TXCC007CC3 | HRCU-A-CB | 10 | 20 | 13 | 34800 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 33100 | 0.49 | 2.91 | 2.59 | 4.96 | 3.2 | 3.74 |  | 15710 | 25600 | 25900 | 1.88 | 3.41 | 3.35 | 2.44 | 2.2 | 2.26 |  | 16588 |  | 19900 | 2.7 |  | 3.2 | 1.8 |  | 1.82 | 60.12% | 76.83% | N/A |  |  | N/A |  | z | [5 empty] | 6000
American Standard | American Standard | AccuComfort Platinum 20 | 6796528 | 4A6V0036A1 | *UD2C080ACV4 4TXFH036CZ3 | HRCU-A-CB | 10 | 20 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8100 | 31200 | 32400 | 0.5 | 2.86 | 2.51 | 4.74 | 3.2 | 3.78 |  | 15710 | 25600 | 25700 | 1.86 | 3.41 | 3.28 | 2.48 | 2.2 | 2.3 |  | 16628 |  | 19900 | 2.66 |  | 3.16 | 1.84 |  | 1.84 | 61.42% | 77.43% | N/A |  |  | N/A |  | z | [5 empty] | 5800
American Standard | American Standard | AccuComfort Platinum 18 | 6796559 | 4A6V8037A1 | *AM8C0B30V21 | HRCU-A-CB | 10 | 18 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32600 | 33900 | 0.5 | 2.81 | 2.55 | 4.92 | 3.4 | 3.9 |  | 15930 | 26200 | 26400 | 1.85 | 3.34 | 3.3 | 2.52 | 2.3 | 2.34 |  | 16688 |  | 20160 | 2.66 |  | 3.16 | 1.84 |  | 1.86 | 59.47% | 76.36% | N/A |  |  | N/A |  | z | [5 empty] | 6240
American Standard | American Standard | AccuComfort Platinum 18 | 6796560 | 4A6V8037A1 | *UD2B080ACV3 4TXCB004CC3 | HRCU-A-CB | 10 | 18 | 12.5 | 34800 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32000 | 33300 | 0.5 | 3.02 | 2.68 | 4.86 | 3.1 | 3.64 |  | 16040 | 25800 | 26100 | 1.95 | 3.44 | 3.46 | 2.42 | 2.2 | 2.22 |  | 16934 |  | 20240 | 2.8 |  | 3.32 | 1.78 |  | 1.78 | 60.78% | 77.55% | N/A |  |  | N/A |  | z | [5 empty] | 5860
American Standard | American Standard | AccuComfort Platinum 18 | 6796562 | 4A6V8037A1 | *UD2C080ACV4 4TXCC007CC3 | HRCU-A-CB | 10 | 18 | 13 | 34600 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32000 | 33100 | 0.49 | 2.93 | 2.57 | 4.96 | 3.2 | 3.78 |  | 15710 | 25800 | 25900 | 1.88 | 3.44 | 3.36 | 2.44 | 2.2 | 2.26 |  | 16488 |  | 19800 | 2.7 |  | 3.22 | 1.78 |  | 1.8 | 59.82% | 76.45% | N/A |  |  | N/A |  | z | [5 empty] | 6100
American Standard | American Standard | AccuComfort Platinum 18 | 6796563 | 4A6V8037A1 | *UD2C100ACV5 4TXCC007CC3 | HRCU-A-CB | 10 | 18 | 13 | 34800 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 33100 | 0.49 | 2.91 | 2.6 | 4.96 | 3.2 | 3.74 |  | 15710 | 25600 | 25900 | 1.88 | 3.41 | 3.35 | 2.44 | 2.2 | 2.26 |  | 16588 |  | 19900 | 2.7 |  | 3.2 | 1.8 |  | 1.82 | 60.12% | 76.83% | N/A |  |  | N/A |  | z | [5 empty] | 6000
American Standard | American Standard | AccuComfort Platinum 18 | 6796565 | 4A6V8037A1 | *UD2C080ACV4 4TXFH036CZ3 | HRCU-A-CB | 10 | 18 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8100 | 31200 | 32400 | 0.5 | 2.86 | 2.52 | 4.74 | 3.2 | 3.76 |  | 15710 | 25600 | 25700 | 1.86 | 3.41 | 3.28 | 2.48 | 2.2 | 2.3 |  | 16628 |  | 19900 | 2.66 |  | 3.16 | 1.84 |  | 1.84 | 61.42% | 77.43% | N/A |  |  | N/A |  | z | [5 empty] | 5800
American Standard | American Standard | AccuComfort Platinum 20 | 6992577 | 4A6V0036A1 | *AM8C0B30V21 | HRCU-A-CB | 10 | 20 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32600 | 33900 | 0.5 | 2.81 | 2.55 | 4.92 | 3.4 | 3.9 |  | 15930 | 26200 | 26400 | 1.85 | 3.34 | 3.3 | 2.52 | 2.3 | 2.34 |  | 16688 |  | 20160 | 2.64 |  | 3.16 | 1.86 |  | 1.86 | 59.47% | 76.36% | N/A |  |  | N/A |  | z | [5 empty] | 6240
American Standard | American Standard | AccuComfort Platinum 18 | 7035709 | 4A6V8036A1 | *DD2C100ACV5 4NXCC005AS3 | HRCU-A-CB | 10 | 18 | 12.5 | 35800 | Yes | Centrally Ducted | N/A | N/A | 8400 | 31600 | 32600 | 0.5 | 2.99 | 2.54 | 4.92 | 3.1 | 3.76 |  | 16040 | 26200 | 26300 | 1.89 | 3.49 | 3.42 | 2.48 | 2.2 | 2.26 |  | 16828 |  | 20200 | 2.7 |  | 3.26 | 1.82 |  | 1.82 | 61.96% | 76.81% | N/A |  |  | N/A |  | z | [5 empty] | 6100
American Standard | American Standard | AccuComfort Platinum 20 | 7125570 | 4A6V0036A1 | *UHMB060ACV3 4TXCB004CC3 | HRCU-A-CB | 10 | 18.5 | 12.5 | 34800 | Yes | Centrally Ducted | N/A | N/A | 8500 | 31000 | 33500 | 0.55 | 2.93 | 2.73 | 4.52 | 3.1 | 3.6 |  | 16150 | 26000 | 26300 | 1.98 | 3.46 | 3.51 | 2.38 | 2.2 | 2.2 |  | 16934 |  | 20300 | 2.82 |  | 3.36 | 1.76 |  | 1.78 | 60.6% | 77.19% | N/A |  |  | N/A |  | z | [5 empty] | 6000
American Standard | American Standard | AccuComfort Platinum 20 | 7125571 | 4A6V0036A1 | *UHMB060ACV3 4TXFH036CZ3 | HRCU-A-CB | 10 | 18.75 | 12.5 | 34800 | Yes | Centrally Ducted | N/A | N/A | 8300 | 30400 | 32700 | 0.56 | 2.87 | 2.68 | 4.34 | 3.1 | 3.58 |  | 15930 | 25600 | 25900 | 1.96 | 3.41 | 3.45 | 2.38 | 2.2 | 2.2 |  | 16788 |  | 20040 | 2.78 |  | 3.32 | 1.76 |  | 1.76 | 61.28% | 77.37% | N/A |  |  | N/A |  | z | [5 empty] | 5860
American Standard | American Standard | AccuComfort Platinum 20 | 7125572 | 4A6V0036A1 | *DHMB060BCV3 4TXFH036CZ3 | HRCU-A-CB | 10 | 19.5 | 12.5 | 34800 | Yes | Centrally Ducted | N/A | N/A | 8300 | 30800 | 33200 | 0.52 | 2.82 | 2.65 | 4.68 | 3.2 | 3.68 |  | 16150 | 25800 | 26100 | 1.94 | 3.44 | 3.41 | 2.44 | 2.2 | 2.24 |  | 17034 |  | 20340 | 2.78 |  | 3.28 | 1.8 |  | 1.82 | 61.27% | 77.93% | N/A |  |  | N/A |  | z | [5 empty] | 5760
American Standard | American Standard | AccuComfort Platinum 18 | 7125581 | 4A6V8037A1 | *DHMB060BCV3 4TXFH036CZ3 | HRCU-A-CB | 10 | 18 | 12.5 | 34800 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 33200 | 0.52 | 2.91 | 2.66 | 4.68 | 3.2 | 3.66 |  | 16150 | 25800 | 26100 | 1.95 | 3.44 | 3.41 | 2.42 | 2.2 | 2.24 |  | 17034 |  | 20340 | 2.78 |  | 3.28 | 1.8 |  | 1.82 | 61.27% | 77.93% | N/A |  |  | N/A |  | z | [5 empty] | 5760
American Standard | American Standard | AccuComfort Platinum 20 | 7161151 | 4A6V0048A1 | *AM8C0C60V51 | HRCU-A-CB | 10 | 19.25 | 12.5 | 46500 | Yes | Centrally Ducted | N/A | N/A | 11800 | 43000 | 43100 | 0.74 | 3.94 | 3.53 | 4.68 | 3.2 | 3.58 |  | 21640 | 34200 | 34700 | 2.56 | 4.55 | 4.54 | 2.48 | 2.2 | 2.24 |  | 22486 |  | 26780 | 3.64 |  | 4.34 | 1.8 |  | 1.8 | 62.13% | 77.18% | N/A |  |  | N/A |  | z | [5 empty] | 7920
American Standard | American Standard | AccuComfort Platinum 20 | 7599436 | 4A6V0036A1 | *AM8C0C48V41 | HRCU-A-CB | 10 | 20.75 | 13.5 | 36000 | Yes | Centrally Ducted | N/A | N/A | 8400 | 33800 | 32800 | 0.5 | 2.83 | 2.38 | 4.92 | 3.5 | 4.04 |  | 15820 | 25400 | 25700 | 1.78 | 3.1 | 3.12 | 2.6 | 2.4 | 2.42 |  | 16548 |  | 19800 | 2.54 |  | 3 | 1.9 |  | 1.94 | 60.37% | 77.04% | N/A |  |  | N/A |  | z | [5 empty] | 5900
American Standard | American Standard | AccuComfort Platinum 20 | 8759144 | 4A6V0036A1 | *UD2C080ACV4 & 4PXCCU48BS3 | HRCU-A-CB | 10 | 21 | 13 | 36800 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33200 | 33300 | 0.52 | 2.42 | 2.41 | 4.78 | 4.0196 | 4.04 |  | 15930 | 26600 | 26700 | 1.84 | 2.42 | 3.24 | 2.54 | 3.2205 | 2.42 |  | 16688 |  | 20220 | 2.62 |  | 3.1 | 1.86 |  | 1.90 | 60.72% | 75.73% | N/A |  |  | N/A | [7 empty] | 6480
American Standard | American Standard | AccuComfort Platinum 20 | 8759145 | 4A6V0036A1 | *UD2C100ACV5 & 4PXCCU48BS3 | HRCU-A-CB | 10 | 21 | 13 | 37000 | Yes | Centrally Ducted | N/A | N/A | 8400 | 33200 | 33300 | 0.51 | 2.44 | 2.37 | 4.82 | 3.9867 | 4.12 |  | 15710 | 26600 | 26600 | 1.81 | 2.44 | 3.2 | 2.54 | 3.1942 | 2.44 |  | 16488 |  | 20080 | 2.58 |  | 3.06 | 1.88 |  | 1.90 | 60.3% | 75.49% | N/A |  |  | N/A | [7 empty] | 6520
American Standard | American Standard | AccuComfort Platinum 18 | 8759184 | 4A6V8036A1 | *UD2C100ACV5 & 4PXCCU36BS3 | HRCU-A-CB | 10 | 18 | 12.5 | 35000 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 32100 | 0.5 | 2.34 | 2.46 | 4.86 | 3.9818 | 3.82 |  | 16040 | 26000 | 26200 | 1.83 | 2.34 | 3.29 | 2.56 | 3.2555 | 2.34 |  | 16934 |  | 20300 | 2.6 |  | 3.14 | 1.90 |  | 1.90 | 63.24% | 77.48% | N/A |  |  | N/A | [7 empty] | 5900
American Standard | American Standard | AccuComfort Platinum 18 | 8759191 | 4A6V8036A1 | *UD2C100ACV5 & 4PXCCU48BS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36200 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32600 | 32800 | 0.51 | 2.44 | 2.35 | 4.82 | 3.9146 | 4.08 |  | 16040 | 26200 | 26400 | 1.79 | 2.44 | 3.17 | 2.62 | 3.1461 | 2.44 |  | 16894 |  | 20300 | 2.56 |  | 3.04 | 1.94 |  | 1.95 | 61.89% | 76.89% | N/A |  |  | N/A | [7 empty] | 6100
American Standard | American Standard | AccuComfort Platinum 18 | 8759192 | 4A6V8036A1 | *UD2B100ACV3 & 4PXCCU60BS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36600 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32400 | 32500 | 0.5 | 2.4 | 2.39 | 4.86 | 3.9555 | 3.98 |  | 16480 | 26400 | 26500 | 1.83 | 2.4 | 3.23 | 2.64 | 3.223 | 2.4 |  | 17440 |  | 20740 | 2.62 |  | 3.1 | 1.96 |  | 1.95 | 63.82% | 78.26% | N/A |  |  | N/A | [7 empty] | 5760
American Standard | American Standard | AccuComfort Platinum 18 | 8759235 | 4A6V8048A1 | *UD2D120ACV5 & 4PXCDU60BS3 | HRCU-A-CB | 10 | 18 | 12.5 | 48000 | Yes | Centrally Ducted | N/A | N/A | 12300 | 44000 | 44600 | 0.78 | 2.4 | 3.4 | 4.62 | 5.3716 | 3.84 |  | 23510 | 37000 | 37400 | 2.56 | 2.4 | 4.56 | 2.7 | 4.517 | 2.4 |  | 24696 |  | 29340 | 3.62 |  | 4.34 | 2.00 |  | 2.00 | 65.78% | 78.45% | N/A |  |  | N/A | [7 empty] | 8060
American Standard | American Standard | AccuComfort Platinum 18 | 8761163 | 4A6V8036A1 | *UD2B080ACV3 & 4TXCB006DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36200 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32800 | 33000 | 0.51 | 2.4 | 2.42 | 4.82 | 4.0043 | 4 |  | 16590 | 26600 | 26800 | 1.87 | 2.4 | 3.28 | 2.6 | 3.2474 | 2.4 |  | 17540 |  | 20900 | 2.66 |  | 3.16 | 1.94 |  | 1.95 | 63.33% | 77.99% | N/A |  |  | N/A | [7 empty] | 5900
American Standard | American Standard | AccuComfort Platinum 18 | 8761164 | 4A6V8036A1 | *UD2B060ACV3 & 4TXCB006DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36000 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32800 | 33000 | 0.52 | 2.4 | 2.43 | 4.74 | 4.0043 | 3.98 |  | 16590 | 26600 | 26800 | 1.86 | 2.4 | 3.28 | 2.62 | 3.2474 | 2.4 |  | 17540 |  | 20900 | 2.66 |  | 3.16 | 1.94 |  | 1.95 | 63.33% | 77.99% | N/A |  |  | N/A | [7 empty] | 5900
American Standard | American Standard | AccuComfort Platinum 18 | 8761165 | 4A6V8036A1 | *UD2C080ACV4 & 4TXCC005DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 35200 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32000 | 32200 | 0.51 | 2.34 | 2.46 | 4.82 | 4.0068 | 3.84 |  | 16150 | 26200 | 26300 | 1.83 | 2.34 | 3.3 | 2.58 | 3.2806 | 2.34 |  | 17094 |  | 20400 | 2.62 |  | 3.14 | 1.92 |  | 1.90 | 63.35% | 77.57% | N/A |  |  | N/A | [7 empty] | 5900
American Standard | American Standard | AccuComfort Platinum 18 | 8761167 | 4A6V8036A1 | *UD2C100ACV5 & 4TXCC005DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 35000 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 32100 | 0.5 | 2.34 | 2.46 | 4.86 | 3.9818 | 3.82 |  | 16040 | 26000 | 26200 | 1.83 | 2.34 | 3.29 | 2.56 | 3.2555 | 2.34 |  | 16934 |  | 20300 | 2.6 |  | 3.14 | 1.90 |  | 1.90 | 63.24% | 77.48% | N/A |  |  | N/A | [7 empty] | 5900
American Standard | American Standard | AccuComfort Platinum 18 | 8761170 | 4A6V8036A1 | *UD2B100ACV3 & 4TXCC007DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36200 | Yes | Centrally Ducted | N/A | N/A | 8400 | 33000 | 33000 | 0.51 | 2.42 | 2.42 | 4.82 | 3.9954 | 4 |  | 16590 | 26800 | 26900 | 1.86 | 2.42 | 3.27 | 2.62 | 3.2448 | 2.42 |  | 17640 |  | 21000 | 2.66 |  | 3.16 | 1.94 |  | 1.95 | 63.64% | 78.07% | N/A |  |  | N/A | [7 empty] | 5900
American Standard | American Standard | AccuComfort Platinum 18 | 8761171 | 4A6V8036A1 | *UD2C080ACV4 & 4TXCC007DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36400 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32600 | 32800 | 0.51 | 2.44 | 2.35 | 4.82 | 3.9146 | 4.08 |  | 16150 | 26400 | 26500 | 1.8 | 2.44 | 3.18 | 2.62 | 3.1701 | 2.44 |  | 16994 |  | 20400 | 2.56 |  | 3.04 | 1.94 |  | 1.95 | 62.2% | 76.98% | N/A |  |  | N/A | [7 empty] | 6100
American Standard | American Standard | AccuComfort Platinum 18 | 8761172 | 4A6V8036A1 | *UHMB080ACV3 & 4TXCC007DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36200 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33000 | 33100 | 0.56 | 2.4 | 2.44 | 4.44 | 4.0287 | 3.98 |  | 16700 | 26800 | 26900 | 1.89 | 2.4 | 3.28 | 2.58 | 3.2718 | 2.4 |  | 17640 |  | 21040 | 2.68 |  | 3.16 | 1.92 |  | 1.95 | 63.56% | 78.22% | N/A |  |  | N/A | [7 empty] | 5860
American Standard | American Standard | AccuComfort Platinum 18 | 8761173 | 4A6V8036A1 | *UD2C100ACV5 & 4TXCC007DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36200 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32600 | 32800 | 0.51 | 2.44 | 2.35 | 4.82 | 3.9146 | 4.08 |  | 16040 | 26200 | 26400 | 1.79 | 2.44 | 3.17 | 2.62 | 3.1461 | 2.44 |  | 16894 |  | 20300 | 2.56 |  | 3.04 | 1.94 |  | 1.95 | 61.89% | 76.89% | N/A |  |  | N/A | [7 empty] | 6100
American Standard | American Standard | AccuComfort Platinum 18 | 8761175 | 4A6V8036A1 | *UHMC100ACV4 & 4TXCC007DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36400 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32800 | 32900 | 0.53 | 2.46 | 2.35 | 4.64 | 3.9066 | 4.1 |  | 16370 | 26600 | 26700 | 1.81 | 2.46 | 3.18 | 2.64 | 3.1682 | 2.46 |  | 17194 |  | 20600 | 2.56 |  | 3.04 | 1.96 |  | 2.00 | 62.61% | 77.15% | N/A |  |  | N/A | [7 empty] | 6100
American Standard | American Standard | AccuComfort Platinum 18 | 8761183 | 4A6V8037A1 | *UD2B080ACV3 & 4TXCB006DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36600 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33200 | 33500 | 0.53 | 2.36 | 2.48 | 4.7 | 4.1218 | 3.96 |  | 16370 | 26800 | 27000 | 1.91 | 2.36 | 3.34 | 2.52 | 3.3273 | 2.36 |  | 17340 |  | 20760 | 2.72 |  | 3.22 | 1.86 |  | 1.90 | 61.97% | 76.89% | N/A |  |  | N/A | [7 empty] | 6240
American Standard | American Standard | AccuComfort Platinum 18 | 8761190 | 4A6V8037A1 | *UHMC100ACV4 & 4TXCC007DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36800 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33200 | 33400 | 0.55 | 2.44 | 2.41 | 4.52 | 3.9867 | 4.06 |  | 16040 | 26800 | 26900 | 1.85 | 2.44 | 3.24 | 2.54 | 3.2182 | 2.44 |  | 16894 |  | 20420 | 2.62 |  | 3.1 | 1.88 |  | 1.95 | 61.14% | 75.91% | N/A |  |  | N/A | [7 empty] | 6480
American Standard | American Standard | AccuComfort Platinum 18 | 8761191 | 4A6V8037A1 | *UD2C100ACV5 & 4TXCC007DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 37000 | Yes | Centrally Ducted | N/A | N/A | 8400 | 33200 | 33300 | 0.51 | 2.44 | 2.37 | 4.82 | 3.9867 | 4.12 |  | 15710 | 26600 | 26600 | 1.81 | 2.44 | 3.2 | 2.54 | 3.1942 | 2.44 |  | 16488 |  | 20080 | 2.58 |  | 3.06 | 1.88 |  | 1.90 | 60.3% | 75.49% | N/A |  |  | N/A | [7 empty] | 6520
American Standard | American Standard | AccuComfort Platinum 18 | 8761192 | 4A6V8037A1 | *UD2C080ACV4 & 4TXCC007DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36800 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33200 | 33300 | 0.52 | 2.42 | 2.41 | 4.78 | 4.0196 | 4.04 |  | 15930 | 26600 | 26700 | 1.84 | 2.42 | 3.24 | 2.54 | 3.2205 | 2.42 |  | 16688 |  | 20220 | 2.62 |  | 3.1 | 1.86 |  | 1.90 | 60.72% | 75.73% | N/A |  |  | N/A | [7 empty] | 6480
American Standard | American Standard | AccuComfort Platinum 18 | 8761198 | 4A6V8048A1 | *UD2D120ACV5 & 4TXCC009DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 12400 | 43500 | 44700 | 0.82 | 2.36 | 3.56 | 4.44 | 5.4006 | 3.68 |  | 23400 | 36600 | 37600 | 2.64 | 2.36 | 4.67 | 2.6 | 4.5439 | 2.36 |  | 24496 |  | 29200 | 3.72 |  | 4.44 | 1.92 |  | 1.95 | 65.32% | 77.66% | N/A |  |  | N/A | [7 empty] | 8400
American Standard | American Standard | AccuComfort Platinum 18 | 8761199 | 4A6V8048A1 | *UD2C080ACV4 & 4TXCC009DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 12400 | 43500 | 44700 | 0.83 | 2.34 | 3.59 | 4.38 | 5.4467 | 3.64 |  | 23180 | 36400 | 37400 | 2.65 | 2.34 | 4.7 | 2.56 | 4.5577 | 2.34 |  | 24250 |  | 28900 | 3.72 |  | 4.46 | 1.90 |  | 1.90 | 64.65% | 77.27% | N/A |  |  | N/A | [7 empty] | 8500
American Standard | American Standard | AccuComfort Platinum 18 | 8761201 | 4A6V8048A1 | *UHMC100ACV4 & 4TXCC009DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 12400 | 43500 | 44800 | 0.85 | 2.36 | 3.57 | 4.28 | 5.4006 | 3.68 |  | 23400 | 36600 | 37500 | 2.66 | 2.36 | 4.67 | 2.58 | 4.5439 | 2.36 |  | 24456 |  | 29140 | 3.72 |  | 4.44 | 1.92 |  | 1.90 | 65.04% | 77.71% | N/A |  |  | N/A | [7 empty] | 8360
American Standard | American Standard | AccuComfort Platinum 18 | 8761202 | 4A6V8048A1 | *UD2C100ACV5 & 4TXCC009DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 12300 | 43500 | 44600 | 0.82 | 2.38 | 3.51 | 4.4 | 5.3552 | 3.72 |  | 23290 | 36600 | 37400 | 2.61 | 2.38 | 4.62 | 2.62 | 4.5058 | 2.38 |  | 24456 |  | 29140 | 3.66 |  | 4.38 | 1.96 |  | 1.95 | 65.34% | 77.91% | N/A |  |  | N/A | [7 empty] | 8260
American Standard | American Standard | AccuComfort Platinum 18 | 8761205 | 4A6V8048A1 | *UD2D120ACV5 & 4TXCD010DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 48000 | Yes | Centrally Ducted | N/A | N/A | 12300 | 44000 | 44600 | 0.78 | 2.4 | 3.4 | 4.62 | 5.3716 | 3.84 |  | 23510 | 37000 | 37400 | 2.56 | 2.4 | 4.56 | 2.7 | 4.517 | 2.4 |  | 24696 |  | 29340 | 3.62 |  | 4.34 | 2.00 |  | 2.00 | 65.78% | 78.45% | N/A |  |  | N/A | [7 empty] | 8060
American Standard | American Standard | AccuComfort Platinum 20 | 8935197 | 4A6V0024A1 | *DD2B060ACV3 & 4PXCBD36BS3 | HRCU-A-CB | 10 | 19.25 | 13.5 | 24400 | Yes | Centrally Ducted | N/A | N/A | 8100 | 22200 | 22000 | 0.53 | 2.54 | 1.57 | 4.48 | 2.5608 | 4.1 |  | 11540 | 17200 | 17100 | 1.22 | 2.54 | 1.98 | 2.78 | 1.9841 | 2.54 |  | 11176 |  | 13020 | 1.62 |  | 1.9 | 2.02 |  | 2.00 | 59.18% | 76.14% | N/A |  |  | N/A | [7 empty] | 4080
American Standard | American Standard | AccuComfort Platinum 20 | 8935198 | 4A6V0024A1 | *DHMB060BCV3 & 4PXCBD36BS3 | HRCU-A-CB | 10 | 19 | 13 | 24400 | Yes | Centrally Ducted | N/A | N/A | 8100 | 22200 | 22100 | 0.53 | 2.5 | 1.6 | 4.48 | 2.6018 | 4.04 |  | 11650 | 17400 | 17300 | 1.23 | 2.5 | 2.02 | 2.78 | 2.0393 | 2.5 |  | 11276 |  | 13220 | 1.64 |  | 1.92 | 2.02 |  | 2.00 | 59.82% | 76.42% | N/A |  |  | N/A | [7 empty] | 4080
American Standard | American Standard | AccuComfort Platinum 20 | 8935199 | 4A6V0024A1 | *UD2B060ACV3 & 4TXCB004DS3 | HRCU-A-CB | 10 | 19 | 13.5 | 24200 | Yes | Centrally Ducted | N/A | N/A | 7800 | 21200 | 21200 | 0.51 | 2.52 | 1.54 | 4.48 | 2.4649 | 4.04 |  | 11650 | 16800 | 16700 | 1.2 | 2.52 | 1.94 | 2.84 | 1.9533 | 2.52 |  | 11416 |  | 13200 | 1.6 |  | 1.86 | 2.10 |  | 2.10 | 62.26% | 79.04% | N/A |  |  | N/A | [7 empty] | 3500
American Standard | American Standard | AccuComfort Platinum 18 | 9119381 | 4A6V8024A1 | *DHMB060BCV3 & 4PXCBD36BS3 | HRCU-A-CB | 10 | 18 | 12.5 | 24000 | Yes | Centrally Ducted | N/A | N/A | 8100 | 22200 | 22100 | 0.53 | 2.5 | 1.6 | 4.48 | 2.6018 | 4.04 |  | 11650 | 17400 | 17300 | 1.23 | 2.5 | 2.02 | 2.78 | 2.0393 | 2.5 |  | 11276 |  | 13220 | 1.64 |  | 1.92 | 2.02 |  | 2.00 | 59.82% | 76.42% | N/A |  |  | N/A | [7 empty] | 4080
American Standard | American Standard | AccuComfort Platinum 18 | 9122524 | 4A6V8024A1 | *DD2B060ACV3 & 4PXCBD36BS3 | HRCU-A-CB | 10 | 18 | 12.5 | 24000 | Yes | Centrally Ducted | N/A | N/A | 8100 | 22200 | 22000 | 0.53 | 2.54 | 1.57 | 4.48 | 2.5608 | 4.1 |  | 11540 | 17200 | 17100 | 1.22 | 2.54 | 1.98 | 2.78 | 1.9841 | 2.54 |  | 11176 |  | 13020 | 1.62 |  | 1.9 | 2.02 |  | 2.00 | 59.18% | 76.14% | N/A |  |  | N/A | [7 empty] | 4080
American Standard | American Standard | AccuComfort Platinum 20 | 9122736 | 4A6V0024A1 | *UHMB060ACV3 & 4PXCBU42BS3 | HRCU-A-CB | 10 | 18 | 13 | 24600 | Yes | Centrally Ducted | N/A | N/A | 8200 | 22200 | 22100 | 0.57 | 2.56 | 1.58 | 4.22 | 2.5408 | 4.1 |  | 12090 | 17300 | 17300 | 1.25 | 2.56 | 1.98 | 2.84 | 1.98 | 2.56 |  | 11782 |  | 13600 | 1.66 |  | 1.9 | 2.08 |  | 2.10 | 61.54% | 78.61% | N/A |  |  | N/A | [7 empty] | 3700
American Standard | American Standard | AccuComfort Platinum 20 | 10093446 | 4A6V0024A1 | TAM9A0B30V31 | HRCU-A-CB | 10 | 19.25 | 13.75 | 24200 | Yes | Centrally Ducted | N/A | N/A | 8000 | 20200 | 21300 | 0.54 | 2.6 | 1.51 | 4.34 | 2.2764 | 4.14 |  | 11430 | 17100 | 17100 | 1.21 | 2.6 | 1.93 | 2.76 | 1.927 | 2.6 |  | 11036 |  | 12920 | 1.62 |  | 1.86 | 2.00 |  | 2.05 | 60.66% | 75.56% | N/A |  |  | N/A | [7 empty] | 4180
American Standard | American Standard | AccuComfort Platinum 20 | 10093447 | 4A6V0036A1 | TAM9A0B30V31 | HRCU-A-CB | 10 | 20 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8600 | 32600 | 21300 | 0.54 | 2.42 | 1.6 | 4.66 | 3.947 | 3.9 |  | 16040 | 26200 | 26600 | 1.82 | 2.42 | 3.22 | 2.58 | 3.1721 | 2.42 |  | 16748 |  | 20220 | 2.58 |  | 3.08 | 1.90 |  | 1.90 | 94.93% | 76.02% | N/A |  |  | N/A | [7 empty] | 6380
American Standard | American Standard | AccuComfort Platinum 20 | 10093448 | 4A6V0036A1 | TAM9A0C36V31 | HRCU-A-CB | 10 | 21 | 13.5 | 35000 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33400 | 21600 | 0.52 | 2.38 | 1.55 | 4.78 | 4.1118 | 4.08 |  | 15820 | 25800 | 26100 | 1.83 | 2.38 | 3.22 | 2.54 | 3.1762 | 2.38 |  | 16448 |  | 19860 | 2.58 |  | 3.08 | 1.86 |  | 1.90 | 91.94% | 76.09% | N/A |  |  | N/A | [7 empty] | 6240
American Standard | American Standard | AccuComfort Platinum 20 | 10093449 | 4A6V0036A1 | TAM9A0C42V41 | HRCU-A-CB | 10 | 21 | 13.5 | 35600 | Yes | Centrally Ducted | N/A | N/A | 8400 | 33600 | 21400 | 0.51 | 2.2 | 1.57 | 4.82 | 4.4749 | 4 |  | 15600 | 24800 | 25200 | 1.9 | 2.2 | 3.36 | 2.4 | 3.3029 | 2.2 |  | 16242 |  | 19440 | 2.7 |  | 3.22 | 1.76 |  | 1.75 | 90.84% | 77.14% | N/A |  |  | N/A | [7 empty] | 5760
American Standard | American Standard | AccuComfort Platinum 20 | 10093452 | 4A6V0048A1 | TAM9A0C60V51 | HRCU-A-CB | 10 | 19.5 | 12.5 | 46500 | Yes | Centrally Ducted | N/A | N/A | 12000 | 43000 | 42700 | 0.78 | 2.26 | 3.56 | 4.5 | 5.5747 | 3.52 |  | 22630 | 35600 | 36100 | 2.65 | 2.26 | 4.67 | 2.5 | 4.6154 | 2.26 |  | 23644 |  | 28140 | 3.74 |  | 4.46 | 1.86 |  | 1.85 | 65.9% | 77.95% | N/A |  |  | N/A | [7 empty] | 7960
American Standard | American Standard | AccuComfort Platinum 18 | 10093454 | 4A6V8024A1 | TAM9A0B30V31 | HRCU-A-CB | 10 | 18 | 13 | 23800 | Yes | Centrally Ducted | N/A | N/A | 8000 | 20000 | 21000 | 0.54 | 2.6 | 1.55 | 4.34 | 2.2538 | 3.96 |  | 11430 | 17100 | 17100 | 1.21 | 2.6 | 1.93 | 2.76 | 1.927 | 2.6 |  | 11036 |  | 12920 | 1.62 |  | 1.86 | 2.00 |  | 2.05 | 61.52% | 75.56% | N/A |  |  | N/A | [7 empty] | 4180
American Standard | American Standard | AccuComfort Platinum 18 | 10093455 | 4A6V8024A1 | TAM9A0C36V31 | HRCU-A-CB | 10 | 18 | 13 | 24000 | Yes | Centrally Ducted | N/A | N/A | 8000 | 21000 | 21400 | 0.54 | 2.52 | 1.52 | 4.34 | 2.4416 | 4.12 |  | 11320 | 16900 | 16900 | 1.23 | 2.52 | 1.96 | 2.7 | 1.9649 | 2.52 |  | 10830 |  | 12780 | 1.64 |  | 1.9 | 1.94 |  | 1.95 | 59.72% | 75.62% | N/A |  |  | N/A | [7 empty] | 4120
American Standard | American Standard | AccuComfort Platinum 18 | 10093456 | 4A6V8036A1 | TAM9A0B30V31 | HRCU-A-CB | 10 | 18 | 12.5 | 34400 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32000 | 43900 | 0.53 | 2.4 | 3.45 | 4.64 | 3.9066 | 3.72 |  | 16370 | 26600 | 26800 | 1.84 | 2.4 | 3.27 | 2.6 | 3.2474 | 2.4 |  | 17340 |  | 20760 | 2.6 |  | 3.12 | 1.96 |  | 1.95 | 47.29% | 77.46% | N/A |  |  | N/A | [7 empty] | 6040
American Standard | American Standard | AccuComfort Platinum 18 | 10093457 | 4A6V8036A1 | TAM9A0C36V31 | HRCU-A-CB | 10 | 18 | 13 | 35000 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32200 | 43400 | 0.52 | 2.36 | 3.36 | 4.68 | 3.9977 | 3.78 |  | 16260 | 26200 | 26400 | 1.85 | 2.36 | 3.27 | 2.58 | 3.2528 | 2.36 |  | 17134 |  | 20500 | 2.64 |  | 3.14 | 1.90 |  | 1.90 | 47.24% | 77.65% | N/A |  |  | N/A | [7 empty] | 5900
American Standard | American Standard | AccuComfort Platinum 18 | 10093458 | 4A6V8036A1 | TAM9A0C42V41 | HRCU-A-CB | 10 | 18 | 12.5 | 35800 | Yes | Centrally Ducted | N/A | N/A | 8400 | 30000 | 43200 | 0.51 | 2.22 | 3.43 | 4.82 | 3.9594 | 3.7 |  | 16040 | 25400 | 25700 | 1.91 | 2.22 | 3.39 | 2.46 | 3.3523 | 2.22 |  | 16894 |  | 20040 | 2.72 |  | 3.24 | 1.82 |  | 1.80 | 46.39% | 77.98% | N/A |  |  | N/A | [7 empty] | 5660
American Standard | American Standard | AccuComfort Platinum 18 | 10093459 | 4A6V8037A1 | TAM9A0B30V31 | HRCU-A-CB | 10 | 18 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8600 | 32600 | 31400 | 0.54 | 2.42 | 2.37 | 4.66 | 3.947 | 3.88 |  | 16040 | 26200 | 26600 | 1.82 | 2.42 | 3.22 | 2.58 | 3.1721 | 2.42 |  | 16748 |  | 20220 | 2.58 |  | 3.08 | 1.90 |  | 1.90 | 64.39% | 76.02% | N/A |  |  | N/A | [7 empty] | 6380
American Standard | American Standard | AccuComfort Platinum 18 | 10093460 | 4A6V8037A1 | TAM9A0C36V31 | HRCU-A-CB | 10 | 18 | 13 | 35800 | Yes | Centrally Ducted | N/A | N/A | 8500 | 32800 | 32200 | 0.52 | 2.38 | 2.3 | 4.78 | 4.0379 | 4.1 |  | 15820 | 25800 | 26100 | 1.83 | 2.38 | 3.22 | 2.54 | 3.1762 | 2.38 |  | 16448 |  | 19860 | 2.58 |  | 3.08 | 1.86 |  | 1.90 | 61.68% | 76.09% | N/A |  |  | N/A | [7 empty] | 6240
American Standard | American Standard | AccuComfort Platinum 18 | 10093461 | 4A6V8037A1 | TAM9A0C42V41 | HRCU-A-CB | 10 | 18 | 12.5 | 46500 | Yes | Centrally Ducted | N/A | N/A | 8400 | 30800 | 33300 | 0.51 | 2.2 | 2.68 | 4.82 | 4.102 | 3.64 |  | 15600 | 24800 | 25200 | 1.9 | 2.2 | 3.36 | 2.4 | 3.3029 | 2.2 |  | 16242 |  | 19440 | 2.7 |  | 3.22 | 1.76 |  | 1.75 | 58.38% | 77.14% | N/A |  |  | N/A | [7 empty] | 5760
American Standard | American Standard | AccuComfort Platinum 18 | 10093462 | 4A6V8048A1 | TAM9A0C42V41 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 12300 | 41500 | 42600 | 0.76 | 2.14 | 3.8 | 4.74 | 5.682 | 3.28 |  | 23290 | 36200 | 36600 | 2.81 | 2.14 | 5 | 2.42 | 4.9563 | 2.14 |  | 24456 |  | 28920 | 4.04 |  | 4.8 | 1.78 |  | 1.75 | 67.89% | 79.02% | N/A |  |  | N/A | [7 empty] | 7680
American Standard | American Standard | AccuComfort Platinum 18 | 10093463 | 4A6V8048A1 | TAM9A0C48V41 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 11900 | 41000 | 43000 | 0.76 | 2.36 | 3.46 | 4.58 | 5.0902 | 3.64 |  | 22960 | 36400 | 36800 | 2.59 | 2.36 | 4.57 | 2.6 | 4.5191 | 2.36 |  | 24190 |  | 28780 | 3.68 |  | 4.38 | 1.92 |  | 1.95 | 66.93% | 78.21% | N/A |  |  | N/A | [7 empty] | 8020
American Standard | American Standard | AccuComfort Platinum 18 | 10093464 | 4A6V8048A1 | TAM9A0C60V51 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 11900 | 41500 | 42600 | 0.77 | 2.32 | 3.54 | 4.52 | 5.2411 | 3.52 |  | 22850 | 36200 | 36600 | 2.62 | 2.32 | 4.64 | 2.56 | 4.5718 | 2.32 |  | 24150 |  | 28680 | 3.72 |  | 4.42 | 1.90 |  | 1.90 | 67.32% | 78.36% | N/A |  |  | N/A | [7 empty] | 7920
American Standard | American Standard | AccuComfort Platinum 18 | 10093467 | 4A6V8049A1 | TAM9A0C60V51 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 12000 | 41000 | 31700 | 0.78 | 2.26 | 2.5 | 4.5 | 5.3154 | 3.72 |  | 22630 | 35600 | 36100 | 2.65 | 2.26 | 4.67 | 2.5 | 4.6154 | 2.26 |  | 23644 |  | 28140 | 3.74 |  | 4.46 | 1.86 |  | 1.85 | 88.77% | 77.95% | N/A |  |  | N/A | [7 empty] | 7960
American Standard | American Standard | AccuComfort Platinum 18 | 10093468 | 4A6V8060A1 | TAM9A0C60V51 | HRCU-A-CB | 10 | 18 | 12.5 | 54000 | Yes | Centrally Ducted | N/A | N/A | 18400 | 50500 | 32300 | 1.21 | 2.1 | 2.55 | 4.46 | 7.0459 | 3.72 |  | 33510 | 49500 | 51100 | 3.94 | 2.1 | 7.14 | 2.5 | 6.9064 | 2.1 |  | 34860 |  | 40780 | 5.6 |  | 6.76 | 1.82 |  | 1.75 | 126.3% | 79.8% | N/A |  |  | N/A | [7 empty] | 10320
American Standard | American Standard | AccuComfort Platinum 20 | 10153439 | 4A6V0036A1 | TEM8A0C36V31+TDR | HRCU-A-CB | 10 | 20 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31800 | 32700 | 0.51 | 2.44 | 2.37 | 4.72 | 3.8186 | 4.04 |  | 15380 | 25600 | 25500 | 1.75 | 2.44 | 3.06 | 2.58 | 3.0741 | 2.44 |  | 16182 |  | 19500 | 2.48 |  | 2.94 | 1.92 |  | 1.95 | 59.63% | 76.47% | N/A |  |  | N/A | [7 empty] | 6000
American Standard | American Standard | AccuComfort Platinum 20 | 10153440 | 4A6V0036A1 | TEM8A0C42V41+TDR | HRCU-A-CB | 10 | 20 | 13 | 35600 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31400 | 32700 | 0.52 | 2.32 | 2.41 | 4.68 | 3.9656 | 3.98 |  | 15490 | 25200 | 25400 | 1.82 | 2.32 | 3.2 | 2.5 | 3.1826 | 2.32 |  | 16182 |  | 19400 | 2.58 |  | 3.06 | 1.84 |  | 1.85 | 59.33% | 76.38% | N/A |  |  | N/A | [7 empty] | 6000
American Standard | American Standard | AccuComfort Platinum 20 | 10153441 | 4A6V0036A1 | TEM8A0C48V41+TDR | HRCU-A-CB | 10 | 20 | 13 | 35600 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31000 | 31100 | 0.52 | 2.4 | 2.52 | 4.62 | 3.7845 | 3.62 |  | 15600 | 25200 | 25600 | 1.78 | 2.4 | 3.12 | 2.56 | 3.0765 | 2.4 |  | 16382 |  | 19700 | 2.52 |  | 2.98 | 1.90 |  | 1.95 | 63.34% | 76.95% | N/A |  |  | N/A | [7 empty] | 5900
American Standard | American Standard | AccuComfort Platinum 20 | 10153442 | 4A6V0036A1 | TEM8A0D48V41+TDR | HRCU-A-CB | 10 | 19.5 | 13 | 35800 | Yes | Centrally Ducted | N/A | N/A | 8400 | 31800 | 33100 | 0.51 | 2.48 | 2.65 | 4.82 | 3.757 | 3.66 |  | 15930 | 25800 | 26100 | 1.77 | 2.48 | 3.08 | 2.64 | 3.0481 | 2.48 |  | 16688 |  | 20000 | 2.52 |  | 2.98 | 1.94 |  | 1.95 | 60.42% | 76.63% | N/A |  |  | N/A | [7 empty] | 6100
American Standard | American Standard | AccuComfort Platinum 20 | 10153444 | 4A6V0048A1 | TEM8A0C48V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 47500 | Yes | Centrally Ducted | N/A | N/A | 11900 | 42000 | 33100 | 0.76 | 2.36 | 2.65 | 4.58 | 5.2144 | 3.66 |  | 22410 | 35600 | 36000 | 2.56 | 2.36 | 4.48 | 2.56 | 4.4198 | 2.36 |  | 23504 |  | 27980 | 3.62 |  | 4.28 | 1.90 |  | 1.90 | 84.53% | 77.72% | N/A |  |  | N/A | [7 empty] | 8020
American Standard | American Standard | AccuComfort Platinum 20 | 10153445 | 4A6V0048A1 | TEM8A0C60V51+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 12200 | 43500 | 32100 | 0.78 | 2.34 | 2.35 | 4.58 | 5.4467 | 4 |  | 22520 | 36200 | 36600 | 2.61 | 2.34 | 4.57 | 2.52 | 4.5327 | 2.34 |  | 23504 |  | 28100 | 3.68 |  | 4.38 | 1.88 |  | 1.90 | 87.54% | 76.78% | N/A |  |  | N/A | [7 empty] | 8500
American Standard | American Standard | AccuComfort Platinum 18 | 10153453 | 4A6V8036A1 | TEM8A0C36V31+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 35200 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31600 | 42600 | 0.51 | 2.4 | 3.37 | 4.72 | 3.8578 | 3.7 |  | 15930 | 25600 | 25800 | 1.8 | 2.4 | 3.16 | 2.6 | 3.1253 | 2.4 |  | 16728 |  | 20040 | 2.56 |  | 3.02 | 1.92 |  | 1.95 | 47.04% | 77.67% | N/A |  |  | N/A | [7 empty] | 5760
American Standard | American Standard | AccuComfort Platinum 18 | 10153454 | 4A6V8036A1 | TEM8A0C42V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31600 | 43900 | 0.51 | 2.32 | 3.45 | 4.72 | 3.9908 | 3.72 |  | 15820 | 25600 | 25800 | 1.84 | 2.32 | 3.25 | 2.52 | 3.2331 | 2.32 |  | 16688 |  | 19940 | 2.62 |  | 3.12 | 1.86 |  | 1.85 | 45.42% | 77.29% | N/A |  |  | N/A | [7 empty] | 5860
American Standard | American Standard | AccuComfort Platinum 18 | 10153455 | 4A6V8036A1 | TEM8A0C48V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 36200 | Yes | Centrally Ducted | N/A | N/A | 8000 | 31000 | 43600 | 0.52 | 2.42 | 3.38 | 4.5 | 3.7533 | 3.78 |  | 15820 | 25400 | 25700 | 1.78 | 2.42 | 3.11 | 2.6 | 3.0753 | 2.42 |  | 16788 |  | 20040 | 2.52 |  | 3 | 1.96 |  | 1.95 | 45.96% | 77.98% | N/A |  |  | N/A | [7 empty] | 5660
American Standard | American Standard | AccuComfort Platinum 18 | 10153456 | 4A6V8036A1 | TEM8A0D48V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31600 | 43200 | 0.51 | 2.46 | 3.43 | 4.76 | 3.7637 | 3.7 |  | 15930 | 25800 | 26100 | 1.78 | 2.46 | 3.11 | 2.62 | 3.0729 | 2.46 |  | 16788 |  | 20100 | 2.52 |  | 3 | 1.96 |  | 1.95 | 46.53% | 77.01% | N/A |  |  | N/A | [7 empty] | 6000
American Standard | American Standard | AccuComfort Platinum 18 | 10153458 | 4A6V8037A1 | TEM8A0C36V31+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31800 | 31200 | 0.51 | 2.44 | 2.38 | 4.72 | 3.8186 | 3.84 |  | 15380 | 25600 | 25500 | 1.75 | 2.44 | 3.06 | 2.58 | 3.0741 | 2.44 |  | 16182 |  | 19500 | 2.48 |  | 2.94 | 1.92 |  | 1.95 | 62.5% | 76.47% | N/A |  |  | N/A | [7 empty] | 6000
American Standard | American Standard | AccuComfort Platinum 18 | 10153459 | 4A6V8037A1 | TEM8A0C42V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 35600 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31400 | 31300 | 0.52 | 2.32 | 2.35 | 4.68 | 3.9656 | 3.9 |  | 15490 | 25200 | 25400 | 1.82 | 2.32 | 3.2 | 2.5 | 3.1826 | 2.32 |  | 16182 |  | 19400 | 2.58 |  | 3.06 | 1.84 |  | 1.85 | 61.98% | 76.38% | N/A |  |  | N/A | [7 empty] | 6000
American Standard | American Standard | AccuComfort Platinum 18 | 10153460 | 4A6V8037A1 | TEM8A0C48V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 35600 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31000 | 32300 | 0.52 | 2.4 | 2.31 | 4.62 | 3.7845 | 4.1 |  | 15600 | 25200 | 25600 | 1.78 | 2.4 | 3.12 | 2.56 | 3.0765 | 2.4 |  | 16382 |  | 19700 | 2.52 |  | 2.98 | 1.90 |  | 1.95 | 60.99% | 76.95% | N/A |  |  | N/A | [7 empty] | 5900
American Standard | American Standard | AccuComfort Platinum 18 | 10153461 | 4A6V8037A1 | TEM8A0D48V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 35800 | Yes | Centrally Ducted | N/A | N/A | 8400 | 31800 | 31700 | 0.51 | 2.48 | 2.49 | 4.82 | 3.757 | 3.74 |  | 15930 | 25800 | 26100 | 1.77 | 2.48 | 3.08 | 2.64 | 3.0481 | 2.48 |  | 16688 |  | 20000 | 2.52 |  | 2.98 | 1.94 |  | 1.95 | 63.09% | 76.63% | N/A |  |  | N/A | [7 empty] | 6100
American Standard | American Standard | AccuComfort Platinum 18 | 10153463 | 4A6V8048A1 | TEM8A0C48V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 46500 | Yes | Centrally Ducted | N/A | N/A | 11900 | 42500 | 43400 | 0.81 | 2.24 | 3.5 | 4.3 | 5.5591 | 3.64 |  | 21310 | 34200 | 35100 | 2.62 | 2.24 | 4.61 | 2.38 | 4.4734 | 2.24 |  | 21900 |  | 26460 | 3.68 |  | 4.4 | 1.74 |  | 1.75 | 60.97% | 75.38% | N/A |  |  | N/A | [7 empty] | 8640
American Standard | American Standard | AccuComfort Platinum 18 | 10153464 | 4A6V8048A1 | TEM8A0C60V51+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 47500 | Yes | Centrally Ducted | N/A | N/A | 12100 | 44500 | 44000 | 0.78 | 2.4 | 3.47 | 4.54 | 5.4327 | 3.72 |  | 22630 | 36800 | 37200 | 2.58 | 2.4 | 4.56 | 2.56 | 4.4926 | 2.4 |  | 23744 |  | 28520 | 3.64 |  | 4.36 | 1.92 |  | 1.90 | 64.82% | 76.67% | N/A |  |  | N/A | [7 empty] | 8680
American Standard | American Standard | AccuComfort Platinum 18 | 10153468 | 4A6V8049A1 | TEM8A0C48V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 47500 | Yes | Centrally Ducted | N/A | N/A | 11900 | 42000 | 32700 | 0.76 | 2.36 | 2.42 | 4.58 | 5.2144 | 3.96 |  | 22410 | 35600 | 36000 | 2.56 | 2.36 | 4.48 | 2.56 | 4.4198 | 2.36 |  | 23504 |  | 27980 | 3.62 |  | 4.28 | 1.90 |  | 1.90 | 85.57% | 77.72% | N/A |  |  | N/A | [7 empty] | 8020
American Standard | American Standard | AccuComfort Platinum 18 | 10153469 | 4A6V8049A1 | TEM8A0C60V51+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 12200 | 43500 | 31000 | 0.78 | 2.34 | 2.5 | 4.58 | 5.4467 | 3.64 |  | 22520 | 36200 | 36600 | 2.61 | 2.34 | 4.57 | 2.52 | 4.5327 | 2.34 |  | 23504 |  | 28100 | 3.68 |  | 4.38 | 1.88 |  | 1.90 | 90.65% | 76.78% | N/A |  |  | N/A | [7 empty] | 8500
American Standard | American Standard |  | 7151530 | 4TXK2709A10N0AA | 4MXW2709A10N0AA | HRCU-A-CB-O | 10 | 27 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2200 | 9800 | 11000 | 0.1 | 0.65 | 1.25 | 6.4476 | 4.4186 | 2.579 |  | 1989 | 5800 | 10630.675 | 0.12 | 0.62822 | 1.2595 | 4.8577 | 2.7058 | 2.4736 |  | 1480 |  | 8000 | 0.15 |  | 1.095 | 2.8916 |  | 2.1412 | 72.73% | 75.25% | Integrated | 72W | Heater on below 34°F | N/A |  | z | [5 empty] | 2630.675
American Standard | American Standard |  | 7151532 | 4TXK2712A10NAA | 4MXW2712A10N0AA | HRCU-A-CB-O | 10 | 25 | 13 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2400 | 13000 | 14000 | 0.1 | 0.96 | 1.35 | 7.0337 | 3.9687 | 3.0393 |  | 2200 | 8000 | 8700 | 0.09 | 0.75 | 1.01 | 7.164 | 3.1261 | 2.5245 |  | 2100 |  | 8300 | 0.085 |  | 1.131 | 7.2406 |  | 2.1507 | 59.29% | 95.4% | Integrated | 72W | Heater on below 34°F | N/A |  | z | [5 empty] | 400
American Standard | American Standard |  | 7151534 | 4TXK2718A10N0AA | 4MXW2718A10N0AA | HRCU-A-CB-O | 10 | 21 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3412 | 19000 | 23202 | 0.4 | 1.58 | 2.5 | 2.4999 | 3.5243 | 2.7199 |  | 2729 | 12100 | 19674 | 0.41 | 1.26 | 2.57 | 1.9507 | 2.8144 | 2.2435 |  | 2388 |  | 15400 | 0.42 |  | 2.29 | 1.6663 |  | 1.9709 | 66.37% | 78.28% | Integrated | 160W | Heater on below 34°F | N/A | [7 empty] | 4274
American Standard | American Standard |  | 9150122 | 4TXK3809A10NUAA | 4MXW3809A10NUAA | HRCU-A-CB-O | 15 | 38 | 16.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2300 | 9000 | 13600 | 0.2 | 0.59 | 1.5 | 3.3703 | 4.4706 | 2.6572 |  | 3545 | 5600 | 14610.8 | 0.365 | 0.74596 | 1.7826 | 2.8464 | 2.2001 | 2.4021 |  | 1745 |  | 12210 | 0.28 |  | 1.72 | 1.8265 |  | 2.0805 | 89.78% | 83.57% | Integrated | 72W | Heater on below 34°F | N/A | [7 empty] | 2400.8
American Standard | American Standard |  | 9150124 | 4TXK3812A10NUAA | 4MXW3812A10NUAA | HRCU-A-CB-O | 14 | 30.5 | 15.25 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 |  | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 |  | 2600 |  | 13304 | 0.22 |  | 1.79 | 3.4636 |  | 2.1782 | 71.14% | 147.8% | Integrated | 72W | Heater on below 34°F | N/A | [7 empty] | -4304
American Standard | American Standard |  | 9150126 | 4TXK3818A10NUAA | 4MXW3818A10NUAA | HRCU-A-CB-O | 12 | 24.5 | 13.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3700 | 18000 | 24400 | 0.35 | 1.5 | 2.5 | 3.0982 | 3.5169 | 2.8604 |  | 3070 | 14200 | 23100 | 0.36 | 1.455 | 3.25 | 2.4992 | 2.8602 | 2.0831 |  | 2388 |  | 20634 | 0.37 |  | 3.3 | 1.8915 |  | 1.8325 | 84.57% | 89.32% | Integrated | 160W | Heater on below 34°F | N/A | [7 empty] | 2466
American Standard | American Standard |  | 9150128 | 4TXK3824A10NUAA | 4MXW3824A10NUAA | HRCU-A-CB-O | 12 | 21.5 | 13 | 22000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6800 | 24000 | 32400 | 0.38 | 2 | 3.7 | 5.2444 | 3.5169 | 2.5664 |  | 3396 | 15500 | 26263 | 0.344 | 1.57 | 3.381 | 2.8932 | 2.8934 | 2.2765 |  | 2887 |  | 24233 | 0.33 |  | 3.175 | 2.5639 |  | 2.2368 | 74.79% | 92.27% | Integrated | 160W | Heater on below 34°F | N/A | [7 empty] | 2030
Bosch | Bosch | Bosch Climate 5000 ductless minisplit series | 9966837 | BMS500-AAS009-0CSXXA | BMS500-AAU009-0AHXXA | HRCU-A-CB-O | 10.5 | 22 | 14 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3580 | 9800 | 12490 | 0.162 | 0.892 | 1.045 | 6.4765 | 3.2198 | 3.5028 |  | 2860 | 5800 | 7868 | 0.175 | 0.625 | 0.962 | 4.7896 | 2.7197 | 2.397 |  | 2513 |  | 6516 | 0.164 |  | 0.933 | 4.4908 |  | 2.0468 | 52.17% | 82.82% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 1352
Bosch | Bosch | Bosch Climate 5000 ductless minisplit series | 9966838 | BMS500-AAS009-1CSXXA | BMS500-AAU009-1AHXXA | HRCU-A-CB-O | 10 | 20.5 | 14 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3530 | 9800 | 13080 | 0.161 | 0.898 | 1.075 | 6.4257 | 3.1983 | 3.5659 |  | 2610 | 6300 | 8111 | 0.172 | 0.689 | 1.017 | 4.4472 | 2.6797 | 2.3374 |  | 2489 |  | 6609 | 0.159 |  | 1.01 | 4.5878 |  | 1.9177 | 50.53% | 81.48% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 1502
Bosch | Bosch | Bosch Climate 5000 ductless minisplit series | 9966839 | BMS500-AAS012-0CSXXA | BMS500-AAU012-0AHXXA | HRCU-A-CB-O | 10 | 20.9 | 12.5 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3680 | 12000 | 12450 | 0.172 | 1.157 | 1.049 | 6.2704 | 3.0396 | 3.4783 |  | 2958 | 7500 | 7360 | 0.182 | 0.865 | 0.909 | 4.7632 | 2.5411 | 2.3729 |  | 2582 |  | 5736 | 0.18 |  | 0.831 | 4.2039 |  | 2.0229 | 46.07% | 77.93% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 1624
Bosch | Bosch | Bosch Climate 5000 ductless minisplit series | 9966843 | BMS500-AAS018-1CSXXA | BMS500-AAU018-1AHXXA | HRCU-A-CB-O | 10 | 22 | 13 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4670 | 18000 | 19190 | 0.231 | 1.669 | 1.674 | 5.9249 | 3.1607 | 3.3596 |  | 3920 | 11100 | 13730 | 0.262 | 1.179 | 1.615 | 4.3849 | 2.7592 | 2.4916 |  | 3274 |  | 12524 | 0.251 |  | 2.087 | 3.8228 |  | 1.7587 | 65.26% | 91.22% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 1206
Bosch | Bosch | Bosch Climate 5000 ductless minisplit series | 9966844 | BMS500-AAS024-1CSXXA | BMS500-AAU024-1AHXXA | HRCU-A-CB-O | 10 | 20 | 12.5 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7200 | 25000 | 29140 | 0.36 | 2.459 | 2.603 | 5.8614 | 2.9796 | 3.2809 |  | 5690 | 16000 | 18650 | 0.486 | 1.906 | 2.478 | 3.4312 | 2.4602 | 2.2057 |  | 5122 |  | 15815 | 0.471 |  | 2.635 | 3.1871 |  | 1.759 | 54.27% | 84.8% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2835
Bryant | Bryant | Evolution Series | 9893411 | 280ANV024000 | FE4ANB006L+UI | HRCU-A-CB | 12 | 20.5 | 16 | 25200 | Yes | Centrally Ducted | N/A | N/A | 14500 | 23600 | 23600 | 0.85 | 1.47 | 1.47 | 4.9994 | 4.7051 | 4.7051 |  | 13700 | 24800 | 24800 | 1.54 | 2.96 | 2.96 | 2.6072 | 2.4555 | 2.4555 |  | 10900 |  | 19600 | 1.47 |  | 2.77 | 2.1731 |  | 2.0737 | 83.05% | 79.03% | N/A |  |  | N/A | [7 empty] | 5200
Bryant | Bryant | Evolution Series | 9893462 | 280ANV024000 | FE4ANF002L+UI | HRCU-A-CB | 10.5 | 19 | 14.5 | 24200 | Yes | Centrally Ducted | N/A | N/A | 14800.2 | 24000 | 24000 | 0.8585 | 1.4847 | 1.4847 | 5.0524 | 4.7375 | 4.7375 |  | 14000 | 25200 | 25200 | 1.5554 | 2.8886 | 2.8886 | 2.6379 | 2.5567 | 2.5567 |  | 11100 |  | 19800 | 1.4847 |  | 2.7977 | 2.1911 |  | 2.0741 | 82.5% | 78.57% | N/A |  |  | N/A | [7 empty] | 5400
Bryant | Bryant | Evolution Series | 9893463 | 280ANV024000 | FE4AN(B,F)003+UI | HRCU-A-CB | 10.5 | 19.5 | 15 | 24400 | Yes | Centrally Ducted | N/A | N/A | 14600 | 23800 | 23800 | 0.8585 | 1.4847 | 1.4847 | 4.9841 | 4.698 | 4.698 |  | 13850 | 25000 | 25000 | 1.5554 | 2.8886 | 2.8886 | 2.6096 | 2.5364 | 2.5364 |  | 11000 |  | 19800 | 1.4847 |  | 2.7977 | 2.1713 |  | 2.0741 | 83.19% | 79.2% | N/A |  |  | N/A | [7 empty] | 5200
Bryant | Bryant | Evolution Series | 9893556 | 280ANV036000 | FE4ANB006L+UI | HRCU-A-CB | 13 | 20.5 | 14.5 | 35000 | Yes | Centrally Ducted | N/A | N/A | 13340 | 33400 | 33400 | 0.95 | 2.07 | 2.07 | 4.1153 | 4.7288 | 4.7288 |  | 13250 | 31600 | 31600 | 1.83 | 3.3 | 3.3 | 2.122 | 2.8064 | 2.8064 |  | 10670 |  | 23600 | 1.88 |  | 3.14 | 1.6633 |  | 2.2027 | 70.66% | 74.68% | N/A |  |  | N/A | [7 empty] | 8000
Bryant | Bryant | Evolution Series | 9893607 | 280ANV036000 | FE4ANF002L+UI | HRCU-A-CB | 10.5 | 18.5 | 12.5 | 33000 | Yes | Centrally Ducted | N/A | N/A | 14140.4 | 35404 | 35400 | 1.083 | 2.3598 | 2.3598 | 3.8265 | 4.3969 | 4.3964 |  | 14045 | 33496 | 30600 | 2.0862 | 3.762 | 3.762 | 1.9731 | 2.6094 | 2.6094 |  | 11310.2 |  | 33496 | 2.1432 |  | 3.5796 | 1.5466 |  | 2.7424 | 94.62% | 109.5% | N/A |  |  | N/A | [7 empty] | -2896
Bryant | Bryant | Evolution Series | 9893608 | 280ANV036000 | FE4AN(B,F)003L+UI | HRCU-A-CB | 10.5 | 19 | 13 | 33400 | Yes | Centrally Ducted | N/A | N/A | 14273.8 | 35738 | 35600 | 1.083 | 2.3598 | 2.3598 | 3.8626 | 4.4384 | 4.4213 |  | 14177.5 | 33812 | 30200 | 2.0862 | 3.762 | 3.762 | 1.9917 | 2.6341 | 2.3527 |  | 11416.9 |  | 25252 | 2.1432 |  | 3.5796 | 1.5612 |  | 2.0674 | 70.93% | 83.62% | N/A |  |  | N/A | [7 empty] | 4948
Bryant | Bryant | Evolution Series | 9893614 | 280ANV036000 | FE4AN(B,F)005L+UI | HRCU-A-CB | 11.5 | 20 | 13.5 | 35000 | Yes | Centrally Ducted | N/A | N/A | 13340 | 33400 | 33400 | 1.0165 | 2.2149 | 2.2149 | 3.8461 | 4.4194 | 4.4194 |  | 13250 | 31600 | 31800 | 1.9581 | 3.531 | 3.531 | 1.9831 | 2.6228 | 2.6394 |  | 10670 |  | 23600 | 2.0116 |  | 3.3598 | 1.5545 |  | 2.0586 | 70.66% | 74.21% | N/A |  |  | N/A | [7 empty] | 8200
Bryant | Bryant | Evolution Series | 9893699 | 280ANV048000 | FE4ANB006L+UI | HRCU-A-CB | 12 | 18 | 13.5 | 47500 | Yes | Centrally Ducted | N/A | N/A | 24370 | 45500 | 45500 | 1.59 | 2.96 | 2.96 | 4.4919 | 4.505 | 4.505 |  | 23840 | 47500 | 47500 | 2.66 | 5.66 | 5.66 | 2.6283 | 2.4595 | 2.4595 |  | 19230 |  | 38070 | 2.55 |  | 4.97 | 2.2101 | #DIV/0! | 2.2449 | 83.67% | 80.15% | N/A |  |  | N/A | [7 empty] | 9430
Bryant | Bryant | Evolution Series | 9893727 | 280ANV048000 | FE4AN(B,F)005L+UI | HRCU-A-CB | 11 | 17.5 | 12.5 | 46500 | Yes | Centrally Ducted | N/A | N/A | 24800 | 46500 | 46500 | 1.7172 | 3.1968 | 3.1968 | 4.2326 | 4.263 | 4.263 |  | 24300 | 48500 | 48500 | 2.8728 | 6.1128 | 6.1128 | 2.479 | 2.3253 | 2.3253 |  | 19600 |  | 38800 | 2.754 |  | 5.3676 | 2.0858 |  | 2.1185 | 83.44% | 80% | N/A |  |  | N/A | [7 empty] | 9700
Bryant | Bryant | Evolution Series | 9893760 | 280ANV060000 | FE4ANB006L+UI | HRCU-A-CB | 12 | 18 | 12.5 | 56000 | Yes | Centrally Ducted | N/A | N/A | 24600 | 55500 | 55500 | 1.75 | 4.15 | 4.15 | 4.1197 | 3.9194 | 3.9194 |  | 24160 | 52500 | 52500 | 2.93 | 6.91 | 6.91 | 2.4166 | 2.2267 | 2.2267 |  | 19400 |  | 40270 | 2.81 |  | 5.93 | 2.03 |  | 1.99 | 72.56% | 76.7% | N/A |  |  | N/A | [7 empty] | 12230
Carrier | Carrier |  | 9118461 | 38MGRQ18B--3 | Non-Ducted Indoor Units | HMSV-A-CB | 10.3 | 22.5 | 12.5 | 18000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 5760 | 19000 | 23960 | 0.52 | 1.53 | 1.95 | 3.2463 | 3.6394 | 3.601 |  | 5376 | 12000 | 15020 | 0.57 | 1.25 | 1.63 | 2.7641 | 2.8135 | 2.7006 |  | 4752 |  | 13990 | 0.58 |  | 1.91 | 2.4012 |  | 2.1466 | 58.39% | 93.14% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 1030
Carrier | Bryant | Preferred Series | 9118462 | 38MGRQ18B--3 | Non-Ducted Indoor Units | HMSV-A-CB | 10.3 | 22.5 | 12.5 | 18000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 5760 | 19000 | 23960 | 0.52 | 1.53 | 1.95 | 3.2463 | 3.6394 | 3.601 |  | 5376 | 12000 | 15020 | 0.57 | 1.25 | 1.63 | 2.7641 | 2.8135 | 2.7006 |  | 4752 |  | 13990 | 0.58 |  | 1.91 | 2.4012 |  | 2.1466 | 58.39% | 93.14% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 1030
Carrier | Carrier |  | 9118477 | 38MGRQ48E--3 | Non-Ducted Indoor Units | HMSV-A-CB | 10.2 | 22.4 | 12.5 | 48000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7210 | 48000 | 55830 | 1.02 | 3.9 | 4.71 | 2.0716 | 3.607 | 3.4739 |  | 6822 | 29600 | 37900 | 1.07 | 3.21 | 5.31 | 1.8685 | 2.7025 | 2.0918 |  | 6577 |  | 36340 | 1.1 |  | 5.39 | 1.7523 |  | 1.9759 | 65.09% | 95.88% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 1560
Carrier | Bryant | Preferred Series | 9118478 | 38MGRQ48E--3 | Non-Ducted Indoor Units | HMSV-A-CB | 10.2 | 22.4 | 12.5 | 48000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7210 | 48000 | 55830 | 1.02 | 3.9 | 4.71 | 2.0716 | 3.607 | 3.4739 |  | 6822 | 29600 | 37900 | 1.07 | 3.21 | 5.31 | 1.8685 | 2.7025 | 2.0918 |  | 6577 |  | 36340 | 1.1 |  | 5.39 | 1.7523 |  | 1.9759 | 65.09% | 95.88% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | n/A |  | z | [5 empty] | 1560
Carrier | Carrier |  | 9854622 | 38MGRQ24C--3 | Non-Ducted Indoor Units | HMSV-A-CB | 10 | 23 | 12.5 | 24000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 6010 | 23000 | 36220 | 0.72 | 1.72 | 3.04 | 2.4463 | 3.919 | 3.4918 |  | 5721 | 13600 | 25150 | 0.76 | 1.48 | 2.79 | 2.2061 | 2.6931 | 2.6418 |  | 5556 |  | 24170 | 0.84 |  | 3.9 | 1.9385 |  | 1.8163 | 66.73% | 96.1% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 980
Carrier | Bryant | Preferred Series | 9854623 | 38MGRQ24C--3 | Non-Ducted Indoor Units | HMSV-A-CB | 10 | 23 | 12.5 | 24000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 6010 | 23000 | 36220 | 0.72 | 1.72 | 3.04 | 2.4463 | 3.919 | 3.4918 |  | 5721 | 13600 | 25150 | 0.76 | 1.48 | 2.79 | 2.2061 | 2.6931 | 2.6418 |  | 5556 |  | 24170 | 0.84 |  | 3.9 | 1.9385 |  | 1.8163 | 66.73% | 96.1% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 980
Carrier | Bryant | Preferred Series | 9854627 | 38MGRQ30D--3 | Non-Ducted Indoor Units | HMSV-A-CB | 10 | 23.8 | 12.5 | 30000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 6350 | 28000 | 37210 | 0.76 | 2.15 | 3.21 | 2.4487 | 3.8167 | 3.3973 |  | 5834 | 17400 | 27670 | 0.82 | 1.83 | 3.85 | 2.0851 | 2.7866 | 2.1063 |  | 5164 |  | 28220 | 0.86 |  | 4.05 | 1.7598 |  | 2.0421 | 75.84% | 102% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | -550
Carrier | Carrier |  | 9118473 | 38MGRQ36D--3 | Non-Ducted Indoor Units | HMSV-A-CB | 10.5 | 21.5 | 13.5 | 36000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7210 | 36000 | 50540 | 1.04 | 2.77 | 4.66 | 2.0318 | 3.8089 | 3.1785 |  | 7210 | 23200 | 37410 | 1.14 | 2.44 | 5.25 | 1.8535 | 2.7866 | 2.0883 |  | 7210 |  | 36080 | 1.2 |  | 5.39 | 1.7609 |  | 1.9618 | 71.39% | 96.44% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 1330
Carrier | Bryant | Preferred Series | 9118474 | 38MGRQ36D--3 | Non-Ducted Indoor Units | HMSV-A-CB | 10.5 | 21.5 | 13.5 | 36000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7210 | 36000 | 50540 | 1.04 | 2.77 | 4.66 | 2.0318 | 3.8089 | 3.1785 |  | 7210 | 23200 | 37410 | 1.14 | 2.44 | 5.25 | 1.8535 | 2.7866 | 2.0883 |  | 7210 |  | 36080 | 1.2 |  | 5.39 | 1.7609 |  | 1.9618 | 71.39% | 96.44% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 1330
Carrier | Carrier |  | 9892461 | 25VNA024A030 | FE4ANB006L | HRCU-A-CB | 12 | 20.5 | 16 | 25200 | Yes | Centrally Ducted | N/A | N/A | 14500 | 23600 | 23600 | 0.85 | 1.47 | 1.47 | 4.9994 | 4.7051 | 4.7051 |  | 13700 | 24800 | 24800 | 1.54 | 2.96 | 2.96 | 2.6072 | 2.4555 | 2.4555 |  | 10900 |  | 19600 | 1.47 |  | 2.77 | 2.1731 |  | 2.0737 | 83.05% | 79.03% | N/A |  |  | N/A | [7 empty] | 5200
Carrier | Carrier |  | 9892512 | 25VNA024A030 | FE4ANF002L + UI | HRCU-A-CB | 10.5 | 19 | 14.5 | 24200 | Yes | Centrally Ducted | N/A | N/A | 14800.2 | 24000 | 24000 | 0.8585 | 1.4847 | 1.4847 | 5.0524 | 4.7375 | 4.7375 |  | 14000 | 25200 | 25200 | 1.5554 | 2.8886 | 2.8886 | 2.6379 | 2.5567 | 2.5567 |  | 11100 |  | 19800 | 1.4847 |  | 2.7977 | 2.1911 |  | 2.0741 | 82.5% | 78.57% | N/A |  |  | N/A | [7 empty] | 5400
Carrier | Carrier |  | 9892513 | 25VNA024A030 | FE4AN(B,F)003 | HRCU-A-CB | 10.5 | 19.5 | 15 | 24400 | Yes | Centrally Ducted | N/A | N/A | 14600 | 23800 | 23800 | 0.8585 | 1.4847 | 1.4847 | 4.9841 | 4.698 | 4.698 |  | 13850 | 25000 | 25000 | 1.5554 | 2.8886 | 2.8886 | 2.6096 | 2.5364 | 2.5364 |  | 11000 |  | 19800 | 1.4847 |  | 2.7977 | 2.1713 |  | 2.0741 | 83.19% | 79.2% | N/A |  |  | N/A | [7 empty] | 5200
Carrier | Carrier |  | 9892607 | 25VNA036A030 | FE4ANB006L | HRCU-A-CB | 13 | 20.5 | 14.5 | 35000 | Yes | Centrally Ducted | N/A | N/A | 13340 | 33400 | 33400 | 0.95 | 2.07 | 2.07 | 4.1153 | 4.7288 | 4.7288 |  | 13250 | 31600 | 31600 | 1.83 | 3.3 | 3.3 | 2.122 | 2.8064 | 2.8064 |  | 10670 |  | 23600 | 1.88 |  | 3.14 | 1.6633 |  | 2.2027 | 70.66% | 74.68% | N/A |  |  | N/A | [7 empty] | 8000
Carrier | Carrier |  | 9892658 | 25VNA036A030 | FE4ANF002L | HRCU-A-CB | 10.5 | 18.5 | 12.5 | 33000 | Yes | Centrally Ducted | N/A | N/A | 14140.4 | 35404 | 35400 | 1.083 | 2.3598 | 2.3598 | 3.8265 | 4.3969 | 4.3964 |  | 14045 | 33496 | 30600 | 2.0862 | 3.762 | 3.762 | 1.9731 | 2.6094 | 2.3838 |  | 11310.2 |  | 33496 | 2.1432 |  | 3.5796 | 1.5466 |  | 2.7424 | 94.62% | 109.5% | N/A |  |  | N/A | [7 empty] | -2896
Carrier | Carrier |  | 9892659 | 25VNA036A030 | FE4AN(B,F)003L+UI | HRCU-A-CB | 10.5 | 19 | 13 | 33400 | Yes | Centrally Ducted | N/A | N/A | 14273.8 | 35738 | 35600 | 1.083 | 2.3598 | 2.3598 | 3.8626 | 4.4384 | 4.4213 |  | 14177.5 | 33812 | 30200 | 2.0862 | 3.762 | 3.762 | 1.9917 | 2.6341 | 2.3527 |  | 11416.9 |  | 25252 | 2.1432 |  | 3.5796 | 1.5612 |  | 2.0674 | 70.93% | 83.62% | N/A |  |  | N/A | [7 empty] | 4948
Carrier | Carrier |  | 9892665 | 25VNA036A030 | FE4AN(B,F)005L+UI | HRCU-A-CB | 11.5 | 20 | 13.5 | 35000 | Yes | Centrally Ducted | N/A | N/A | 13340 | 33400 | 33400 | 1.0165 | 2.2149 | 2.2149 | 3.8461 | 4.4194 | 4.4194 |  | 13250 | 31600 | 31800 | 1.9581 | 3.531 | 3.531 | 1.9831 | 2.6228 | 2.6394 |  | 10670 |  | 23600 | 2.0116 |  | 3.3598 | 1.5545 |  | 2.0586 | 70.66% | 74.21% | N/A |  |  | N/A | [7 empty] | 8200
Carrier | Carrier |  | 9892751 | 25VNA048A030 | FE4ANB006L | HRCU-A-CB | 12 | 18 | 13.5 | 47500 | Yes | Centrally Ducted | N/A | N/A | 24370 | 45500 | 45500 | 1.59 | 2.96 | 2.96 | 4.4919 | 4.505 | 4.505 |  | 23840 | 47500 | 47500 | 2.66 | 5.66 | 5.66 | 2.6283 | 2.4595 | 2.4595 |  | 19230 |  | 38070 | 2.55 |  | 4.97 | 2.2101 | #DIV/0! | 2.2449 | 83.67% | 80.15% | N/A |  |  | N/A | [7 empty] | 9430
Carrier | Carrier |  | 9892779 | 25VNA048A030 | FE4AN(B,F)005L+UI | HRCU-A-CB | 11 | 17.5 | 12.5 | 46500 | Yes | Centrally Ducted | N/A | N/A | 24800 | 46500 | 46500 | 1.7172 | 3.1968 | 3.1968 | 4.2326 | 4.263 | 4.263 |  | 24300 | 48500 | 48500 | 2.8728 | 6.1128 | 6.1128 | 2.479 | 2.3253 | 2.3253 |  | 19600 |  | 38800 | 2.754 |  | 5.3676 | 2.0858 |  | 2.1185 | 83.44% | 80% | N/A |  |  | N/A | [7 empty] | 9700
Carrier | Carrier |  | 9892813 | 25VNA060A030 | FE4ANB006L | HRCU-A-CB | 12 | 18 | 12.5 | 56000 | Yes | Centrally Ducted | N/A | N/A | 24600 | 55500 | 55500 | 1.75 | 4.15 | 4.15 | 4.1197 | 3.9194 | 3.9194 |  | 24160 | 52500 | 52500 | 2.93 | 6.91 | 6.91 | 2.4166 | 2.2267 | 2.2267 |  | 19400 |  | 40270 | 2.81 |  | 5.93 | 2.03 |  | 1.99 | 72.56% | 76.7% | N/A |  |  | N/A | [7 empty] | 12230
Carrier | Bryant | Evolution Series | 7029861 | 280ANV060000 | FE4ANB006L | N/A | 12 | 18 | 12.7 |  | Yes | Centrally Ducted | N/A | N/A | 24690 | 55500 | 55500 | 1.75 | 4.2165 | 4.2165 | 4.14 | 3.86 | 3.86 |  | 24160 | 52500 | 52500 | 2.93 | 6.9351 | 6.9351 | 2.42 | 2.22 | 2.22 |  | 19480 |  | 40270 | 2.81 |  | 5.93 | 2.03 |  | 1.99 | 72.56% | 76.7% | N/A |  |  | N/A |  | z | [5 empty] | 12230
Carrier | Bryant | Evolution Series | 7029862 | 280ANV036000 | FE4ANB006L | N/A | 13 | 20.5 | 14.5 |  | Yes | Centrally Ducted | N/A | N/A | 13340 | 33400 | 33400 | 0.95 | 2.23 | 2.23 | 4.12 | 4.4 | 4.4 |  | 13250 | 31600 | 31600 | 1.83 | 3.65 | 3.65 | 2.12 | 2.54 | 2.54 |  | 10670 |  | 23600 | 1.88 |  | 3.14 | 1.66 |  | 2.2 | 70.66% | 74.68% | N/A |  |  | N/A |  | z | [5 empty] | 8000
Carrier | Bryant | Evolution Series | 7029863 | 280ANV048000 | FE4ANB006L | N/A | 12.5 | 18.3 | 13.5 |  | Yes | Centrally Ducted | N/A | N/A | 24370 | 45500 | 45500 | 1.59 | 3.2386 | 3.2386 | 4.49 | 4.12 | 4.12 |  | 23840 | 47500 | 47500 | 2.66 | 3.35 | 6.27 | 2.6283 | 2.22 | 2.22 |  | 19230 |  | 38070 | 2.55 |  | 4.97 | 2.21 |  | 2.24 | 83.67% | 80.15% | N/A |  |  | N/A |  | z | [5 empty] | 9430
Carrier | Bryant | Evolution Series | 7029864 | 280ANV024000 | FE4ANB006L | N/A | 13 | 20.5 | 16 |  | Yes | Centrally Ducted | N/A | N/A | 14510 | 23600 | 24800 | 0.85 | 1.47 | 1.47 | 5.01 | 4.7 | 4.7 |  | 13740 | 24800 | 24800 | 1.54 | 2.86 | 2.86 | 2.62 | 2.54 | 2.54 |  | 10930 |  | 19630 | 1.47 |  | 2.77 | 1.73 |  | 2.08 | 79.15% | 79.15% | N/A |  |  | N/A |  | z | [5 empty] | 5170
Carrier | Bryant | Preferred Series | 8856652 | 38MAQB18R--3 | 619REQ018DBMA | HRCU-A-CB | 10.5 | 19.6 | 12.5 | 16500 | Yes | Ductless | Single-zone | Ducted Indoor Units | 5500 | 18000 | 19000 | 0.38842 | 1.4777 | 1.7348 | 4.15 | 3.57 | 3.21 |  | 5500 | 12200 | 18000 | 0.5069 | 1.4077 | 2.4652 | 3.18 | 2.54 | 2.14 |  | 5500 |  | 18000 | 0.67729 |  | 3.0146 | 2.38 |  | 1.75 | 94.74% | 100% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 0
Carrier | Carrier |  | 8856653 | 38MAQB18R--3 | 40MBQB18D--3 | HRCU-A-CB | 10.5 | 19.6 | 12.5 | 16500 | Yes | Ductless | Single-zone | Ducted Indoor Units | 5500 | 18000 | 19000 | 0.38842 | 1.4777 | 1.7348 | 4.15 | 3.57 | 3.21 |  | 5500 | 12200 | 18000 | 0.5069 | 1.4077 | 2.4652 | 3.18 | 2.54 | 2.14 |  | 5500 |  | 18000 | 0.67729 |  | 3.0146 | 2.38 |  | 1.75 | 94.74% | 100% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 0
Carrier | Bryant | Preferred Series | 8738643 | 38MAQB24R--3 | 619PEQ024BBMA | HRCU-A-CB-O | 10.3 | 20.5 | 13 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5500 | 24000 | 29680 | 0.323 | 2.26 | 3.19 | 4.98 | 3.1 | 2.73 |  | 4700 | 15400 | 25710 | 0.31 | 1.71 | 3.87 | 4.42 | 2.64 | 1.95 |  | 2856 |  | 24030 | 0.295 |  | 3.98 | 2.83 |  | 1.77 | 80.96% | 93.47% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z | [5 empty] | 1680
Carrier | Bryant | Preferred Series | 8738645 | 38MAQB12R--3 | 619PEQ012BBMA | HRCU-A-CB-O | 12 | 22.5 | 12.5 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4000 | 11800 | 14980 | 0.183 | 0.971 | 1.39 | 6.42 | 3.56 | 3.16 |  | 3250 | 7800 | 13580 | 0.176 | 0.865 | 1.76 | 5.412 | 2.64 | 2.26 |  | 2030 |  | 12010 | 0.141 |  | 1.78 | 4.22 |  | 1.98 | 80.17% | 88.44% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z | [5 empty] | 1570
Carrier | Bryant | Preferred Series | 8738646 | 38MAQB09R--3 | 619PEQ009BBMA | HRCU-A-CB-O | 11.2 | 25 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3500 | 10900 | 14980 | 0.15 | 0.81 | 1.39 | 6.88 | 3.94 | 3.16 |  | 2750 | 6900 | 13580 | 0.145 | 0.737 | 1.76 | 5.5585 | 2.74 | 2.26 |  | 1907 |  | 10900 | 0.13 |  | 1.613 | 4.3 |  | 1.98 | 72.76% | 80.27% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z | [5 empty] | 2680
Carrier | Bryant | Preferred Series | 8856654 | 38MAQB18R--3 | 619REQ018CBMA | HRCU-A-CB-O | 10.5 | 20 | 12.5 | 16000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4700 | 18000 | 24630 | 0.27 | 1.53 | 2.53 | 5.1 | 3.43 | 2.85 |  | 3750 | 12000 | 20590 | 0.25 | 1.38 | 2.93 | 4.3962 | 2.55 | 2.06 |  | 2660 |  | 19010 | 0.23 |  | 3.18 | 3.39 |  | 1.75 | 77.18% | 92.33% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z | [5 empty] | 1580
Carrier | Bryant |  | 10056166 | 38MAQB18R--3 | 40MBCQ18---3 | HRCU-A-CB-O | 10.5 | 20 | 12.5 | 16000 | Yes | Ductless | Singlezone | Non-ducted indoor units (Mini-splits) | 4700 | 18000 | 24630 | 0.27 | 1.53 | 2.53 | 5.1 | 3.43 | 2.85 |  | 3750 | 12000 | 20590 | 0.25 | 1.38 | 2.93 | 4.3962 | 2.55 | 2.06 |  | 2660 |  | 19010 | 0.23 |  | 3.18 | 3.39 |  | 1.75 | 77.18% | 92.33% | Integrated | 3 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. |  |  | z
Carrier | Bryant |  | 10056158 | 38MAQB18R--3 | 40MBDQ18---3 | HRCU-A-CB | 11 | 19.9 | 12.5 | 16500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5500 | 19000 | 19000 | 0.38842 | 1.9005 | 1.7348 | 4.15 | 2.93 | 3.21 |  | 5500 | 13400 | 20200 | 0.5069 | 1.4492 | 2.7665 | 3.18 | 2.71 | 2.14 |  | 5500 |  | 19000 | 0.67729 |  | 3.182 | 2.38 |  | 1.75 | 100% | 94.06% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. |  |  | z
Carrier | Bryant |  | 10056159 | 38MAQB24R--3 | 40MBDQ24---3 | HRCU-A-CB | 12.5 | 20.5 | 12.5 | 24000 | Yes | Ductless | Singlezone | Non-ducted indoor units (Mini-splits) | 6000 | 24000 | 29250 | 0.42373 | 1.8414 | 2.7389 | 4.15 | 3.82 | 3.13 | 6000 | 6000 | 17300 | 25400 | 0.55299 | 1.9806 | 3.4787 | 3.18 | 2.56 | 2.14 | 6000 | 6000 |  | 24000 | 0.73887 |  | 3.8437 | 2.38 |  | 1.83 | 82.05% | 94.49% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. |  |  | z | [5 empty] | 1400
Carrier | Carrier |  | 9854626 | 38MGRQ30D--3 | Non-Ducted Indoor Units | HMSV-A-CB | 10 | 23.8 | 12.5 | 30000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 6350 | 28000 | 37210 | 0.76 | 2.15 | 3.21 | 2.4487 | 3.8167 | 3.3973 |  | 5834 | 17400 | 27670 | 0.82 | 1.83 | 3.85 | 2.0852 | 2.7866 | 2.1063 |  | 5164 |  | 28220 | 0.86 |  | 4.05 | 1.7598 |  | 2.0421 | 75.84% | 102% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z |  |  | 1.367 | 1.166 | 1.835 | 2752
Carrier | Carrier |  | 7992954 | 38GRQB09---301 | 40GRQB09H--301 | HRCU-A-CB-O | 10.3 | 30.5 | 15.7 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.4994 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.44 | 1.5 | 1.99 | 0
Carrier | Carrier |  | 7992956 | 38GRQB12---301 | 40GRQB12H--301 | HRCU-A-CB-O | 10.3 | 23 | 12.7 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5003 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 2.14 | 1.466 | 2.113 | 5376
Carrier | Carrier |  | 7992958 | 38GRQB18---301 | 40GRQB18H--301 | HRCU-A-CB-O | 10.3 | 21 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.1427 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 |  |  |  | 2680
Carrier | Carrier |  | 8738635 | 38MAQB09R--3 | 40MAQB09B--3 | HRCU-A-CB-O | 11.2 | 25 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3500 | 10900 | 14980 | 0.15 | 0.81 | 1.39 | 6.88 | 3.94 | 3.16 |  | 2750 | 6900 | 13580 | 0.145 | 0.737 | 1.76 | 5.5585 | 2.74 | 2.26 |  | 1907 |  | 10900 | 0.13 |  | 1.613 | 4.3 |  | 1.98 | 72.76% | 80.27% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z | [5 empty] | 1570
Carrier | Carrier |  | 8738636 | 38MAQB12R--3 | 40MAQB12B--3 | HRCU-A-CB-O | 12 | 22.5 | 12.5 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4000 | 11800 | 14980 | 0.183 | 0.971 | 1.39 | 6.42 | 3.56 | 3.16 |  | 3250 | 7800 | 13580 | 0.176 | 0.865 | 1.76 | 5.412 | 2.64 | 2.26 |  | 2030 |  | 12010 | 0.141 |  | 1.78 | 4.22 |  | 1.98 | 80.17% | 88.44% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z | [5 empty] | 1680
Carrier | Carrier |  | 8738638 | 38MAQB24R--3 | 40MAQB24B--3 | HRCU-A-CB-O | 10.3 | 20.5 | 13 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5500 | 24000 | 29680 | 0.323 | 2.26 | 3.19 | 4.98 | 3.1 | 2.73 |  | 4700 | 15400 | 25710 | 0.31 | 1.71 | 3.87 | 4.4435 | 2.64 | 1.95 |  | 2856 |  | 24030 | 0.295 |  | 3.98 | 2.83 |  | 1.77 | 80.96% | 93.47% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z | [5 empty] | 1580
Carrier | Carrier |  | 8856655 | 38MAQB18R--3 | 40MBQB18C--3 | HRCU-A-CB-O | 10.5 | 20 | 12.5 | 16000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4700 | 18000 | 24630 | 0.27 | 1.53 | 2.53 | 5.1 | 3.43 | 2.85 |  | 3750 | 12000 | 20590 | 0.25 | 1.38 | 2.93 | 4.3962 | 2.55 | 2.06 |  | 2660 |  | 19010 | 0.23 |  | 3.18 | 3.39 |  | 1.75 | 77.18% | 92.33% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | N/A |  | z |  |  | 1.36 | 2.93 | 2.5 | 3760
Daikin AC (Americas), Inc | Daikin | MXS Series | 8103542 | 2MXS18NMVJU | CTXS09HVJU+CTXS09LVJU | HMSV-A-CB | 10.7 | 18.9 | 12.5 | 18000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 4900 | 18900 | 25000 | 0.29 | 1.26 | 1.69 | 4.94 | 4.4 | 4.34 |  | 3800 | 12780 | 16910 | 0.29 | 1.11 | 1.49 | 3.8404 | 3.37 | 3.33 |  | 3190 |  | 13150 | 0.29 |  | 1.4 | 3.21 |  | 2.76 | 52.6% | 77.76% | Accessory (KEH063A4E) |  | Temp. below 23 degrees | 0 | 2910 | z | 11580 | 0.29 | 2.39 | 3.42 | 2.05 | 5420
Daikin AC (Americas), Inc | Daikin | MXS Series | 8103869 | 3MXS24NMVJU | CTXS07LVJU+CTXS09LVJU+CTXS09LVJU | HMSV-A-CB | 12.5 | 17.9 | 12.7 | 24000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 8500 | 24000 | 36000 | 0.43 | 1.46 | 2.97 | 5.79 | 4.82 | 3.55 |  | 6570 | 16230 | 24350 | 0.43 | 1.29 | 2.62 | 4.478 | 3.69 | 2.72 |  | 5500 |  | 18930 | 0.43 |  | 2.46 | 3.75 |  | 2.26 | 52.58% | 77.74% | Accessory (KEH063A4E) |  | Temp. below 23 degrees | 0 | 5020 | z | 16670 | 0.43 |  |  |  | 4550
Daikin AC (Americas), Inc | Daikin | MXL Aurora Series | 8849535 | 2MXL18QMVJU | 40GRQB18H--301 | HMSV-A-CB | 10.3 | 17 | 12.7 | 18000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7710 | 18940 | 36000 | 0.47 | 1.32 | 3.17 | 4.81 | 4.21 | 3.33 |  | 5020 | 12330 | 23480 | 0.41 | 1.15 | 2.77 | 3.5885 | 3.14 | 2.48 |  | 4050 |  | 18930 | 0.39 |  | 2.62 | 3.04 |  | 2.12 | 52.58% | 80.62% | N/A |  |  | N/A | [7 empty] | 5180
Daikin AC (Americas), Inc | Daikin | MXL Aurora Series | 8849539 | 3MXL24QMVJU | CTXS07LVJU+FTXS09LVJU+FTXS09LVJU | HMSV-A-CB | 12.5 | 17.9 | 12.7 | 24000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7720 | 24000 | 41000 | 0.44 | 1.54 | 3.52 | 5.14 | 4.57 | 3.41 |  | 5030 | 15670 | 26780 | 0.38 | 1.35 | 3.08 | 3.8795 | 3.4 | 2.55 |  | 4060 |  | 21600 | 0.36 |  | 2.92 | 3.31 |  | 2.17 | 52.68% | 80.66% | N/A |  |  | N/A | [7 empty] | 3800
Daikin AC (Americas), Inc | Daikin | DZ20VC | 10324709 | DZ20VC0241B | CA*F3642*6D*+MBVC1200**-1A*+TXV | HRCU-A-CB | 10 | 21 | 13 | 23400 | Yes | Centrally Ducted | N/A | N/A | 5507 | 23600 | 23600 | 0.33 | 1.87 | 1.87 | 4.91 | 3.7 | 3.7 |  | 3943 | 13915 | 15200 | 0.338 | 1.487 | 1.82 | 3.419 | 2.74 | 2.45 |  | 1650 |  | 11400 | 0.296 |  | 1.6 | 1.63 |  | 2.09 | 48.31% | 75% | N/A |  |  | N/A | [7 empty] | 6700
Daikin AC (Americas), Inc | Daikin | DZ20VC | 10324711 | DZ20VC0361B | CA*F3743*6D*+MBVC1600**-1A*+TXV | HRCU-A-CB | 10 | 21 | 14 | 35400 | Yes | Centrally Ducted | N/A | N/A | 13438 | 35000 | 35000 | 0.721 | 2.48 | 2.48 | 5.46 | 4.14 | 4.14 |  | 8580 | 18365 | 28800 | 0.722 | 2.092 | 3.72 | 3.4829 | 2.57 | 2.27 |  | 5135 |  | 22100 | 0.722 |  | 3.48 | 2.08 |  | 1.86 | 63.14% | 76.74% | N/A |  |  | N/A | [7 empty] | 8000
Daikin AC (Americas), Inc | Daikin | DZ20VC | 10324713 | DZ20VC0481B | CA*F4961*6D*+MBVC2000**-1A*+TXV | HRCU-A-CB | 10 | 20 | 13 | 46500 | Yes | Centrally Ducted | N/A | N/A | 13274 | 45500 | 45500 | 0.796 | 3.42 | 3.42 | 4.88 | 3.9 | 3.9 |  | 8394 | 28254 | 34000 | 0.766 | 2.926 | 4.15 | 3.2117 | 2.83 | 2.4 |  | 5390 |  | 26000 | 0.722 |  | 3.87 | 2.19 |  | 1.97 | 57.14% | 76.47% | N/A |  |  | N/A | [7 empty] | 8000
Daikin AC (Americas), Inc | Daikin | DZ20VC | 10324715 | DZ20VC0601B | CA*F4961*6D*+MBVC2000**-1A*+TXV | HRCU-A-CB | 10 | 20 | 12.5 | 52500 | Yes | Centrally Ducted | N/A | N/A | 15848 | 50000 | 50000 | 0.891 | 3.76 | 3.76 | 5.21 | 3.9 | 3.9 |  | 9302 | 32293 | 34000 | 0.92 | 3.466 | 4.07 | 2.96 | 2.73 | 2.45 |  | 5407 |  | 26000 | 0.901 |  | 3.85 | 1.76 |  | 1.98 | 52% | 76.47% | N/A |  |  | N/A |  |  |  |  | 1.49 |  | 1.46 | 2710
Daikin AC (Americas), Inc | Daikin | Quaternity Series | 3208521 | RXG09HVJU | FTXG09HVJU | HRCU-A-CB-O | 11 | 26.1 | 15.8 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4668 | 12000 | 18670 | 0.224 | 0.78 | 1.94 | 6.11 | 4.51 | 2.82 |  | 3003 | 8100 | 12170 | 0.194 | 0.72 | 1.68 | 4.54 | 3.3 | 2.12 |  | 2330 |  | 9460 | 0.182 |  | 1.57 | 3.75 |  | 1.77 | 50.67% | 77.73% | Accessory (KEH041A45) |  | Temp. below 23 degrees | -4 |  | z | 7430 |  | 1.58 |  | 1.46 | 2880
Daikin AC (Americas), Inc | Daikin | Quaternity Series | 3208522 | RXG12HVJU | FTXG12HVJU | HRCU-A-CB-O | 10.55 | 24.2 | 14 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4668 | 16000 | 19130 | 0.224 | 1.16 | 2.14 | 6.11 | 4.04 | 2.62 |  | 3003 | 10400 | 12920 | 0.192 | 0.98 | 1.78 | 4.58 | 3.1 | 2.13 |  | 2330 |  | 10040 | 0.181 |  | 1.67 | 3.77 |  | 1.76 | 52.48% | 77.71% | Accessory (KEH041A45) |  | Temp. below 23 degrees | -4 |  | z | 7880 |  | 1.67 |  | 1.54 | 3190
Daikin AC (Americas), Inc | Daikin | Quaternity Series | 3208523 | RXG15HVJU | FTXG15HVJU | HRCU-A-CB-O | 10 | 21 | 12.9 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4668 | 18000 | 21280 | 0.234 | 1.32 | 2.16 | 5.85 | 3.99 | 2.89 |  | 3003 | 11100 | 14340 | 0.203 | 1.08 | 1.87 | 4.34 | 3 | 2.25 |  | 2330 |  | 11150 | 0.19 |  | 1.75 | 3.59 |  | 1.87 | 52.4% | 77.75% | Accessory (KEH041A45) |  | Temp. below 23 degrees | -4 |  | z | 8750 |  | 0.82 | 3.66 | 2.18 | 1497
Daikin AC (Americas), Inc | Daikin | LV Series | 5265753 | RXS09LVJU | FTXS09LVJU | HRCU-A-CB-O | 12.5 | 24.5 | 15.3 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4400 | 12000 | 15600 | 0.22 | 0.79 | 1.27 | 5.99 | 4.45 | 3.6 |  | 2408 | 6520 | 8465 | 0.15 | 0.55 | 0.88 | 4.72 | 3.48 | 2.81 |  | 1982 |  | 6968 | 0.14 |  | 0.84 | 4.08 |  | 2.43 | 44.67% | 82.32% | Accessory (KEH041A41) |  | Temp. below 23 degrees | 0 | 1727 | z | 6070 | 0.14 | 0.82 | 3.94 | 2.52 | 1729
Daikin AC (Americas), Inc | Daikin | LV Series | 5265755 | RXS12LVJU | FTXS12LVJU | HRCU-A-CB-O | 12.5 | 23 | 12.8 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4800 | 14400 | 18000 | 0.22 | 0.97 | 1.27 | 6.53 | 4.35 | 4.15 |  | 2593 | 7816 | 9780 | 0.15 | 0.67 | 0.88 | 5.08 | 3.4 | 3.25 |  | 2135 |  | 8051 | 0.14 |  | 0.84 | 4.39 |  | 2.81 | 44.73% | 82.32% | Accessory (KEH041A41) |  | Temp. below 23 degrees | 0 | 1860 | z | 7013 | 0.14 | 1.06 | 2.64 | 2.41 | 2142
Daikin AC (Americas), Inc | Daikin | LV Series | 5265756 | RXS15LVJU | FTXS15LVJU | HRCU-A-CB-O | 11.6 | 20.6 | 14.4 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5800 | 18000 | 22300 | 0.39 | 1.32 | 1.64 | 4.35 | 4 | 3.97 |  | 3149 | 9780 | 12114 | 0.27 | 0.92 | 1.14 | 3.4 | 3.13 | 3.11 |  | 2592 |  | 9972 | 0.26 |  | 1.09 | 2.94 |  | 2.69 | 44.72% | 82.32% | Accessory (KEH041A42) |  | Temp. below 23 degrees | 0 | 2258 | z | 8687 | 0.25 | 1.36 | 2.53 | 2.24 | 2561
Daikin AC (Americas), Inc | Daikin | LV Series | 5265757 | RXS18LVJU | FTXS18LVJU | HRCU-A-CB-O | 11 | 20.3 | 12.7 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5800 | 21600 | 26700 | 0.41 | 1.71 | 2.12 | 4.17 | 3.7 | 3.7 |  | 3149 | 11725 | 14485 | 0.28 | 1.19 | 1.47 | 3.26 | 2.89 | 2.89 |  | 2592 |  | 11924 | 0.27 |  | 1.4 | 2.82 |  | 2.49 | 44.66% | 82.32% | Accessory (KEH041A42) |  | Temp. below 23 degrees | 0 | 2258 | z | 10387 | 0.26 | 1.77 | 2.59 | 2.03 | 3013
Daikin AC (Americas), Inc | Daikin | LV Series | 5265758 | RXS24LVJU | FTXS24LVJU | HRCU-A-CB-O | 10.6 | 20 | 12.5 | 21400 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7800 | 25400 | 31400 | 0.54 | 2.21 | 2.75 | 4.25 | 3.37 | 3.34 |  | 4260 | 13781 | 17041 | 0.37 | 1.54 | 1.91 | 3.34 | 2.63 | 2.61 |  | 3507 |  | 14028 | 0.36 |  | 1.82 | 2.89 |  | 2.26 | 44.68% | 82.32% | Accessory (KEH041A43) |  | Temp. below 23 degrees | 0 | 3055 | z | 12220 | 0.35 |  |  |  | 1501
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849330 | RXL15QMVJU | FTX15NMVJU | HRCU-A-CB-O | 12.5 | 20 | 13 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5814 | 18295 | 24566 | 0.39 | 1.341 | 2.307 | 4.37 | 4 | 3.12 |  | 3784 | 11904 | 19755 | 0.341 | 1.17 | 2.361 | 3.25 | 2.98 | 2.45 |  | 2958 |  | 18254 | 0.32 |  | 2.361 | 2.71 |  | 2.27 | 74.31% | 92.4% | N/A |  |  | N/A |  | z | [5 empty] | 1399
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849445 | RXL15QMVJU | FVXS15NVJU | HRCU-A-CB-O | 11.3 | 20 | 12.5 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5814 | 18056 | 23884 | 0.34 | 1.401 | 1.809 | 5.01 | 3.78 | 3.87 |  | 3784 | 11751 | 19414 | 0.297 | 1.222 | 2.105 | 3.73 | 2.82 | 2.7 |  | 2958 |  | 18015 | 0.279 |  | 2.198 | 3.11 |  | 2.4 | 75.43% | 92.79% | N/A |  |  | N/A |  | z | [5 empty] | 1058
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849458 | RXL12QMVJU | FTX12NMVJU | HRCU-A-CB-O | 12 | 20 | 12.5 | 10900 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4446 | 13679 | 18766 | 0.24 | 1.026 | 1.562 | 5.43 | 3.91 | 3.52 |  | 2893 | 8902 | 15388 | 0.21 | 0.895 | 1.789 | 4.04 | 2.92 | 2.52 |  | 2262 |  | 14330 | 0.197 |  | 1.86 | 3.37 |  | 2.26 | 76.36% | 93.12% | N/A |  |  | N/A |  | z | [5 empty] | 1017
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849459 | RXL09QMVJU | FVXS09NVJU | HRCU-A-CB-O | 11.7 | 20 | 12.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4446 | 10089 | 14330 | 0.24 | 0.721 | 1.356 | 5.43 | 4.1 | 3.1 |  | 2893 | 6565 | 11082 | 0.21 | 0.629 | 1.378 | 4.04 | 3.06 | 2.36 |  | 2262 |  | 10065 | 0.197 |  | 1.384 | 3.37 |  | 2.13 | 70.24% | 90.82% | N/A |  |  | N/A |  | z | [5 empty] | 1218
Daikin AC (Americas), Inc | Daikin | Aurora Series | 8849533 | RXL09QMVJU | FTX09NMVJU | HRCU-A-CB-O | 12.5 | 20 | 12.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4446 | 10942 | 16036 | 0.23 | 0.761 | 1.701 | 5.67 | 4.21 | 2.76 |  | 2893 | 7121 | 12136 | 0.201 | 0.664 | 1.642 | 4.22 | 3.14 | 2.17 |  | 2262 |  | 10918 | 0.189 |  | 1.623 | 3.51 |  | 1.97 | 68.08% | 89.96% | N/A |  |  | N/A |  | z | [5 empty] | 1880
Daikin AC (Americas), Inc | Daikin | Vista | 9966569 | RX09QMVJU | FFQ09Q2VJU | HRCU-A-CB-O | 11.7 | 20.9 | 13 | 9100 | Yes | Ductless | Single-zone | Non-ducted indoor units (Cassette) | 4600 | 10000 | 14000 | 0.25 | 0.64 | 1.15 | 5.4 | 4.59 | 3.57 |  | 3150 | 5830 | 8150 | 0.22 | 0.45 | 0.81 | 4.18 | 3.8 | 2.94 |  | 2420 |  | 6270 | 0.21 |  | 0.76 | 3.38 |  | 2.42 | 44.79% | 76.93% | accessory (KEH067A41E) | 140 | Temp below 23 degrees | N/A | [7 empty] | 2260
Daikin AC (Americas), Inc | Daikin | Vista | 9966684 | RX12QMVJU | FFQ12Q2VJU | HRCU-A-CB-O | 11.2 | 20.2 | 12.5 | 10800 | Yes | Ductless | Single-zone | Non-ducted indoor units (Cassette) | 4600 | 13500 | 16800 | 0.25 | 0.99 | 1.45 | 5.4 | 4.02 | 3.39 |  | 3150 | 7850 | 9760 | 0.22 | 0.7 | 1.03 | 4.18 | 3.28 | 2.76 |  | 2420 |  | 7500 | 0.21 |  | 0.96 | 3.38 |  | 2.28 | 44.64% | 76.84% | accessory (KEH067A41E) | 140 | Temp. below 23 degrees | N/A | [7 empty] | 2190
Daikin AC (Americas), Inc | Daikin | Vista | 9966775 | RX15QMVJU | FFQ15Q2VJU | HRCU-A-CB-O | 11 | 20.7 | 12.5 | 14400 | Yes | Ductless | Single-zone | Non-ducted indoor units (Cassette) | 5200 | 16200 | 16300 | 0.31 | 1.24 | 1.3 | 4.916 | 3.8288 | 3.6747 |  | 3570 | 9400 | 9460 | 0.27 | 0.87 | 0.92 | 3.8751 | 3.1665 | 3.0135 |  | 2740 |  | 7270 | 0.26 |  | 0.86 | 3.08 |  | 2.47 | 44.6% | 76.85% | accessory (KEH063A4E) | 140 | Temp below 23 degrees | N/A | [7 empty] | 2910
Daikin AC (Americas), Inc | Daikin | Vista | 10318063 | RX18QMVJU | FFQ18Q2VJU | HRCU-A-CB-O | 10.1 | 19.3 | 12.5 | 17400 | Yes | Ductless | Single-zone | Non-ducted indoor units (Cassette) | 5400 | 21600 | 21800 | 0.37 | 1.88 | 1.92 | 4.2773 | 3.3672 | 3.3276 |  | 3640 | 12490 | 12610 | 0.33 | 1.33 | 1.36 | 3.24 | 2.74 | 2.72 |  | 2800 |  | 9700 | 0.31 |  | 1.27 | 2.6471 |  | 2.2384 | 44.5% | 76.92% | accessory (KEH063A4E) | 140 | Temp below 23 degrees | N/A | [7 empty] | 800
Electrolux Home Products | Frigidaire |  | 8718583 | FFHP093CS2 | FFHP093WS2 | HRCU-A-CB-O | 10.5 | 23 | 14 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1900 | 11000 | 12000 | 0.16 | 1.02 | 1.2 | 3.4802 | 3.1606 | 2.9307 |  | 4100 | 7800 | 11000 | 0.43 | 0.83 | 1.37 | 2.7944 | 2.7542 | 2.3531 |  | 3300 |  | 10200 | 0.46 |  | 1.45 | 2.1025 |  | 2.0616 | 85% | 92.73% | Integrated | 72 | If outdoor temperature is lower than temperature setting of Pan Heater, the Pan Heater will be activated. | N/A | [7 empty] | 2200
Electrolux Home Products | Frigidaire |  | 8718584 | FFHP123CS2 | FFHP123WS2 | HRCU-A-CB-O | 10.1 | 22 | 12.5 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2400 | 13000 | 14000 | 0.4 | 1.1 | 1.4 | 1.7584 | 3.4636 | 2.9307 |  | 4000 | 7500 | 11000 | 0.42 | 0.84 | 1.34 | 2.7912 | 2.6167 | 2.4058 |  | 3200 |  | 8800 | 0.45 |  | 1.27 | 2.0841 |  | 2.0307 | 62.86% | 80% | Integrated | 72±5% | If outdoor temperature is lower than temperature setting of Pan Heater, the Pan Heater will be activated. | N/A | [7 empty] | 2262.2
Electrolux Home Products | Frigidaire |  | 8718585 | FFHP183CS2 | FFHP183WS2 | HRCU-A-CB-O | 10 | 20 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7340 | 8806.37 | 19315.3 | 0.58 | 0.633 | 2.468 | 3.7089 | 4.0772 | 2.2937 |  | 7120 | 12470.86 | 18687.5 | 0.61 | 1.37 | 2.613 | 3.4208 | 2.6678 | 2.096 |  | 6870 |  | 16425.3 | 0.63 |  | 2.622 | 3.1959 |  | 1.8359 | 85.04% | 87.89% | Integrated | 160±5% | If outdoor temperature is lower than temperature setting of Pan Heater, the Pan Heater will be activated. | N/A | [7 empty] | 895
EMERSON QUIET KOOL CO.,LTD | EMERSON QUIET KOOL | Max Heat RAC Series | 10298956 | HP-25EACH09R2O | HP-25EACH09R2I | HRCU-A-CB-O | 11.2 | 25 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4185 | 10900 | 15365 | 0.23319 | 0.82762 | 1.4251 | 5.2598 | 3.8598 | 3.1599 |  | 6900 | 6900 | 12575 | 0.73806 | 0.73806 | 1.852 | 2.7399 | 2.7399 | 1.9899 |  | 10720 |  | 11680 | 1.7621 |  | 1.945 | 1.7829 |  | 1.7599 | 76.02% | 92.88% | Integrated | 150 | Temp. below 0 degrees | N/A | [7 empty] | 2130
EMERSON QUIET KOOL CO.,LTD | EMERSON QUIET KOOL | Max Heat RAC Series | 10298957 | HP-22EACH12R2O | HP-22EACH12R2I | HRCU-A-CB-O | 12 | 22.5 | 13 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4110 | 11800 | 15570 | 0.22728 | 0.97694 | 1.3955 | 5.3 | 3.54 | 3.27 |  | 7800 | 7800 | 14140 | 0.86593 | 0.86593 | 1.8752 | 2.64 | 2.64 | 2.21 |  | 11800 |  | 12010 | 1.9762 |  | 1.9555 | 1.7499 |  | 1.7999 | 77.14% | 84.94% | Integrated | 150 | Temp. below 0 degrees | N/A | [7 empty] | 1120
EMERSON QUIET KOOL CO.,LTD | EMERSON QUIET KOOL | Max Heat RAC Series | 10298959 | HP-20EACH24R2O | HP-20EACH24R2I | HRCU-A-CB-O | 11.5 | 20.5 | 13 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 11795 | 24000 | 29680 | 0.68726 | 1.9539 | 3.1981 | 5.03 | 3.6 | 2.72 |  | 15400 | 15400 | 25710 | 1.6353 | 1.6353 | 3.8642 | 2.76 | 2.76 | 1.95 |  | 23260 |  | 24590 | 3.8298 |  | 3.9817 | 1.78 |  | 1.81 | 82.85% | 95.64% | Integrated | 150 | Temp. below 0 degrees | N/A | [7 empty] | 6502
Friedrich Air Conditioning | Friedrich | J-Series | 8915232 | MR24DY3JMA | Non-Ducted | HMSV-A-CB | 10.6 | 21.7 | 13.5 | 20000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 9240 | 24000 | 28800 | 1.092 | 1.8 | 2.52 | 2.4798 | 3.9076 | 3.3494 |  | 5580 | 14500 | 21097 | 0.945 | 1.56 | 1.71 | 1.7305 | 2.7241 | 3.6157 |  | 4332 |  | 14595 | 0.917 |  | 1.65 | 1.3845 |  | 2.5923 | 50.68% | 69.18% | N/A |  |  | N/A | [7 empty] | 6285
Friedrich Air Conditioning | Friedrich | J-Series | 8915234 | MR24DY3JMA | Mixed | HMSV-A-CB | 10.2 | 19.6 | 12.5 | 18900 | Yes | Ductless | Multi-zone | Mixed Ducted and Non-ducted indoor units | 10230 | 23250 | 27900 | 1.171 | 1.859 | 2.6 | 2.5603 | 3.6654 | 3.1449 |  | 6270 | 14250 | 20394 | 1.008 | 1.61 | 1.76 | 1.823 | 2.594 | 3.396 |  | 4932 |  | 14109 | 0.973 |  | 1.7 | 1.4855 |  | 2.4323 | 50.57% | 69.18% | N/A |  |  | N/A | [7 empty] | 3412.3
Friedrich Air Conditioning | Friedrich | J-Series | 7000021 | MR09Y3J | MW09Y3J | HRCU-A-CB-O | 11 | 21.5 | 13.3 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 10800 | 17061 | 0.2 | 0.7 | 1.39 | 4.34 | 4.52 | 3.6 |  | 2700 | 5880 | 15355 | 0.27 | 0.56 | 1.9 | 2.89 | 3.08 | 2.37 |  | 2070 |  | 11942.7 | 0.28 |  | 1.95 | 2.16 |  | 1.79 | 70% | 77.78% | Integrated | 60W @230V | Base pan heater starts when outside temperature is less than 0C (heating mode). The heater turns off when temperature is greater than 3C. | N/A |  | z | [5 empty] | 4435.4
Friedrich Air Conditioning | Friedrich | J-Series | 7000022 | MR12Y3J | MW12Y3J | HRCU-A-CB-O | 11 | 21.5 | 12.5 | 11200 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 13300 | 22178 | 0.19 | 1 | 2.08 | 4.49 | 3.9 | 3.12 |  | 2700 | 6880 | 19960 | 0.26 | 0.81 | 2.85 | 3.04 | 2.49 | 2.05 |  | 2070 |  | 15524.6 | 0.266 |  | 2.91 | 2.28 |  | 2 | 70% | 77.78% | Integrated | 60W @230V | Base pan heater starts when outside temperature is less than 0C (heating mode). The heater turns off when temperature is greater than 3C. | N/A |  | z | [5 empty] | 7001.4
Friedrich Air Conditioning | Friedrich | J-Series | 7012589 | MR24Y3J | MW24Y3J | HRCU-A-CB-O | 11 | 21.5 | 12.5 | 22000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6200 | 27000 | 38898 | 0.53 | 2.38 | 4.19 | 3.43 | 3.4 | 2.72 |  | 5456 | 17240 | 34230 | 0.58 | 1.92 | 4.61 | 2.76 | 2.63 | 2.18 |  | 4278 |  | 27228.6 | 0.6 |  | 4.42 | 2.08 |  | 1.8 | 70% | 79.55% | N/A |  |  | N/A |  | z |  |  | 1.25 | 1.6846 | 1.5371 | 1600
Friedrich Air Conditioning | Friedrich | J-Series | 7086358 | MRH12Y3J | MWH12Y3J | HRCU-A-CB-O | 11 | 25 | 14.1 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 13300 | 13600 | 13950 | 0.956 | 0.983 | 1.09 | 4.0772 | 4.0547 | 3.7508 |  | 8500 | 8800 | 9100 | 0.809 | 0.831 | 0.855 | 3.0792 | 3.1035 | 3.1192 |  | 7000 |  | 7500 | 0.901 |  | 0.95 | 2.2769 |  | 2.3137 | 53.76% | 82.42% | N/A |  |  | -13° | 6300 |  | 6556 | 1.096 | 2.14 | 1.8 | 1.64 | 1500
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8033584 | AOU18RLXFZH | Non-Ducted Indoor Units | HMSV-A-CB | 10.3 | 21.5 | 13.5 | 18000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 6200 | 22000 | 24400 | 0.52 | 1.7 | 2.02 | 3.85 | 3.8 | 3.54 |  | 6619 | 14200 | 23500 | 0.81 | 1.6 | 3.18 | 2.4 | 2.6 | 2.16 |  | 6210 |  | 22000 | 0.89 |  | 3.49 | 2.04 |  | 1.85 | 90.16% | 93.62% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 3378 | z | 12000 | 0.55 | 2.44 | 2.19 | 1.62 | 500
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8033586 | AOU24RLXFZH | Non-Ducted Indoor Units | HMSV-A-CB | 10.3 | 20 | 13.3 | 22000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 6200 | 25000 | 29800 | 0.5 | 1.81 | 2.85 | 4 | 4.04 | 3.06 |  | 6005 | 15400 | 26000 | 0.62 | 1.73 | 3.57 | 2.84 | 2.6 | 2.13 |  | 5869 |  | 25500 | 0.62 |  | 3.57 | 2.77 |  | 2.09 | 85.57% | 98.08% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 3207 | z | 13500 | 0.43 | 3.59 | 2.03 | 1.81 | 2934
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8908615 | AOU36RLXFZH | Non-Ducted Indoor Units | HMSV-A-CB | 10.3 | 20 | 13 | 35200 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 12000 | 36400 | 42000 | 0.7 | 2.67 | 3.29 | 5.02 | 4 | 3.74 |  | 11212 | 21400 | 39341 | 1.09 | 2.38 | 5.13 | 3.02 | 2.64 | 2.25 |  | 10376 |  | 36407 | 1.12 |  | 5.28 | 2.72 |  | 2.02 | 86.68% | 92.54% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 6301 | z | 22110 | 0.91 | 3.84 | 3.8304 | 2.7858 | 8700
Fujitsu General America, Inc. | Fujitsu | J-Series | 8693477 | AOU48RLAVM | Non-Ducted Indoor Units | HMSV-A-CB | 11.4 | 19.8 | 12.5 | 4800 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 16630 | 54000 | 54000 | 0.91 | 4.06 | 4.06 | 5.3565 | 3.8981 | 3.8981 |  | 15400 | 33000 | 50000 | 1 | 3.4055 | 4.46 | 4.5134 | 2.84 | 3.2856 |  | 12720 |  | 41300 | 0.92288 |  | 4.12 | 4.0396 |  | 2.9379 | 76.48% | 82.6% | Not Needed | - | - | -4 | 11240 |  | 36500 | 0.86016 | 3.75 | 3.7845 | 2.626 | 4100
Fujitsu General America, Inc. | Fujitsu | J-Series | 8693480 | AOU36RLAVM | Non-Ducted Indoor Units | HMSV-A-CB | 11.4 | 19 | 13.3 | 3600 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 16460 | 42000 | 42000 | 0.87 | 3.2 | 3.2 | 5.5462 | 3.8466 | 3.8466 |  | 16460 | 25800 | 42000 | 1.2 | 2.7005 | 4.43 | 4.021 | 2.8 | 2.7786 |  | 14860 |  | 37900 | 1.1043 |  | 4.06 | 3.9429 |  | 2.7359 | 90.24% | 90.24% | Not Needed | - | - | -4 | 13170 |  | 33600 | 1.02 | 2.05 | 2.71 | 2 | 1400
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RL2 Series | 5063325 | AOU9RLS2 | ASU9RLS2 | HRCU-A-CB-O | 12.5 | 27.2 | 16.1 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 22000 | 0.2 | 0.8 | 1.99 | 4.5 | 4.4 | 3.24 |  | 2320 | 9400 | 16400 | 0.2 | 1.09 | 1.97 | 3.4 | 2.54 | 2.45 |  | 2150 |  | 15000 | 0.21 |  | 2.06 | 3 |  | 2.18 | 68.18% | 91.46% | N/A |  |  | -5 | 1945 | z | 13500 | 0.21 | 2.1 | 2.9 | 2.1 | 1400
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RL2 Series | 5063326 | AOU12RLS2 | ASU12RLS2 | HRCU-A-CB-O | 12 | 25 | 13.8 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 22110 | 0.2 | 1.2 | 2 | 4.5 | 3.91 | 3.24 |  | 2491 | 10200 | 17900 | 0.2 | 1.1 | 2 | 3.65 | 2.72 | 2.63 |  | 2320 |  | 16500 | 0.21 |  | 2.1 | 3.24 |  | 2.34 | 74.63% | 92.18% | N/A |  |  | -5 | 2081 | z | 15000 | 0.21 | 1.92 | 4.54 | 2.14 | 1100
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Compact Cassette | 5751311 | AOU9RLFC | AUU9RLF | HRCU-A-CB-O | 13 | 24 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 18000 | 0.15 | 0.89 | 1.8 | 6 | 3.95 | 2.93 |  | 2744 | 9400 | 16100 | 0.14 | 0.96 | 1.78 | 5.65 | 2.88 | 2.66 |  | 2610 |  | 15000 | 0.15 |  | 1.87 | 5.11 |  | 2.41 | 83.33% | 93.17% | N/A |  |  | -5 | 2378 | z | 13500 | 0.15 | 1.92 | 4.54 | 2.14 | 1100
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Slim Duct | 5751312 | AOU9RLFC | ARU9RLF | HRCU-A-CB-O | 12.2 | 21.5 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 18000 | 0.15 | 0.85 | 1.8 | 6 | 4.14 | 2.93 |  | 2744 | 9400 | 16100 | 0.14 | 0.96 | 1.78 | 5.65 | 2.88 | 2.66 |  | 2610 |  | 15000 | 0.15 |  | 1.87 | 5.11 |  | 2.41 | 83.33% | 93.17% | N/A |  |  | -5 | 2378 | z | 13500 | 0.15 | 2.32 | 3.75 | 1.9 | 1100
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Compact Cassette | 5751313 | AOU12RLFC | AUU12RLF | HRCU-A-CB-O | 12.2 | 21.9 | 12.8 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 19400 | 0.15 | 1.44 | 2 | 6 | 3.26 | 2.85 |  | 2793 | 10200 | 17600 | 0.17 | 1.16 | 2.15 | 4.76 | 2.58 | 2.41 |  | 2647 |  | 16500 | 0.18 |  | 2.25 | 4.31 |  | 2.18 | 85.05% | 93.75% | N/A |  |  | -5 | 2377 | z | 15000 | 0.19 | 2.32 | 3.75 | 1.9 | 1100
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Slim Duct | 5751314 | AOU12RLFC | ARU12RLF | HRCU-A-CB-O | 11.5 | 20 | 12.8 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 19400 | 0.15 | 1.3 | 2 | 6 | 3.61 | 2.85 |  | 2793 | 10200 | 17600 | 0.17 | 1.16 | 2.15 | 4.76 | 2.58 | 2.41 |  | 2647 |  | 16500 | 0.18 |  | 2.25 | 4.31 |  | 2.18 | 85.05% | 93.75% | N/A |  |  | -5 | 2377 | z | 15000 | 0.19 | 2 | 2.73 | 1.83 | 0
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFFH Series | 6936995 | AOU9RLFF | AGU9RLF | HRCU-A-CB-O | 12.6 | 26 | 16 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 18800 | 0.2 | 0.88 | 1.84 | 4.5428 | 3.9966 | 2.99 |  | 2320 | 7500 | 14000 | 0.2 | 0.78 | 1.82 | 3.4 | 2.8 | 2.25 |  | 2115 |  | 14000 | 0.19 |  | 2.1 | 3.26 |  | 1.95 | 74.47% | 100% | N/A |  |  | -5 | 2047 | z | 12500 | 0.22 | 2.06 | 2.82 | 1.85 | 0
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFFH Series | 6936996 | AOU12RLFF | AGU12RLF | HRCU-A-CB-O | 11.6 | 22.7 | 13.1 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 19500 | 0.2 | 1.44 | 1.84 | 4.5428 | 3.2565 | 3.1 |  | 2457 | 10600 | 15000 | 0.24 | 1.19 | 2.17 | 3 | 2.6 | 2.02 |  | 2423 |  | 15000 | 0.24 |  | 2.17 | 2.96 |  | 2.02 | 76.92% | 100% | N/A |  |  | -5 | 2115 | z | 13000 | 0.22 | 2.86 | 2.92 | 1.79 | 500
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFFH Series | 6936997 | AOU15RLFF | AGU15RLF | HRCU-A-CB-O | 11.2 | 20.3 | 12.5 | 14200 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 18000 | 20800 | 0.18 | 1.58 | 2.01 | 5.0475 | 3.3389 | 3.03 |  | 2832 | 11600 | 19000 | 0.32 | 1.3 | 2.89 | 2.59 | 2.62 | 1.93 |  | 2798 |  | 18500 | 0.26 |  | 2.91 | 3.15 |  | 1.86 | 88.94% | 97.37% | N/A |  |  | -5 | 2593 | z | 17500 | 0.26 | 2.07 | 1.42 | 1.56 | 0
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFF Series | 6937309 | AOU9RLFFH | AGU9RLF | HRCU-A-CB-O | 12.4 | 26 | 16 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 18800 | 0.2 | 0.88 | 1.84 | 4.5428 | 3.9966 | 2.99 |  | 2320 | 7500 | 14000 | 0.35 | 0.78 | 1.97 | 1.94 | 2.8 | 2.08 |  | 2115 |  | 14000 | 0.34 |  | 2.25 | 1.82 |  | 1.82 | 74.47% | 100% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 1843 | z | 11000 | 0.38 | 2.99 | 1.38 | 1.37 | 0
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFF Series | 6937310 | AOU12RLFFH | AGU12RLF | HRCU-A-CB-O | 11.3 | 22.7 | 13.1 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 19500 | 0.2 | 1.44 | 1.84 | 4.5428 | 3.2565 | 3.1 |  | 2457 | 10600 | 15000 | 0.39 | 1.19 | 2.32 | 1.85 | 2.6 | 1.89 |  | 2423 |  | 15000 | 0.39 |  | 2.32 | 1.82 |  | 1.89 | 76.92% | 100% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 2252 | z | 14000 | 0.48 | 2.93 | 1.66 | 1.55 | 500
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Floor Mounted RLFF Series | 6937311 | AOU15RLFFH | AGU15RLF | HRCU-A-CB-O | 11 | 20.3 | 12.5 | 14200 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 18000 | 20800 | 0.18 | 1.58 | 2.01 | 5.0475 | 3.3389 | 3.03 |  | 2832 | 11600 | 19000 | 0.47 | 1.3 | 3.04 | 1.77 | 2.62 | 1.83 |  | 2798 |  | 18500 | 0.41 |  | 3.06 | 2 |  | 1.77 | 88.94% | 97.37% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 2320 | z | 15500 | 0.41 | 2.09 | 2.77 | 2.1 | 1000
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3 Series | 7993242 | AOU12RLS3 | ASU12RLS3 | HRCU-A-CB-O | 14 | 29.3 | 15.2 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 22110 | 0.2 | 1.01 | 1.94 | 4.5428 | 4.6429 | 3.34 |  | 2491 | 9600 | 17500 | 0.21 | 0.85 | 2.06 | 3.48 | 3.3 | 2.49 |  | 2320 |  | 16500 | 0.22 |  | 2.1 | 3.09 |  | 2.3 | 74.63% | 94.29% | N/A |  |  | -5 | 2081 | z | 15000 | 0.22 | 2.74 | 3.33 | 1.98 | 1000
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3 Series | 7993243 | AOU15RLS3 | ASU15RLS3 | HRCU-A-CB-O | 13.4 | 25.3 | 13.9 | 14500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 18000 | 23900 | 0.17 | 1.15 | 2.19 | 5.29 | 4.5874 | 3.2 |  | 2798 | 11200 | 21500 | 0.2 | 1.04 | 2.59 | 4.1 | 3.14 | 2.43 |  | 2696 |  | 20500 | 0.21 |  | 2.75 | 3.76 |  | 2.18 | 85.77% | 95.35% | N/A |  |  | -5 | 2388 | z | 18500 | 0.21 | 2.23 | 1.26 | 1.51 | 1000
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3 Series | 7993244 | AOU12RLS3H | ASU12RLS3 | HRCU-A-CB-O | 13.8 | 29.3 | 15.2 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 22110 | 0.2 | 1.01 | 1.94 | 4.5 | 4.6429 | 3.34 |  | 2491 | 9600 | 17500 | 0.36 | 0.88 | 2.21 | 2.03 | 3.18 | 2.32 |  | 2320 |  | 16500 | 0.37 |  | 2.25 | 1.84 |  | 2.15 | 74.63% | 94.29% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 1638 | z | 11500 | 0.38 | 2.88 | 1.65 | 1.63 | 1000
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3HY Series | 7993245 | AOU15RLS3H | ASU15RLS3 | HRCU-A-CB-O | 13.3 | 25.3 | 13.9 | 14500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 18000 | 23900 | 0.17 | 1.15 | 2.19 | 5.29 | 4.5874 | 3.2 |  | 2798 | 11200 | 21500 | 0.35 | 1.07 | 2.74 | 2.34 | 3.06 | 2.3 |  | 2696 |  | 20500 | 0.36 |  | 2.9 | 2.19 |  | 2.07 | 85.77% | 95.35% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 2081 | z | 16000 | 0.37 | 2.09 | 2.59 | 1.89 | 1000
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3 Series | 8004699 | AOU9RLS3 | ASU9RLS3 | HRCU-A-CB-O | 14.2 | 33 | 18 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 22000 | 0.2 | 0.66 | 1.93 | 4.5 | 5.3288 | 3.34 |  | 2286 | 7000 | 16000 | 0.21 | 0.59 | 2.06 | 3.19 | 3.46 | 2.28 |  | 2150 |  | 15000 | 0.22 |  | 2.1 | 2.86 |  | 2.09 | 68.18% | 93.75% | N/A |  |  | -5 | 1945 | z | 13500 | 0.22 | 2.23 | 1.18 | 1.44 | 1000
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3HY Series | 8004700 | AOU9RLS3H | ASU9RLS3 | HRCU-A-CB-O | 14 | 33 | 18 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 22000 | 0.2 | 0.66 | 1.93 | 4.5 | 5.3288 | 3.34 |  | 2286 | 7000 | 16000 | 0.36 | 0.61 | 2.21 | 1.86 | 3.36 | 2.12 |  | 2150 |  | 15000 | 0.37 |  | 2.25 | 1.7 |  | 1.95 | 68.18% | 93.75% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 1535 | z | 11000 | 0.38 | 2.09 | 2.59 | 1.89 | 1000
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall mounted RLS3 Series | 8703348 | AOU9RLS3 | ASU9RLS3Y | HRCU-A-CB-O | 14.2 | 33 | 18 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 22000 | 0.2 | 0.66 | 1.93 | 4.5426 | 5.3288 | 3.34 |  | 2286 | 7000 | 16000 | 0.21 | 0.59 | 2.06 | 3.19 | 3.46 | 2.28 |  | 2150 |  | 15000 | 0.22 |  | 2.1 | 2.86 |  | 2.09 | 68.18% | 93.75% | N/A |  |  | -5 | 1945 | z | 13500 | 0.22 | 2.23 | 1.18 | 1.44 | 1000
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall mounted H Series | 8703349 | AOU9RLS3H | ASU9RLS3Y | HRCU-A-CB-O | 14 | 33 | 18 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 12000 | 22000 | 0.2 | 0.66 | 1.93 | 4.5426 | 5.33 | 3.34 |  | 2286 | 7000 | 16000 | 0.36 | 0.61 | 2.21 | 1.86 | 3.36 | 2.12 |  | 2150 |  | 15000 | 0.37 |  | 2.25 | 1.7 |  | 1.95 | 68.18% | 93.75% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 1535 | z | 11000 | 0.38 | 2.09 | 2.77 | 2.1 | 1000
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3HY Series | 8703350 | AOU12RLS3 | ASU12RLS3Y | HRCU-A-CB-O | 14 | 29.3 | 15.2 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 22110 | 0.2 | 1.01 | 1.94 | 4.5426 | 4.64 | 3.34 |  | 2491 | 9600 | 17500 | 0.21 | 0.85 | 2.06 | 3.48 | 3.3 | 2.49 |  | 2320 |  | 16500 | 0.22 |  | 2.1 | 3.09 |  | 2.3 | 74.63% | 94.29% | N/A |  |  | -5 | 2081 | z | 15000 | 0.22 | 2.23 | 1.26 | 1.51 | 1000
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3H Series | 8703506 | AOU12RLS3H | ASU12RLS3Y | HRCU-A-CB-O | 13.8 | 29.3 | 15.2 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 22110 | 0.2 | 1.01 | 1.94 | 4.5426 | 4.64 | 3.34 |  | 2491 | 9600 | 17500 | 0.36 | 0.88 | 2.21 | 2.03 | 3.18 | 2.32 |  | 2320 |  | 16500 | 0.37 |  | 2.25 | 1.84 |  | 2.15 | 74.63% | 94.29% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 1638 | z | 11500 | 0.38 | 2.74 | 3.33 | 1.98 | 1000
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall mounted RLS3 Series | 8703507 | AOU15RLS3 | ASU15RLS3Y | HRCU-A-CB-O | 13.4 | 25.3 | 13.9 | 14500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 18000 | 23900 | 0.17 | 1.15 | 2.19 | 5.3442 | 4.59 | 3.2 |  | 2798 | 11200 | 21500 | 0.2 | 1.04 | 2.59 | 4.1 | 3.14 | 2.43 |  | 2696 |  | 20500 | 0.21 |  | 2.75 | 3.76 |  | 2.18 | 85.77% | 95.35% | N/A |  |  | -5 | 2388 | z | 18500 | 0.21 | 2.88 | 1.65 | 1.63 | 1000
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLS3HY Series | 8703508 | AOU15RLS3H | ASU15RLS3Y | HRCU-A-CB-O | 13.3 | 25.3 | 13.9 | 14500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 18000 | 23900 | 0.17 | 1.15 | 2.19 | 5.3442 | 4.59 | 3.2 |  | 2798 | 11200 | 21500 | 0.35 | 1.07 | 2.74 | 2.34 | 3.06 | 2.3 |  | 2696 |  | 20500 | 0.36 |  | 2.9 | 2.19 |  | 2.07 | 85.77% | 95.35% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 2081 | z | 16000 | 0.37 | 2.22 | 4.21 | 2.6 | 1159
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLF/RLX Series | 8718495 | AOU18RLXFW1 | ASU18RLF | HRCU-A-CB-O | 10.5 | 20 | 13.3 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7000 | 21600 | 29000 | 0.48 | 1.75 | 2.99 | 4.27 | 3.62 | 2.84 |  | 5485 | 14600 | 22759 | 0.42 | 1.39 | 2.85 | 3.83 | 3.08 | 2.34 |  | 5205 |  | 21600 | 0.39 |  | 2.6 | 3.91 |  | 2.43 | 74.48% | 94.91% | N/A |  |  | -5 | 4745 | z | 19688 | 0.33 | 1.83 | 3.01 | 2.87 | 1159
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLF/RLX Series | 8779045 | AOU18RLXFWH | ASU18RLF | HRCU-A-CB-O | 10.4 | 20 | 13.3 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7000 | 21600 | 29000 | 0.48 | 1.75 | 2.99 | 4.27 | 3.62 | 2.84 |  | 5485 | 14600 | 22759 | 0.57 | 1.42 | 3 | 2.82 | 3.02 | 2.22 |  | 5205 |  | 21600 | 0.54 |  | 2.75 | 2.82 |  | 2.3 | 74.48% | 94.91% | Integrated | 150 | Operation depends on outdoor temperature & demand | -15 | 4317 | z | 17913 | 0.42 | 3.22 | 4.4 | 1.8 | 2480
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8779046 | AOU24RLXFWH | ASU24RLF | HRCU-A-CB-O | 10.5 | 19.5 | 12.5 | 22000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7500 | 21850 | 36200 | 0.5 | 1.94 | 3.38 | 4.4 | 3.3 | 3.14 |  | 5740 | 16720 | 27700 | 0.64 | 2.11 | 3.59 | 2.63 | 2.32 | 2.26 |  | 5220 |  | 25220 | 0.64 |  | 3.59 | 2.4 |  | 2.06 | 69.67% | 91.05% | Integrated | 0.15 | Cold outside & demand | -15 | 7510 |  | 19720 | 0.5 | 3.95 | 3.12 | 1.7 | 3160
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8912454 | AOU30RLXEH | ASU30RLE | HRCU-A-CB-O | 11.8 | 18.7 | 12.5 | 30000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 8000 | 22600 | 37200 | 0.5 | 2.4 | 2.54 | 4.7 | 2.77 | 2.54 |  | 7570 | 21400 | 35200 | 0.53 | 2.52 | 4.51 | 4.2 | 2.49 | 2.29 |  | 6890 |  | 32040 | 0.53 |  | 4.55 | 3.79 |  | 2.06 | 86.13% | 91.02% | Integrated | 0.15 | Cold outside & demand | -15 | 4620 |  | 22860 | 0.46 | - | - | - | 970
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLF Series | 6961728 | AOU9RLFW1 | ASU9RLF1 | HRCU-A-CB-O | 11 | 23 | 13.8 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1700 | 12000 | 15000 | 0.25 | 0.89 | 1.6 | 2 | 3.95 | 2.75 |  | 1079 | 7600 | 9500 | 0.2 | 0.71 | 1.27 | 1.59 | 3.1363 | 2.1917 |  | 969 |  | 8530 | 0.19944 |  | 1.27 | 1.4236 |  | 1.9679 | 56.87% | 89.79% | N/A |  |  | N/A | - |  | - | - | - | - | - | -
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLF Series | 6961729 | AOU12RLFW1 | ASU12RLF1 | HRCU-A-CB-O | 11 | 22 | 12.5 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 16000 | 19100 | 0.25 | 1.28 | 1.99 | 3.6 | 3.66 | 2.8122 |  | 1795 | 9400 | 11200 | 0.19 | 0.96 | 1.4925 | 2.8 | 2.869 | 2.196 |  | 1949 |  | 12150 | 0.22266 |  | 1.7723 | 2.57 |  | 2.0071 | 63.61% | 108.5% | N/A |  |  | N/A | - |  | - | - | - | - | - | -
Fujitsu General America, Inc. | Fujitsu | Halcyon Single-room Mini-Split Systems Wall Mounted RLB Series | 7937663 | AOU18RLB | ASU18RLB | HRCU-A-CB-O | 10.6 | 19 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3100 | 18000 | 20000 | 0.17 | 1.285 | 2.06 | 5.29 | 4.11 | 2.8447 |  | 2798 | 11500 | 16700 | 0.2 | 1.15 | 2.1 | 4.0991 | 2.92 | 2.3327 |  | 2696 |  | 15400 | 0.21 |  | 2.18 | 3.76 |  | 2.0698 | 77% | 92.22% | N/A |  |  | N/A | - |  | - | - | 3.28 | 2.94 | 2.02 | -
Fujitsu General America, Inc. | Fujitsu | Halcyon Multi-room Mini-Split Systems | 8718545 | AOU24RLXFW1 | ASU24RLF | HRCU-A-CB-O | 10.6 | 19.5 | 12.5 | 22000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7500 | 21850 | 36200 | 0.5 | 1.94 | 3.38 | 4.4 | 3.3 | 3.14 |  | 5740 | 16720 | 27700 | 0.49 | 1.96 | 3.44 | 3.44 | 2.49 | 2.36 |  | 5220 |  | 25220 | 0.49 |  | 3.44 | 3.13 |  | 2.15 | 69.67% | 91.05% | Not Needed | - | - | -5 | 4670 |  | 22550 | 0.47 |  |  |  | 645
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | ML-Series | 9920040 | MLA012S4S-1P | ducted indoor units | HMSV-A-CB | 10 | 19 | 12.5 | 11500 | Yes | Ductless | Multi-zone | Ducted Indoor Units | 3752 | 12000 | 17021 | 0.189 | 0.961 | 1.692 | 5.818 | 3.6596 | 2.9482 |  | 3292 | 8500 | 12986 | 0.232 | 0.966 | 2.028 | 4.1586 | 2.5788 | 1.8766 |  | 2718 |  | 12341 | 0.205 |  | 2.031 | 3.8857 |  | 1.7808 | 72.5% | 95.03% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 920
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058816 | MPB009S4S-1P | ducted indoor units | HMSV-A-CB | 10.5 | 19.5 | 13.5 | 9000 | Yes | Ductless | Multi-zone | Ducted Indoor Units | 3056 | 10000 | 12764 | 0.166 | 0.718 | 1.342 | 5.3953 | 4.0818 | 2.7875 |  | 2588 | 6200 | 8991 | 0.176 | 0.64 | 1.212 | 4.3095 | 2.8391 | 2.1741 |  | 2312 |  | 8071 | 0.164 |  | 1.18 | 4.1316 |  | 2.0046 | 63.23% | 89.77% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 3144
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058821 | MPB024S4S-1P | ducted indoor units | HMSV-A-CB | 10.5 | 20 | 12.5 | 24000 | Yes | Ductless | Multi-zone | Ducted Indoor Units | 7020 | 24400 | 32812 | 0.452 | 1.986 | 3.376 | 4.5517 | 3.6007 | 2.8484 |  | 5862 | 16800 | 18826 | 0.541 | 1.851 | 2.731 | 3.1756 | 2.66 | 2.0203 |  | 5028 |  | 15682 | 0.491 |  | 2.498 | 3.0011 |  | 1.8398 | 47.79% | 83.3% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 6572
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10062010 | MPB018S4M-1P | Non-Ducted Indoor Units | HMSV-A-CB | 10.3 | 22.5 | 12.5 | 18000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 5760 | 19000 | 24480 | 0.52 | 1.547 | 1.98 | 3.2463 | 3.5995 | 3.6234 |  | 5376 | 12000 | 16234 | 0.566 | 1.256 | 2.15 | 2.7837 | 2.8 | 2.2129 |  | 4752 |  | 9662 | 0.581 |  | 1.524 | 2.397 |  | 1.858 | 39.47% | 59.52% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 7525
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10062012 | MPB030S4M-1P | Non-Ducted Indoor Units | HMSV-A-CB | 10.3 | 23 | 12.5 | 28000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 6010 | 28000 | 36180 | 0.715 | 2.104 | 3.17 | 2.4634 | 3.9002 | 3.3449 |  | 5721 | 17200 | 24345 | 0.765 | 1.788 | 3.451 | 2.1917 | 2.8193 | 2.0675 |  | 5556 |  | 16820 | 0.843 |  | 2.526 | 1.9316 |  | 1.9515 | 46.49% | 69.09% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 12553
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10062016 | MPB048S4M-1P | Non-Ducted Indoor Units | HMSV-A-CB | 10.2 | 22.4 | 12.5 | 48000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7210 | 48000 | 55820 | 1.02 | 3.908 | 4.705 | 2.0716 | 3.5996 | 3.477 |  | 6822 | 29600 | 36673 | 1.081 | 3.213 | 4.567 | 1.8495 | 2.6999 | 2.3534 |  | 6567 |  | 24120 | 1.115 |  | 3.938 | 1.7261 |  | 1.795 | 43.21% | 65.77% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2894
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | ML-Series | 9920054 | MLA030S4M-1P | Non-Ducted Indoor Units | HMSV-A-CB | 10.4 | 22 | 13 | 28000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 5820 | 28000 | 37720 | 0.895 | 2.345 | 3.475 | 1.9058 | 3.4994 | 3.1812 |  | 5411 | 18000 | 31054 | 0.924 | 1.925 | 4.176 | 1.7162 | 2.7404 | 2.1794 |  | 5145 |  | 28160 | 1.008 |  | 4.041 | 1.4959 |  | 2.0423 | 74.66% | 90.68% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2125
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | ML-Series | 9920055 | MLA036S4M-1P | Non-Ducted Indoor Units | HMSV-A-CB | 10.5 | 21.5 | 13.5 | 36000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7210 | 36000 | 50350 | 1.02 | 2.777 | 4.64 | 2.0716 | 3.7993 | 3.1802 |  | 6845 | 23200 | 38125 | 1.091 | 2.446 | 5.502 | 1.8387 | 2.7797 | 2.0308 |  | 6425 |  | 36000 | 1.146 |  | 5.379 | 1.6431 |  | 1.9614 | 71.5% | 94.43% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2387
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 8129529 | MPA009S4S-1P | MWMA009S4-1P | HRCU-A-CB-O | 10 | 23.5 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3102 | 10000 | 11800 | 0.153 | 0.801 | 1.308 | 5.9419 | 3.6588 | 2.6439 |  | 2388 | 5700 | 8678 | 0.178 | 0.702 | 1.098 | 3.9318 | 2.3796 | 2.3163 |  | 2173 |  | 6291 | 0.167 |  | 0.884 | 3.8134 |  | 2.0856 | 53.31% | 72.49% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 5628
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 8129532 | MPA012S4S-1P | MWMA012S4-1P | HRCU-A-CB-O | 10 | 21.5 | 13 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3820 | 12000 | 16500 | 0.182 | 1.047 | 1.71 | 6.1513 | 3.359 | 2.8279 |  | 3224 | 7600 | 11920 | 0.226 | 0.844 | 1.484 | 4.1808 | 2.639 | 2.354 |  | 2674 |  | 6292 | 0.196 |  | 0.98 | 3.9983 |  | 1.8816 | 38.13% | 52.79% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2443
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 8129542 | MPA024S4S-1P | MWMA024S4-1P | HRCU-A-CB-O | 10 | 20 | 12.5 | 23000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7060 | 25000 | 31850 | 0.446 | 2.275 | 3.42 | 4.6392 | 3.2206 | 2.7293 |  | 5597 | 17800 | 18825 | 0.532 | 1.877 | 2.461 | 3.0833 | 2.7793 | 2.2418 |  | 4942 |  | 16382 | 0.483 |  | 2.202 | 2.9987 |  | 2.1803 | 51.43% | 87.02% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 4231
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 8129566 | MPA012S4S-1P | M22A012S4-1P | HRCU-A-CB-O | 10 | 20.5 | 13 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4062 | 12000 | 16916 | 0.195 | 0.93 | 1.702 | 6.1049 | 3.7816 | 2.9128 |  | 7200 | 3178 | 11696 | 0.799 | 0.229 | 1.498 | 2.6409 | 4.0672 | 2.2882 |  | 2716 |  | 7465 | 0.218 |  | 1.143 | 3.6513 |  | 1.9141 | 44.13% | 63.83% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 1120
GD Midea Air-Conditioning Equipment Co.,Ltd | Comfort-Aire/Century |  | 8779089 | A-VMH24SU-1 | B-VMH24SU-1 | HRCU-A-CB-O | 11.5 | 20.5 | 13 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 11795 | 24000 | 29680 | 0.68726 | 1.9539 | 3.1981 | 5.0298 | 3.5999 | 2.7199 |  | 15400 | 15400 | 25710 | 1.6353 | 1.6353 | 3.8642 | 2.7599 | 2.7599 | 1.9499 |  | 23260 |  | 24590 | 3.8298 |  | 3.9817 | 1.7799 |  | 1.8099 | 82.85% | 95.64% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2130
GD Midea Air-Conditioning Equipment Co.,Ltd | Comfort-Aire/Century |  | 8779091 | B-VMH12SU-1 | A-VMH12SU-1 | HRCU-A-CB-O | 12 | 22.5 | 13 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4110 | 11800 | 15570 | 0.22728 | 0.97694 | 1.3955 | 5.2998 | 3.5399 | 3.2699 |  | 7800 | 7800 | 14140 | 0.86593 | 0.86593 | 1.8752 | 2.6399 | 2.6399 | 2.2099 |  | 11800 |  | 12010 | 1.9762 |  | 1.9555 | 1.7499 |  | 1.7999 | 77.14% | 84.94% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 895
GD Midea Air-Conditioning Equipment Co.,Ltd | Comfort-Aire/Century |  | 8779092 | A-VMH09SU-1 | B-VMH09SU-1 | HRCU-A-CB-O | 11.2 | 25 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4185 | 10900 | 15365 | 0.23319 | 0.82762 | 1.4251 | 5.2598 | 3.8598 | 3.1599 |  | 6900 | 6900 | 12575 | 0.73806 | 0.73806 | 1.852 | 2.7399 | 2.7399 | 1.9899 |  | 10720 |  | 11680 | 1.7621 |  | 1.945 | 1.7829 |  | 1.7599 | 76.02% | 92.88% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 895
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis |  | 9038618 | WUHO09KW25S | WUHI09KHW | HRCU-A-CB-O | 11.2 | 25 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4185 | 10900 | 15365 | 0.23319 | 0.82762 | 1.4251 | 5.2598 | 3.8598 | 3.1599 |  | 6900 | 6900 | 12575 | 0.73806 | 0.73806 | 1.852 | 2.7399 | 2.7399 | 1.9899 |  | 10720 |  | 11680 | 1.7621 |  | 1.945 | 1.7829 |  | 1.7599 | 76.02% | 92.88% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 2130
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis |  | 9038619 | WUHO12KW22S | WUHI12KHW | HRCU-A-CB-O | 12 | 22.5 | 12.5 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4110 | 11800 | 15570 | 0.22728 | 0.97694 | 1.3955 | 5.2998 | 3.5399 | 3.2699 |  | 7800 | 7800 | 14140 | 0.86593 | 0.86593 | 1.8752 | 2.6399 | 2.6399 | 2.2099 |  | 11800 |  | 12010 | 1.9762 |  | 1.9555 | 1.7499 |  | 1.7999 | 77.14% | 84.94% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 1120
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis |  | 9038621 | WUHO24KW20S | WUHI24KHW | HRCU-A-CB-O | 11.5 | 20.5 | 13 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 11795 | 24000 | 29680 | 0.68726 | 1.9539 | 3.1981 | 5.0298 | 3.5999 | 2.7199 |  | 15400 | 15400 | 25710 | 1.6353 | 1.6353 | 3.8642 | 2.7599 | 2.7599 | 1.9499 |  | 23260 |  | 24590 | 3.8298 |  | 3.9817 | 1.7799 |  | 1.8099 | 82.85% | 95.64% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 1279.9856
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis |  | 9038626 | WSM09MH20S/O | WSM09MH20S/I | HRCU-A-CB-O | 10 | 20.5 | 14 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2908 | 9800 | 11602.2672 | 0.2454 | 0.89757 | 1.1766 | 3.4729 | 3.1999 | 2.8899 |  | 6300 | 6300 | 7979.9856 | 0.68896 | 0.68896 | 1.0929 | 2.6799 | 2.6799 | 2.1399 |  | 6600 |  | 6700 | 1.0075 |  | 1.0122 | 1.9199 |  | 1.9399 | 57.75% | 83.96% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | -104
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis |  | 9038628 | WSM18MH20S/O | WSM18MH20S/I | HRCU-A-CB-O | 10 | 22 | 13 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6093 | 18000 | 19146 | 0.37915 | 1.6695 | 1.5896 | 4.7097 | 3.1599 | 3.5299 |  | 11100 | 11100 | 12396 | 1.1787 | 1.1787 | 1.5013 | 2.7599 | 2.7599 | 2.4199 |  | 10460.09 |  | 12500 | 1.5252 |  | 2.0816 | 2.0099 |  | 1.7599 | 65.29% | 100.8% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 2515
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis |  | 9038629 | WSM24MH20S/O | WSM24MH20S/I | HRCU-A-CB-O | 10 | 20 | 12.5 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 10271 | 25000 | 27303 | 0.64679 | 2.4588 | 3.5723 | 4.654 | 2.9799 | 2.2399 |  | 16000 | 16000 | 18330 | 1.9062 | 1.9062 | 2.798 | 2.4599 | 2.4599 | 1.9199 |  | 14800 |  | 15815 | 2.4786 |  | 2.6336 | 1.7499 |  | 1.7599 | 57.92% | 86.28% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 1285
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | ML-Series | 9920038 | MLA009S4S-1P | MWMA009S4-2P | HRCU-A-CB-O | 10.5 | 24 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2750 | 10900 | 14360 | 0.159 | 0.828 | 1.35 | 5.0688 | 3.8581 | 3.1174 |  | 2200 | 6900 | 12115 | 0.191 | 0.738 | 1.815 | 3.3757 | 2.7401 | 1.9562 |  | 1925 |  | 10830 | 0.172 |  | 1.7 | 3.28 |  | 1.867 | 75.42% | 89.39% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 1121
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | ML-Series | 9920041 | MLA012S4S-1P | MWMA012S4-2P | HRCU-A-CB-O | 10 | 22 | 12.5 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3660 | 12000 | 15600 | 0.188 | 0.994 | 1.8 | 5.7055 | 3.5381 | 2.5399 |  | 2928 | 7800 | 13159 | 0.226 | 0.866 | 2.105 | 3.797 | 2.6397 | 1.8321 |  | 2562 |  | 12038 | 0.203 |  | 1.972 | 3.6988 |  | 1.789 | 77.17% | 91.48% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 1125
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | ML-Series | 9920047 | MLA024S4S-1P | MWMA024S4-2P | HRCU-A-CB-O | 10 | 20 | 12.5 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7260 | 24000 | 31200 | 0.451 | 1.954 | 3.27 | 4.7177 | 3.5996 | 2.7963 |  | 5808 | 15400 | 27155 | 0.541 | 1.635 | 4.33 | 3.1463 | 2.7604 | 1.838 |  | 5082 |  | 26030 | 0.487 |  | 4.29 | 3.0583 |  | 1.7782 | 83.43% | 95.86% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2387
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 9962873 | MPA009S4S-1P | MWMA009S4-2P | HRCU-A-CB-O | 10 | 23.5 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3102 | 10000 | 11800 | 0.153 | 0.801 | 1.308 | 5.9419 | 3.6588 | 2.6439 |  | 2388 | 5700 | 8678 | 0.178 | 0.702 | 1.098 | 3.9318 | 2.3796 | 2.3163 |  | 2173 |  | 6291 | 0.167 |  | 0.884 | 3.8134 |  | 2.0856 | 53.31% | 72.49% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 5628
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 9962874 | MPA012S4S-1P | MWMA012S4-2P | HRCU-A-CB-O | 10 | 21.5 | 13 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3820 | 12000 | 16500 | 0.182 | 1.047 | 1.71 | 6.1513 | 3.359 | 2.8279 |  | 3224 | 7600 | 11920 | 0.226 | 0.844 | 1.484 | 4.1808 | 2.639 | 2.354 |  | 2674 |  | 6292 | 0.196 |  | 0.98 | 3.9983 |  | 1.8816 | 38.13% | 52.79% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2443
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 9962876 | MPA024S4S-1P | MWMA024S4-2P | HRCU-A-CB-O | 10 | 20 | 12.5 | 23000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7060 | 25000 | 31850 | 0.446 | 2.275 | 3.42 | 4.6392 | 3.2206 | 2.7293 |  | 5597 | 17800 | 18825 | 0.532 | 1.877 | 2.461 | 3.0833 | 2.7793 | 2.2418 |  | 4942 |  | 16382 | 0.483 |  | 2.202 | 2.9987 |  | 2.1803 | 51.43% | 87.02% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 4231
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 9962880 | MPA012S4S-1P | M22A012S4-2P | HRCU-A-CB-O | 10 | 20.5 | 13 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4062 | 12000 | 16916 | 0.195 | 0.93 | 1.702 | 6.1049 | 3.7816 | 2.9128 |  | 7200 | 3178 | 11696 | 0.799 | 0.229 | 1.498 | 2.6409 | 4.0672 | 2.2882 |  | 2716 |  | 7465 | 0.218 |  | 1.143 | 3.6513 |  | 1.9141 | 44.13% | 63.83% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 3374
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056167 | MPB009S4S-1L | MWMB009S4-1L | HRCU-A-CB-O | 11.2 | 24.5 | 15 | 9500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3550 | 11000 | 14500 | 0.151 | 0.862 | 1.65 | 6.8901 | 3.7399 | 2.5755 |  | 2840 | 6500 | 10150 | 0.181 | 0.676 | 1.38 | 4.5985 | 2.818 | 2.1556 |  | 2485 |  | 6776 | 0.16308 |  | 1.02 | 4.4658 |  | 1.9469 | 46.73% | 66.76% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 4335
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056168 | MPB012S4S-1L | MWMB012S4-1L | HRCU-A-CB-O | 13 | 22 | 10.2 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3690 | 12000 | 16600 | 0.17 | 1.028 | 1.74 | 6.3614 | 3.4211 | 2.796 |  | 2952 | 7600 | 11220 | 0.204 | 0.857 | 1.421 | 4.2409 | 2.599 | 2.314 |  | 2583 |  | 6885 | 0.1836 |  | 1.006 | 4.1231 |  | 2.0058 | 41.48% | 61.36% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 900
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056169 | MPB009S4S-1P | MWMA009S4-1P | HRCU-A-CB-O | 10.8 | 23.5 | 14.9 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3009 | 9800 | 12700 | 0.144 | 0.756 | 1.33 | 6.124 | 3.7991 | 2.7985 |  | 2407 | 5800 | 8890 | 0.173 | 0.616 | 1.098 | 4.0776 | 2.7594 | 2.3729 |  | 2106 |  | 7990 | 0.156 |  | 1.175 | 3.9565 |  | 1.9929 | 62.91% | 89.88% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 900
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056170 | MPB009S4S-1P | MWMA009S4-2P | HRCU-A-CB-O | 10.8 | 23.5 | 14.9 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3009 | 9800 | 12700 | 0.144 | 0.756 | 1.33 | 6.124 | 3.7991 | 2.7985 |  | 2407 | 5800 | 8890 | 0.173 | 0.616 | 1.098 | 4.0776 | 2.7594 | 2.3729 |  | 2106 |  | 7990 | 0.156 |  | 1.175 | 3.9565 |  | 1.9929 | 62.91% | 89.88% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2976
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056171 | MPB012S4S-1P | MWMA012S4-1P | HRCU-A-CB-O | 11 | 22.7 | 13.7 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3880 | 12000 | 17300 | 0.177 | 0.999 | 1.68 | 6.4244 | 3.5204 | 3.0179 |  | 3104 | 7700 | 12110 | 0.212 | 0.816 | 1.414 | 4.291 | 2.7655 | 2.51 |  | 2716 |  | 9134 | 0.192 |  | 1.382 | 4.1457 |  | 1.937 | 52.8% | 75.43% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 2976
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056172 | MPB012S4S-1P | MWMA012S4-2P | HRCU-A-CB-O | 11 | 22.7 | 13.7 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3880 | 12000 | 17300 | 0.177 | 0.999 | 1.68 | 6.4244 | 3.5204 | 3.0179 |  | 3104 | 7700 | 12110 | 0.212 | 0.816 | 1.414 | 4.291 | 2.7655 | 2.51 |  | 2716 |  | 9134 | 0.192 |  | 1.382 | 4.1457 |  | 1.937 | 52.8% | 75.43% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 3942
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056173 | MPB018S4S-1P | MWMA018S4-1P | HRCU-A-CB-O | 10.4 | 21 | 13 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4870 | 18000 | 23000 | 0.231 | 1.589 | 2.4 | 6.1786 | 3.3199 | 2.8086 |  | 3896 | 11400 | 15120 | 0.277 | 1.228 | 1.723 | 4.122 | 2.7207 | 2.5718 |  | 3409 |  | 11178 | 0.25 |  | 1.616 | 3.9963 |  | 2.0272 | 48.6% | 73.93% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 3942
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056174 | MPB018S4S-1P | MWMA018S4-2P | HRCU-A-CB-O | 10.4 | 21 | 13 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4870 | 18000 | 23000 | 0.231 | 1.589 | 2.4 | 6.1786 | 3.3199 | 2.8086 |  | 3896 | 11400 | 15120 | 0.277 | 1.228 | 1.723 | 4.122 | 2.7207 | 2.5718 |  | 3409 |  | 11178 | 0.25 |  | 1.616 | 3.9963 |  | 2.0272 | 48.6% | 73.93% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 826
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056175 | MPB024S4S-1P | MWMA024S4-1P | HRCU-A-CB-O | 11.5 | 20.7 | 13.7 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7100 | 25000 | 32890 | 0.44 | 1.959 | 3.35 | 4.7291 | 3.7401 | 2.8773 |  | 5680 | 15300 | 18925 | 0.528 | 1.661 | 2.618 | 3.1527 | 2.6996 | 2.1186 |  | 4970 |  | 18099 | 0.475 |  | 2.561 | 3.0664 |  | 2.0712 | 55.03% | 95.64% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 826
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10056176 | MPB024S4S-1P | MWMA024S4-2P | HRCU-A-CB-O | 11.5 | 20.7 | 13.7 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7100 | 25000 | 32890 | 0.44 | 1.959 | 3.35 | 4.7291 | 3.7401 | 2.8773 |  | 5680 | 15300 | 18925 | 0.528 | 1.661 | 2.618 | 3.1527 | 2.6996 | 2.1186 |  | 4970 |  | 18099 | 0.475 |  | 2.561 | 3.0664 |  | 2.0712 | 55.03% | 95.64% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 4649
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058825 | MPB018S4S-1P | MCFB018S4-2P | HRCU-A-CB-O | 10.5 | 20 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4826 | 18000 | 23011 | 0.238 | 1.552 | 2.425 | 5.9427 | 3.399 | 2.781 |  | 3964 | 12000 | 14923 | 0.282 | 1.303 | 1.831 | 4.1196 | 2.699 | 2.3886 |  | 3423 |  | 10274 | 0.253 |  | 1.433 | 3.9651 |  | 2.1012 | 44.65% | 68.85% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 509
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058826 | MPB024S4S-1P | MCFA024S4-1P | HRCU-A-CB-O | 11 | 20 | 12.5 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7002 | 24000 | 32821 | 0.448 | 1.733 | 3.368 | 4.5805 | 4.0587 | 2.856 |  | 5592 | 15000 | 18214 | 0.534 | 1.537 | 2.538 | 3.069 | 2.8602 | 2.1032 |  | 4811 |  | 17705 | 0.487 |  | 2.569 | 2.8952 |  | 2.0198 | 53.94% | 97.21% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 509
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058827 | MPB024S4S-1P | MCFA024S4-2P | HRCU-A-CB-O | 11 | 20 | 12.5 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7002 | 24000 | 32821 | 0.448 | 1.733 | 3.368 | 4.5805 | 4.0587 | 2.856 |  | 5592 | 15000 | 18214 | 0.534 | 1.537 | 2.538 | 3.069 | 2.8602 | 2.1032 |  | 4811 |  | 17705 | 0.487 |  | 2.569 | 2.8952 |  | 2.0198 | 53.94% | 97.21% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 1034
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058830 | MPB009S4S-1P | M22A009S4-1P | HRCU-A-CB-O | 10.5 | 20 | 13 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3038 | 10000 | 12680 | 0.152 | 0.85 | 1.336 | 5.8576 | 3.4479 | 2.7815 |  | 2412 | 5800 | 8912 | 0.178 | 0.639 | 1.202 | 3.9713 | 2.6601 | 2.1729 |  | 2102 |  | 7878 | 0.159 |  | 1.172 | 3.8744 |  | 1.97 | 62.13% | 88.4% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 1034
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058831 | MPB009S4S-1P | M22A009S4-2P | HRCU-A-CB-O | 10.5 | 20 | 13 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3038 | 10000 | 12680 | 0.152 | 0.85 | 1.336 | 5.8576 | 3.4479 | 2.7815 |  | 2412 | 5800 | 8912 | 0.178 | 0.639 | 1.202 | 3.9713 | 2.6601 | 2.1729 |  | 2102 |  | 7878 | 0.159 |  | 1.172 | 3.8744 |  | 1.97 | 62.13% | 88.4% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 3550
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058832 | MPB012S4S-1P | M22A012S4-1P | HRCU-A-CB-O | 10.5 | 21.5 | 14 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3883 | 12000 | 17120 | 0.181 | 0.902 | 1.694 | 6.2873 | 3.8989 | 2.9619 |  | 3086 | 7500 | 12012 | 0.219 | 0.82 | 1.523 | 4.1298 | 2.6805 | 2.3115 |  | 2695 |  | 8462 | 0.201 |  | 1.31 | 3.9295 |  | 1.8931 | 49.43% | 70.45% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 3550
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058833 | MPB012S4S-1P | M22A012S4-2P | HRCU-A-CB-O | 10.5 | 21.5 | 14 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3883 | 12000 | 17120 | 0.181 | 0.902 | 1.694 | 6.2873 | 3.8989 | 2.9619 |  | 3086 | 7500 | 12012 | 0.219 | 0.82 | 1.523 | 4.1298 | 2.6805 | 2.3115 |  | 2695 |  | 8462 | 0.201 |  | 1.31 | 3.9295 |  | 1.8931 | 49.43% | 70.45% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 5803
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058834 | MPB018S4S-1P | M22A018S4-1P | HRCU-A-CB-O | 10.3 | 20 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4895 | 18000 | 22688 | 0.244 | 1.499 | 2.412 | 5.8794 | 3.5192 | 2.7567 |  | 3931 | 12000 | 15213 | 0.282 | 1.274 | 1.899 | 4.0853 | 2.7605 | 2.3478 |  | 3535 |  | 9410 | 0.261 |  | 1.391 | 3.9694 |  | 1.9826 | 41.48% | 61.85% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 5803
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058835 | MPB018S4S-1P | M22A018S4-2P | HRCU-A-CB-O | 10.3 | 20 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4895 | 18000 | 22688 | 0.244 | 1.499 | 2.412 | 5.8794 | 3.5192 | 2.7567 |  | 3931 | 12000 | 15213 | 0.282 | 1.274 | 1.899 | 4.0853 | 2.7605 | 2.3478 |  | 3535 |  | 9410 | 0.261 |  | 1.391 | 3.9694 |  | 1.9826 | 41.48% | 61.85% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 3301
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058836 | MPB024S4S-1P | M33A024S4-1P | HRCU-A-CB-O | 10.5 | 20 | 12.5 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7050 | 24400 | 32546 | 0.448 | 2.043 | 3.368 | 4.6119 | 3.5002 | 2.832 |  | 5712 | 15800 | 18628 | 0.541 | 1.809 | 2.639 | 3.0943 | 2.5597 | 2.0687 |  | 4886 |  | 15327 | 0.496 |  | 2.395 | 2.887 |  | 1.8755 | 47.09% | 82.28% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 3301
GD Midea Air-Conditioning Equipment Co.,Ltd | Lennox | MP-Series | 10058836 | MPB024S4S-1P | M33A024S4-2P | HRCU-A-CB-O | 10.5 | 20 | 12.5 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7050 | 24400 | 32546 | 0.448 | 2.043 | 3.368 | 4.6119 | 3.5002 | 2.832 |  | 5712 | 15800 | 18628 | 0.541 | 1.809 | 2.639 | 3.0943 | 2.5597 | 2.0687 |  | 4886 |  | 15327 | 0.496 |  | 2.395 | 2.887 |  | 1.8755 | 47.09% | 82.28% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | 1634.2
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8775842 | MOBA30-09HFN1-MT0W | CCA3U-09HRFN1-M(C) | HRCU-A-CB-O | 10.5 | 20 | 13 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3038 | 10000 | 12680 | 0.152 | 0.85 | 1.336 | 5.8576 | 3.4479 | 2.7815 |  | 2412 | 5800 | 8912 | 0.178 | 0.639 | 1.202 | 3.9713 | 2.6601 | 2.1729 |  | 2102 |  | 7878 | 0.159 |  | 1.172 | 3.8744 |  | 1.97 | 62.13% | 88.4% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8775845 | MOB30-12HFN1-MT0W | CCA3U-12HRFN1-M(C) | HRCU-A-CB-O | 10.5 | 21.5 | 14 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3883 | 12000 | 13353 | 0.181 | 0.902 | 1.09 | 6.2873 | 3.8989 | 3.5903 |  | 3086 | 7500 | 9902 | 0.219 | 0.82 | 1.33 | 4.1298 | 2.6805 | 2.1819 |  | 2695 |  | 8462 | 0.201 |  | 1.31 | 3.9295 |  | 1.8931 | 63.37% | 85.46% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8775849 | MOCA31-18HFN1-MT0W | CCA3U-18HRFN1-M(C) | HRCU-A-CB-O | 10.3 | 20 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4895 | 18000 | 19358 | 0.244 | 1.499 | 1.68 | 5.8794 | 3.5192 | 3.3769 |  | 3931 | 12000 | 13936 | 0.282 | 1.274 | 1.55 | 4.0853 | 2.7605 | 2.635 |  | 3535 |  | 9410 | 0.261 |  | 1.391 | 3.9694 |  | 1.9826 | 48.61% | 67.52% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8952869 | MOB30-09HFN1-MX0W | CS11M-09HRFN1-MX0W(A) | HRCU-A-CB-O | 11.2 | 25 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2760 | 10900 | 15080 | 0.162 | 0.832 | 1.345 | 4.9931 | 3.8395 | 3.2859 |  | 2230 | 6900 | 11390 | 0.191 | 0.741 | 1.668 | 3.4217 | 2.729 | 2.0012 |  | 1931 |  | 10826 | 0.175 |  | 1.71 | 3.2338 |  | 1.8554 | 71.79% | 95.05% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 9680947 | MOBA30-09HFN1-MT0W | CS11M-09HRFN1-MX0W(A) | HRCU-A-CB-O | 10.8 | 23.5 | 14.9 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3009 | 9800 | 13360 | 0.144 | 0.756 | 1.1 | 6.124 | 3.7991 | 3.5595 |  | 2407 | 5800 | 8280 | 0.173 | 0.616 | 1.04 | 4.0776 | 2.7594 | 2.3333 |  | 2106 |  | 7990 | 0.156 |  | 1.175 | 3.9565 |  | 1.9929 | 59.81% | 96.5% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8952870 | MOB30-12HFN1-MV0W | CS11M-12HRFN1-MU5W | HRCU-A-CB-O | 12 | 22.5 | 13 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3658 | 11800 | 15135 | 0.188 | 0.994 | 1.35 | 5.7024 | 3.4791 | 3.2857 |  | 2931 | 7800 | 12448 | 0.226 | 0.866 | 1.96 | 3.8008 | 2.6397 | 1.8613 |  | 2558 |  | 12029 | 0.203 |  | 1.971 | 3.693 |  | 1.7886 | 79.48% | 96.63% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 9680948 | MOCA31-18HFN1-MT0W | CS11M-12HRFN1-MU5W | HRCU-A-CB-O | 11 | 22.7 | 13.7 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3880 | 12000 | 13660 | 0.177 | 0.999 | 1.1 | 6.4244 | 3.5204 | 3.6394 |  | 3104 | 7700 | 9930 | 0.212 | 0.816 | 1.35 | 4.291 | 2.7655 | 2.1557 |  | 2716 |  | 9134 | 0.192 |  | 1.382 | 4.1457 |  | 1.937 | 66.87% | 91.98% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 9680949 | MOCA31-18HFN1-MT0W | CS11M-18HRFN1-MT0W | HRCU-A-CB-O | 10.4 | 21 | 13 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4870 | 18000 | 19590 | 0.231 | 1.589 | 1.71 | 6.1786 | 3.3199 | 3.3575 |  | 3896 | 11400 | 14020 | 0.277 | 1.228 | 1.65 | 4.122 | 2.7207 | 2.4902 |  | 3409 |  | 11178 | 0.25 |  | 1.616 | 3.9963 |  | 2.0272 | 57.06% | 79.73% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8775829 | MOD30-24HFN1-MT0W | CS11M-23HRFN1-MT0W | HRCU-A-CB-O | 11.5 | 20.5 | 13 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7255 | 24000 | 30235 | 0.451 | 1.954 | 3.17 | 4.7145 | 3.5996 | 2.7953 |  | 5813 | 15400 | 26330 | 0.541 | 1.635 | 4.18 | 3.149 | 2.7604 | 1.8461 |  | 5078 |  | 26026 | 0.487 |  | 4.29 | 3.0559 |  | 1.778 | 86.08% | 98.85% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 9680950 | MOD31-24HFN1-MT0W | CS11M-23HRFN1-MT0W | HRCU-A-CB-O | 11.5 | 20.7 | 13.7 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7100 | 25000 | 29740 | 0.44 | 1.959 | 2.66 | 4.7291 | 3.7401 | 3.2767 |  | 5680 | 15300 | 19040 | 0.528 | 1.661 | 2.53 | 3.1527 | 2.6996 | 2.2056 |  | 4970 |  | 18099 | 0.475 |  | 2.561 | 3.0664 |  | 2.0712 | 60.86% | 95.06% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8775852 | MOD31-24HFN1-MT0W | MCDU-24HRFN1-M(C) | HRCU-A-CB-O | 10.5 | 20 | 12.5 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7050 | 24400 | 30246 | 0.448 | 2.043 | 2.65 | 4.6119 | 3.5002 | 3.345 |  | 5712 | 15800 | 19158 | 0.541 | 1.809 | 2.58 | 3.0943 | 2.5597 | 2.1762 |  | 4886 |  | 15327 | 0.496 |  | 2.395 | 2.887 |  | 1.8755 | 50.67% | 80% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8989603 | MOBA30-09HFN1-MT0W | MSAEB-09HRFN1-MT0W | HRCU-A-CB-O | 10 | 20.5 | 14 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3530 | 9800 | 13080 | 0.161 | 0.898 | 1.075 | 6.4257 | 3.1983 | 3.5659 |  | 2610 | 6300 | 8111 | 0.172 | 0.689 | 1.017 | 4.4472 | 2.6797 | 2.3374 |  | 2489 |  | 6609 | 0.159 |  | 1.01 | 4.5878 |  | 1.9177 | 50.53% | 81.48% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 9104551 | MOCA31-18HFN1-MT0W | MSAED-18HRFN1-MT0W | HRCU-A-CB-O | 10 | 22 | 13 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4670 | 18000 | 19190 | 0.231 | 1.669 | 1.674 | 5.9249 | 3.1607 | 3.3596 |  | 3920 | 11100 | 13730 | 0.262 | 1.179 | 1.615 | 4.3849 | 2.7592 | 2.4916 |  | 3274 |  | 12524 | 0.251 |  | 2.087 | 3.8228 |  | 1.7587 | 65.26% | 91.22% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 9104550 | MOD31-24HFN1-MT0W | MSAED-23HRFN1-MT0W | HRCU-A-CB-O | 10 | 20 | 12.5 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7200 | 25000 | 29140 | 0.36 | 2.459 | 2.603 | 5.8614 | 2.9796 | 3.2809 |  | 5690 | 16000 | 18650 | 0.486 | 1.906 | 2.478 | 3.4312 | 2.4602 | 2.2057 |  | 5122 |  | 15815 | 0.471 |  | 2.635 | 3.1871 |  | 1.759 | 54.27% | 84.8% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8775850 | MOCA31-18HFN1-MT0W | MUEU-18HRFN1-M(C) | HRCU-A-CB-O | 10.5 | 20 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4826 | 18000 | 19020 | 0.238 | 1.552 | 1.65 | 5.9427 | 3.399 | 3.3783 |  | 3964 | 12000 | 13823 | 0.282 | 1.303 | 1.531 | 4.1196 | 2.699 | 2.6461 |  | 3423 |  | 10274 | 0.253 |  | 1.433 | 3.9651 |  | 2.1012 | 54.02% | 74.33% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GD Midea Air-Conditioning Equipment Co.,Ltd | DIRECT AIR |  | 8775853 | MOD31-24HFN1-MT0W | MUEU-24HRFN1-M(C) | HRCU-A-CB-O | 11 | 20 | 12.5 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7002 | 24000 | 29873 | 0.448 | 1.733 | 2.69 | 4.5805 | 4.0587 | 3.2546 |  | 5592 | 15000 | 18214 | 0.534 | 1.537 | 2.538 | 3.069 | 2.8602 | 2.1032 |  | 4811 |  | 17705 | 0.487 |  | 2.569 | 2.8952 |  | 2.0198 | 59.27% | 97.21% | Integrated | 15000% | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | 0 | 0 |  | 0 | 0 | 0 | #DIV/0! | #DIV/0!
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | TOSOT |  | 10062018 | TW09HQ3D6DO | TW09HQ3D6DI | HRCU-A-CB-O | 15 | 38 | 16.5 | 9000 | YES | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2300 | 9000 | 13600 | 0.2 | 0.59 | 1.5 | 3.3703 | 4.4706 | 2.6572 |  | 3545 | 5600 | 14610.8 | 0.365 | 0.74596 | 1.7826 | 2.8464 | 2.2001 | 2.4021 |  | 1745 |  | 12976.6 | 0.28 |  | 1.8216 | 1.8265 |  | 2.0878 | 95.42% | 88.82% | Integrated | 72W | Heater on below 34°F | N/A | [7 empty] | 1000
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | TOSOT |  | 10062019 | TW12HQ3D6DO | TW12HQ3D6DI | HRCU-A-CB-O | 14 | 30.5 | 15.3 | 12000 | YES | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 |  | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 |  | 2600 |  | 8000 | 0.22 |  | 0.86 | 3.4636 |  | 2.7262 | 42.78% | 88.89% | Integrated | 72W | Heater on below 34°F | N/A | [7 empty] | 1500
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | TOSOT |  | 10062020 | TW18HQ3D6DO | TW18HQ3D6DI | HRCU-A-CB-O | 12 | 24.5 | 13.5 | 18000 | YES | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3900 | 18000 | 26000 | 0.32 | 1.5 | 3.3 | 3.57 | 3.52 | 2.31 |  | 3700 | 14000 | 23000 | 0.31 | 1.45 | 3.2 | 3.5 | 2.83 | 2.11 |  | 3500 |  | 21500 | 0.3 |  | 3.1 | 3.42 |  | 2.03 | 82.69% | 93.48% | Integrated | 16000% | Under heating mode, the compressor in opening condition, while the outdoor ambient temperature ia below 0 ℃, the chassis heating begin to work. | N/A | [7 empty] | 3709.68
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | TOSOT |  | 10062021 | TW24HQ3D6DO | TW24HQ3D6DI | HRCU-A-CB-O | 12 | 21.5 | 13 | 22000 | YES | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6800 | 24000 | 32000 | 0.38 | 2 | 3.7 | 5.2446 | 3.517 | 2.5348 |  | 4500 | 15737 | 26263 | 0.5 | 1.57 | 3.38 | 2.6377 | 2.9377 | 2.2773 |  | 4000 |  | 22553.32 | 0.6 |  | 3.2 | 1.9539 |  | 2.0656 | 70.48% | 85.87% | Integrated | 16000% | If T outer ring is less than T chassis electric heating open temperature, then the chassis electric heating work； | N/A | [7 empty] | 4644
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Tosot | Multi Zone | 10064019 | TM24H4O | Non-Ducted Indoor Units | HMSV-A-CB | 11 | 21 | 12.5 | 24000 | Yes | Ductless | Multizone | Non-ducted indoor units (Mini-splits) | 7500 | 29000 | 35000 | 0.95 | 2.32 | 4.55 | 2.3137 | 3.6634 | 2.2544 |  | 17900 | 18800 | 23000 | 1.96 | 2 | 2.23 | 2.6765 | 2.7549 | 3.0227 |  | 17800 |  | 18356 | 2.79 |  | 2.97 | 1.8698 |  | 1.8113 | 52.45% | 79.81% | Integrated | 160W% | Heater on at or below 34°F, during defrost only | N/A | [7 empty] | 4644
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Tosot | Multi Zone | 10064021 | TM30H4O | Non-Ducted Indoor Units | HMSV-A-CB | 11.5 | 21 | 12.5 | 28400 | Yes | Ductless | Multizone | Non-ducted indoor units (Mini-splits) | 8189 | 30000 | 32414 | 1.05 | 2.35 | 2.65 | 2.2857 | 3.7413 | 3.5848 |  | 17800 | 18100 | 24000 | 1.98 | 2.03 | 2.25 | 2.6347 | 2.6131 | 3.1261 |  | 18800 |  | 19356 | 2.89 |  | 3.01 | 1.9065 |  | 1.8846 | 59.71% | 80.65% | Integrated | 96W | Heater on at or below 34°F, during defrost only | N/A | [7 empty] | 6144
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Tosot | Multi Zone | 10064023 | TM36H4O | Non-Ducted Indoor Units | HMSV-A-CB | 11.5 | 21 | 12.5 | 34000 | Yes | Ductless | Multizone | Non-ducted indoor units (Mini-splits) | 8871 | 42500 | 44356 | 1.25 | 3.37 | 3.6 | 2.0799 | 3.696 | 3.611 |  | 19800 | 26500 | 27500 | 2.01 | 2.7 | 2.95 | 2.887 | 2.8764 | 2.732 |  | 20800 |  | 21356 | 2.99 |  | 3.12 | 2.0388 |  | 2.006 | 48.15% | 77.66% | Integrated | 96W | Heater on at or below 34°F, during defrost only | N/A | [7 empty] | 2752
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Tosot | Lomo Plus | 10062018 | TW09HQ3D6DO | TW09HQ3D6DI | HRCU-A-CB-O | 15 | 38 | 16.5 | 9000 | Yes | Ductless | Single zone | Non-ducted indoor units (Mini-splits) | 2300 | 9000 | 13600 | 0.2 | 0.59 | 1.5 | 3.3703 | 4.4706 | 2.6572 |  | 3545 | 5600 | 14610.8 | 0.365 | 0.74596 | 1.7826 | 2.8464 | 2.2001 | 2.4021 |  | 1745 |  | 12976.6 | 0.28 |  | 1.8216 | 1.8265 |  | 2.0878 | 95.42% | 88.82% | Integrated | 72W | Heater on below 34°F | N/A | [7 empty] | 0
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Tosot | Lomo Plus | 10062020 | TW18HQ3D6DO | TW18HQ3D6DI | HRCU-A-CB-O | 12 | 24.5 | 13.5 | 18000 | Yes | Ductless | Single zone | Non-ducted indoor units (Mini-splits) | 3900 | 18000 | 26000 | 0.32 | 1.5 | 3.3 | 3.5718 | 3.5169 | 2.309 |  | 3700 | 14000 | 23000 | 0.31 | 1.45 | 3.2 | 3.4979 | 2.8297 | 2.1064 |  | 3500 |  | 21500 | 0.3 |  | 3.1 | 3.4192 |  | 2.0326 | 82.69% | 93.48% | Interated | 160W | Heater on below 32°F during compressor operation only. | N/A | [7 empty] | 5376
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Tosot | Lomo Plus | 10062021 | TW24HQ3D6DO | TW24HQ3D6DI | HRCU-A-CB-O | 12 | 21.5 | 13 | 24000 | Yes | Ductless | Single zone | Non-ducted indoor units (Mini-splits) | 6800 | 24000 | 32000 | 0.38 | 2 | 3.7 | 5.2444 | 3.5169 | 2.5347 |  | 4500 | 15737 | 26263 | 0.5 | 1.57 | 3.38 | 2.6376 | 2.9376 | 2.2772 |  | 4000 |  | 22553.32 | 0.6 |  | 3.2 | 1.9538 |  | 2.0655 | 70.48% | 85.87% | Integrated | 160W | Heater on below 32°F during compressor operation only. | N/A | [7 empty] | 1500
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Tosot | Lomo Plus | 10062019 | TW12HQ3D6DO | TW12HQ3D6DI | HRCU-A-CB-O | 14 | 30.5 | 15.3 | 12000 | Yes | Ductless | Single zone | Non-ducted indoor units (Mini-splits) | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 |  | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 |  | 2600 |  | 8000 | 0.22 |  | 0.86 | 3.4636 |  | 2.7262 | 42.78% | 88.89% | Integrated | 72W | Heater on below 34°F | N/A | [7 empty] | 3710
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Free Match G-Series | 9084225 | GWHD(24)ND3GO | Non-Ducted Indoor Units | HMSV-A-CB | 11 | 21 | 12.5 | 24000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7500 | 29000 | 35000 | 0.95 | 2.32 | 4.55 | 2.3137 | 3.6634 | 2.2544 |  | 17900 | 18800 | 23000 | 1.96 | 2 | 2.23 | 2.6765 | 2.7549 | 3.0227 |  | 17800 |  | 18356 | 2.79 |  | 2.97 | 1.8698 |  | 1.8113 | 52.45% | 79.81% | Integrated | 160 | When ambient temp ≤ 1 degree celsius | N/A | [7 empty] | 4644
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Free Match G-Series | 9084226 | GWHD(30)ND3GO | Non-Ducted Indoor Units | HMSV-A-CB | 11.5 | 21 | 12.5 | 28400 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 8189 | 30000 | 32414 | 1.05 | 2.35 | 2.65 | 2.2857 | 3.7413 | 3.5848 |  | 17800 | 18100 | 24000 | 1.98 | 2.03 | 2.25 | 2.6347 | 2.6131 | 3.1261 |  | 18800 |  | 19356 | 2.89 |  | 3.01 | 1.9065 |  | 1.8846 | 59.71% | 80.65% | Integrated | 96 | When ambient temp ≤ 1 degree celsius | N/A | [7 empty] | 6144
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Free Match G-Series | 9084227 | GWHD(36)ND3GO | Non-Ducted Indoor Units | HMSV-A-CB | 11.5 | 21 | 12.5 | 34000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 8871 | 42500 | 44356 | 1.25 | 3.37 | 3.6 | 2.0799 | 3.696 | 3.611 |  | 19800 | 26500 | 27500 | 2.01 | 2.7 | 2.95 | 2.887 | 2.8764 | 2.732 |  | 20800 |  | 21356 | 2.99 |  | 3.12 | 2.0388 |  | 2.006 | 48.15% | 77.66% | Integrated | 96 | When ambient temp ≤ 1 degree celsius | N/A | [7 empty] | 2752
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | U-Crown Series | 7607465 | GWH09UC-D3DNA4C/O | GWH09UC-D3DN***/I | HRCU-A-CB-O | 10.5 | 30.5 | 15.7 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.35 | 3.4993 | 4.324 | 2.8743 |  | 2388 | 5500 | 13240 | 0.2 | 0.56 | 1.35 | 3.4993 | 2.8784 | 2.8743 |  | 2388 |  | 10488 | 0.4 |  | 1.55 | 1.7496 |  | 1.9831 | 79.21% | 79.21% | Integrated | 72W | Heater on below 34°F of outdoor temperature | N/A | [7 empty] | 0
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | U-Crown Series | 7607467 | GWH12UC-D3DNA4C/O | GWH12UC-D3DN***/I | HRCU-A-CB-O | 10.5 | 23 | 12.7 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.21 | 1.22 | 4.5001 | 3.1487 | 3.1229 |  | 3071 | 13000 | 13000 | 0.2 | 1.21 | 1.22 | 4.5001 | 3.1487 | 3.1229 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.2501 |  | 2.7608 | 100% | 100% | Integrated | 72W | Heater on below 34°F of outdoor temperature | N/A | [7 empty] | 5376
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | U-Crown Series | 7607469 | GWH18UC-D3DNA4C/O | GWH18UC-D3DN***/I | HRCU-A-CB-O | 10.5 | 21 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.8 | 2.5 | 3.1426 | 3.0935 | 2.8798 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.1426 | 2.5013 | 2.8798 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.9998 |  | 2.8548 | 78.12% | 78.12% | Integrated | 72W | Heater on below 34°F of outdoor temperature | N/A | [7 empty] | 1500
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Extreme Series | 9114294 | GWH18YE-D3DNA1A/O | GWH18AAE-D3DN***/I | HRCU-A-CB-O | 12 | 24.5 | 13.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3900 | 18000 | 26000 | 0.32 | 1.5 | 3.3 | 3.5718 | 3.5169 | 2.309 |  | 3700 | 14000 | 23000 | 0.31 | 1.45 | 3.2 | 3.4979 | 2.8297 | 2.1064 |  | 3500 |  | 21500 | 0.3 |  | 3.1 | 3.4192 |  | 2.0326 | 82.69% | 93.48% | N/A |  |  | N/A | [7 empty] | 3710
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Extreme Series | 9123256 | GWH24YE-D3DNA1A/O | GWH24AAE-D3DN***/I | HRCU-A-CB-O | 12 | 21.5 | 13 | 22000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6800 | 24000 | 32000 | 0.38 | 2 | 3.7 | 5.2444 | 3.5169 | 2.5347 |  | 4500 | 15737 | 26263 | 0.5 | 1.57 | 3.38 | 2.6376 | 2.9376 | 2.2772 |  | 4000 |  | 22553 | 0.6 |  | 3.2 | 1.9538 |  | 2.0655 | 70.48% | 85.87% | N/A |  |  | N/A | [7 empty] | 1634
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Extreme Series | 9944775 | GWH09YD-D3DNA1A/O | GWH09AAD-D3DN***/I | HRCU-A-CB-O | 15 | 38 | 16.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2300 | 9000 | 13600 | 0.2 | 0.59 | 1.5 | 3.3703 | 4.4706 | 2.6572 |  | 3545 | 5600 | 14611 | 0.37 | 0.75 | 1.78 | 2.8079 | 2.1883 | 2.4057 |  | 1745 |  | 12977 | 0.28 |  | 1.82 | 1.8265 |  | 2.0897 | 95.42% | 88.82% | N/A |  |  | N/A | [7 empty] | 1000
GREE ELECTRIC APPLIANCES INC. OF ZHUHAI GREE ELECTRIC APPLIANCES INC. OF ZHUHAI | Gree | Extreme Series | 9944776 | GWH12YD-D3DNA1A/O | GWH12AAD-D3DN***/I | HRCU-A-CB-O | 14 | 30.5 | 15.3 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 |  | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 |  | 2600 |  | 8000 | 0.22 |  | 0.86 | 3.4636 |  | 2.7262 | 42.78% | 88.89% | N/A |  |  | N/A | [7 empty] | 1190
Haier | Haier | Novel Series | 6970203 | HSU09VHG(DB)-W | HSU09VHG(DB)-G | HRCU-A-CB-O | 10 | 18 | 13 | 8500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4000 | 9000 | 10140 | 0.27 | 0.65 | 0.82 | 4.342 | 4.0581 | 3.6242 |  | 3200 | 5600 | 7190 | 0.27 | 0.52 | 0.64 | 3.4736 | 3.1563 | 3.2926 |  | 2800 |  | 6000 | 0.27 |  | 0.75 | 3.0394 |  | 2.3447 | 59.17% | 83.45% | N/A |  |  | N/A |  | z | [5 empty] | 3140
Haier | Haier | Novel Series | 6970204 | HSU12VHG(DB)-W | HSU12VHG(DB)-G | HRCU-A-CB-O | 10 | 20 | 13 | 11900 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4780 | 12600 | 14190 | 0.271 | 0.97 | 1.12 | 5.16 | 3.8071 | 3.71 |  | 3750 | 9000 | 10070 | 0.37 | 1.12 | 1.2 | 2.91 | 2.34 | 2.45 |  | 2380 |  | 6930 | 0.24 |  | 0.88 | 2.82 |  | 2.3 | 48.84% | 68.82% | N/A |  |  | N/A |  | z | [5 empty] | 2960
Haier | Haier | Advanced Series | 8021588 | 1U12ES2VHA | AW12ES2VHA | HRCU-A-CB-O | 11 | 23 | 12.5 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4100 | 16000 | 19800 | 0.225 | 1.25 | 1.66 | 5.33 | 3.7515 | 3.49 |  | 3550 | 12220 | 13120 | 0.33 | 1.19 | 1.25 | 3.11 | 3 | 3.07 |  | 2960 |  | 10160 | 0.3 |  | 1.21 | 2.85 |  | 2.46 | 51.31% | 77.44% | N/A |  |  | N/A |  | z | [5 empty] | 4700
Haier | Haier | Advanced Series | 8028490 | 1U18ES2VHA | AW18ES2VHA | HRCU-A-CB-O | 11 | 21 | 12.6 | 17000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5400 | 22000 | 26400 | 0.4 | 1.83 | 2.9 | 3.96 | 3.5234 | 2.67 |  | 4500 | 14000 | 19600 | 0.45 | 1.5 | 2.7 | 2.93 | 2.74 | 2.13 |  | 3800 |  | 14900 | 0.43 |  | 2.1 | 2.59 |  | 2.08 | 56.44% | 76.02% | N/A |  |  | N/A |  | z | [5 empty] | 5500
Haier | Haier | Advanced Series | 8028525 | 1U24ES2VHA | AW24ES2VHA | HRCU-A-CB-O | 10 | 20 | 12.5 | 22000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6800 | 27700 | 34800 | 0.55 | 2.35 | 3.3 | 3.62 | 3.4546 | 3.09 |  | 5800 | 18500 | 26000 | 0.58 | 1.9 | 3.25 | 2.93 | 2.85 | 2.35 |  | 4700 |  | 20500 | 0.55 |  | 2.8 | 2.51 |  | 2.15 | 58.91% | 78.85% | N/A |  |  | N/A |  | z | [5 empty] | 800
Haier | Haier | Advanced Series | 8028528 | 1U09ES2VHA | AW09ES2VHA | HRCU-A-CB-O | 12 | 23.5 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4000 | 10000 | 15000 | 0.25 | 0.65 | 1.2 | 4.69 | 4.509 | 3.66 |  | 3200 | 7400 | 10800 | 0.27 | 0.63 | 1.1 | 3.54 | 3.44 | 2.88 |  | 2800 |  | 10000 | 0.26 |  | 1.18 | 3.16 |  | 2.48 | 66.67% | 92.59% | N/A |  |  | N/A |  | z | [5 empty] | 0
Haier | Haier | Arctic Series | 8862047 | 1U09EH2VHA | AW09EH2VHA | HRCU-A-CB-O | 13 | 28 | 15.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4000 | 12000 | 22000 | 0.245 | 0.9 | 1.65 | 4.785 | 3.9078 | 3.908 |  | 3100 | 9000 | 12000 | 0.26 | 0.82 | 1.18 | 3.494 | 3.217 | 2.981 |  | 2800 |  | 12000 | 0.26 |  | 1.58 | 3.156 |  | 2.226 | 54.55% | 100% | Integrated | 300W | Mainly depending on outdoor temperature, but also subject to other running parameters, pressure, compressor speed etc. | N/A |  | z | [5 empty] | 0
Haier | Haier | Arctic Series | 8862052 | 1U12EH2VHA | AW12EH2VHA | HRCU-A-CB-O | 12 | 25 | 13 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4100 | 16500 | 22200 | 0.225 | 1.345 | 1.69 | 5.341 | 3.5954 | 3.85 |  | 3200 | 10000 | 16500 | 0.33 | 1.185 | 1.595 | 2.842 | 2.473 | 3.032 |  | 2900 |  | 16500 | 0.3 |  | 2.152 | 2.833 |  | 2.247 | 74.32% | 100% | Integrated | 300W | Mainly depending on outdoor temperature, but also subject to other running parameters, pressure, compressor speed etc. | N/A |  | z | [5 empty] | 0
Haier | Haier | Arctic Series | 8862057 | 1U18EH2VHA | AW18EH2VHA | HRCU-A-CB-O | 10 | 20 | 12.5 | 19000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6800 | 20400 | 26400 | 0.55 | 1.64 | 3.1 | 3.624 | 3.6457 | 2.496 |  | 5800 | 18500 | 20400 | 0.58 | 1.9 | 2.95 | 2.931 | 2.854 | 2.027 |  | 4700 |  | 20400 | 0.55 |  | 3.15 | 2.505 |  | 1.898 | 77.27% | 100% | Integrated | 300W | Mainly depending on outdoor temperature, but also subject to other running parameters, pressure, compressor speed etc. | N/A |  | z |  |  | 1.367 | 1.166 | 1.835 | 2752
International Comfort Products | HEIL | High Wall System | 8177081 | DLCAHB09K1A | DLFAHH09K1A | HRCU-A-CB-O | 10.3 | 30.5 | 15.7 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.3242 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 3003 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835 | 2752
International Comfort Products | KEEPRITE | High Wall System | 8177082 | DLCAHB09K1A | DLFAHH09K1A | HRCU-A-CB-O | 10.3 | 30.5 | 15.7 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 3004 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835 | 2752
International Comfort Products | TEMPSTAR | High Wall System | 8177083 | DLCAHB09K1A | DLFAHH09K1A | HRCU-A-CB-O | 10.3 | 30.5 | 15.7 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 3006 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835 | 2752
International Comfort Products | DAY & NIGHT | High Wall System | 8177084 | DLCAHB09K1A | DLFAHH09K1A | HRCU-A-CB-O | 10.3 | 30.5 | 15.7 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 3002 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835 | 2752
International Comfort Products | ARCOAIRE | High Wall System | 8177085 | DLCAHB09K1A | DLFAHH09K1A | HRCU-A-CB-O | 10.3 | 30.5 | 15.7 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835 | 2752
International Comfort Products | KENMORE | High Wall System | 8177086 | DLCAHB09K1A | DLFAHH09K1A | HRCU-A-CB-O | 10.3 | 30.5 | 15.7 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 3005 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.367 | 1.166 | 1.835 | 2752
International Comfort Products | COMFORTMAKER | High Wall System | 8177087 | DLCAHB09K1A | DLFAHH09K1A | HRCU-A-CB-O | 10.3 | 30.5 | 15.7 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2388 | 9000 | 13240 | 0.2 | 0.61 | 1.345 | 3.499 | 4.32 | 2.885 |  | 2388 | 5500 | 13240 | 0.2 | 0.557 | 1.345 | 3.499 | 2.893 | 2.885 |  | 2388 |  | 10488 | 0.4 |  | 1.553 | 1.749 |  | 1.979 | 79.21% | 79.21% | Integrated | 3001 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 2388 | z | 8560 | 0.6 | 1.44 | 1.5 | 1.99 | 0
International Comfort Products | HEIL | High Wall System | 8177090 | DLCAHB12K1A | DLFAHH12K1A | HRCU-A-CB-O | 10.3 | 23 | 12.7 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 2997 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99 | 0
International Comfort Products | KEEPRITE | High Wall System | 8177091 | DLCAHB12K1A | DLFAHH12K1A | HRCU-A-CB-O | 10.3 | 23 | 12.7 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 2998 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99 | 0
International Comfort Products | TEMPSTAR | High Wall System | 8177092 | DLCAHB12K1A | DLFAHH12K1A | HRCU-A-CB-O | 10.3 | 23 | 12.7 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99 | 0
International Comfort Products | DAY & NIGHT | High Wall System | 8177093 | DLCAHB12K1A | DLFAHH12K1A | HRCU-A-CB-O | 10.3 | 23 | 12.7 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 2996 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99 | 0
International Comfort Products | ARCOAIRE | High Wall System | 8177094 | DLCAHB12K1A | DLFAHH12K1A | HRCU-A-CB-O | 10.3 | 23 | 12.7 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 2994 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99 | 0
International Comfort Products | KENMORE | High Wall System | 8177095 | DLCAHB12K1A | DLFAHH12K1A | HRCU-A-CB-O | 10.3 | 23 | 12.7 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 2999 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 1.44 | 1.5 | 1.99 | 0
International Comfort Products | COMFORTMAKER | High Wall System | 8177096 | DLCAHB12K1A | DLFAHH12K1A | HRCU-A-CB-O | 10.3 | 23 | 12.7 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 | 13000 | 13000 | 0.2 | 1.212 | 1.22 | 4.5 | 3.143 | 3.12 |  | 3071 |  | 13000 | 0.4 |  | 1.38 | 2.25 |  | 2.76 | 100% | 100% | Integrated | 2995 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3071 | z | 9800 | 0.6 | 2.14 | 1.466 | 2.113 | 5376
International Comfort Products | HEIL | High Wall System | 8177099 | DLCAHB18K1A | DLFAHH18K1A | HRCU-A-CB-O | 10.3 | 21 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 3003 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113 | 5376
International Comfort Products | KEEPRITE | High Wall System | 8177100 | DLCAHB18K1A | DLFAHH18K1A | HRCU-A-CB-O | 10.3 | 21 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 3004 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113 | 5376
International Comfort Products | TEMPSTAR | High Wall System | 8177101 | DLCAHB18K1A | DLFAHH18K1A | HRCU-A-CB-O | 10.3 | 21 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 3006 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113 | 5376
International Comfort Products | DAY & NIGHT | High Wall System | 8177102 | DLCAHB18K1A | DLFAHH18K1A | HRCU-A-CB-O | 10.3 | 21 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 3002 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113 | 5376
International Comfort Products | ARCOAIRE | High Wall System | 8177103 | DLCAHB18K1A | DLFAHH18K1A | HRCU-A-CB-O | 10.3 | 21 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 3000 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113 | 5376
International Comfort Products | KENMORE | High Wall System | 8177104 | DLCAHB18K1A | DLFAHH18K1A | HRCU-A-CB-O | 10.3 | 21 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 3005 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75 | 2.14 | 1.466 | 2.113 | 5376
International Comfort Products | COMFORTMAKER | High Wall System | 8177105 | DLCAHB18K1A | DLFAHH18K1A | HRCU-A-CB-O | 10.3 | 21 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3753 | 19000 | 24566 | 0.35 | 1.797 | 2.5 | 3.14 | 3.098 | 2.879 |  | 3753 | 12717 | 24566 | 0.35 | 1.49 | 2.5 | 3.14 | 2.501 | 2.879 |  | 3753 |  | 19190 | 0.55 |  | 1.97 | 1.999 |  | 2.85 | 78.12% | 78.12% | Integrated | 3001 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | -22 | 3753 | z | 15430 | 0.75
Lennox Industries | Lennox | Elite XP20 Series | 8550469 | XP20-036-230A** | CBX32MV-036-230 | HRCU-A-CB | 10 | 20 | 13.5 | 34400 | Yes | Centrally Ducted | N/A | N/A | 10400 | 33200 | 33200 | 0.64 | 3 | 3 | 4.7624 | 3.2433 | 3.2433 |  | 21800 | 21800 | 21800 | 2.7 | 2.7 | 2.7 | 2.3663 | 2.3663 | 2.3663 |  | 19000 |  | 19000 | 2.7 |  | 2.7 | 2.0624 |  | 2.0624 | 57.23% | 87.16% | N/A |  |  |  | 0 |  | 0
Lennox Industries | Lennox | Elite XP20 Series | 8550470 | XP20-036-230A** | CBX40UHV-036-230 | HRCU-A-CB | 10 | 20 | 13.5 | 34400 | Yes | Centrally Ducted | N/A | N/A | 10400 | 33000 | 33000 | 0.64 | 3 | 3 | 4.7624 | 3.2238 | 3.2238 |  | 21800 | 21800 | 21800 | 2.7 | 2.7 | 2.7 | 2.3663 | 2.3663 | 2.3663 |  | 19000 |  | 19000 | 2.6 |  | 2.6 | 2.1417 |  | 2.1417 | 57.58% | 87.16% | N/A |  |  |  | 0 |  | 0 |  |  |  |  | 2894
Lennox Industries, Inc. | Lennox | ML-Series | 8994418 | MLA030S4M-1P | Non-Ducted Indoor Units | N/A | 10.4 | 22 | 13 |  | Yes | Ductless | Multi-zone | N/A | 5820 | 28000 | 37720 | 0.895 | 2.345 | 3.475 | 1.9058 | 3.4994 | 3.1812 |  | 5411 | 18000 | 31054 | 0.924 | 1.925 | 4.176 | 1.7162 | 2.7404 | 2.1794 |  | 5145 |  | 28160 | 1.008 |  | 4.041 | 1.4959 |  | 2.0423 | 74.66% | 90.68% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0 |  |  |  |  | 2125
Lennox Industries, Inc. | Lennox | ML-Series | 8994421 | MLA036S4M-1P | Non-Ducted Indoor Units | N/A | 10.5 | 21.5 | 13.5 |  | Yes | Ductless | Multi-zone | N/A | 7210 | 36000 | 50350 | 1.02 | 2.777 | 4.64 | 2.0716 | 3.7993 | 3.1802 |  | 6845 | 23200 | 38125 | 1.091 | 2.446 | 5.502 | 1.8387 | 2.7797 | 2.0308 |  | 6425 |  | 36000 | 1.146 |  | 5.379 | 1.6431 |  | 1.9614 | 71.5% | 94.43% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0 |  |  |  |  | 1285
Lennox Industries, Inc. | Lennox | ML-Series | 9920038 | MLA009S4S-1P | MWMA009S4-2P | HRCU-A-CB-O | 10.5 | 24 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2750 | 10900 | 14360 | 0.159 | 0.828 | 1.35 | 5.0688 | 3.8581 | 3.1174 |  | 2200 | 6900 | 12115 | 0.191 | 0.738 | 1.815 | 3.3757 | 2.7401 | 1.9562 |  | 1925 |  | 10830 | 0.172 |  | 1.7 | 3.28 |  | 1.867 | 75.42% | 89.39% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 1121
Lennox Industries, Inc. | Lennox | ML-Series | 9920041 | MLA012S4S-1P | MWMA012S4-2P | HRCU-A-CB-O | 10 | 22 | 12.5 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3660 | 12000 | 15600 | 0.188 | 0.994 | 1.8 | 5.7055 | 3.5381 | 2.5399 |  | 2928 | 7800 | 13159 | 0.226 | 0.866 | 2.105 | 3.797 | 2.6397 | 1.8321 |  | 2562 |  | 12038 | 0.203 |  | 1.972 | 3.6988 |  | 1.789 | 77.17% | 91.48% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 1125
Lennox Industries, Inc. | Lennox | ML-Series | 9920047 | MLA024S4S-1P | MWMA024S4-2P | HRCU-A-CB-O | 10 | 20 | 12.5 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7260 | 24000 | 31200 | 0.451 | 1.954 | 3.27 | 4.7177 | 3.5996 | 2.7963 |  | 5808 | 15400 | 27155 | 0.541 | 1.635 | 4.33 | 3.1463 | 2.7604 | 1.838 |  | 5082 |  | 26030 | 0.487 |  | 4.29 | 3.0583 |  | 1.7782 | 83.43% | 95.86% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | 1285
Lennox Industries, Inc. | Lennox | ML-Series | 8898932 | MLA009S4S-1P | MWMA009S4-1P | N/A | 10.5 | 24 | 14.5 |  | Yes | Ductless | Single-zone | N/A | 2750 | 10900 | 14360 | 0.159 | 0.828 | 1.35 | 5.0688 | 3.8581 | 3.1174 |  | 2200 | 6900 | 12115 | 0.191 | 0.738 | 1.815 | 3.3757 | 2.7401 | 1.9562 |  | 1925 |  | 10830 | 0.172 |  | 1.7 | 3.28 |  | 1.867 | 75.42% | 89.39% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0 |  |  |  |  | 645
Lennox Industries, Inc. | Lennox | ML-Series | 8898934 | MLA012S4S-1P | MMDA012S4-1P | N/A | 10 | 19 | 12.5 |  | Yes | Ductless | Single-zone | N/A | 3752 | 12000 | 17021 | 0.189 | 0.961 | 1.692 | 5.818 | 3.6596 | 2.9482 |  | 3292 | 8500 | 12986 | 0.232 | 0.966 | 2.028 | 4.1586 | 2.5788 | 1.8766 |  | 2718 |  | 12341 | 0.205 |  | 2.031 | 3.8857 |  | 1.7808 | 72.5% | 95.03% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0 |  |  |  |  | 1121
Lennox Industries, Inc. | Lennox | ML-Series | 8898935 | MLA012S4S-1P | MWMA012S4-1P | N/A | 10 | 22 | 12.5 |  | Yes | Ductless | Single-zone | N/A | 3660 | 12000 | 15600 | 0.188 | 0.994 | 1.8 | 5.7055 | 3.5381 | 2.5399 |  | 2928 | 7800 | 13159 | 0.226 | 0.866 | 2.105 | 3.797 | 2.6397 | 1.8321 |  | 2562 |  | 12038 | 0.203 |  | 1.972 | 3.6988 |  | 1.789 | 77.17% | 91.48% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0 |  |  |  |  | 1125
Lennox Industries, Inc. | Lennox | ML-Series | 8898941 | MLA024S4S-1P | MWMA024S4-1P | N/A | 10 | 20 | 12.5 |  | Yes | Ductless | Single-zone | N/A | 7260 | 24000 | 31200 | 0.451 | 1.954 | 3.27 | 4.7177 | 3.5996 | 2.7963 |  | 5808 | 15400 | 27155 | 0.541 | 1.635 | 4.33 | 3.1463 | 2.7604 | 1.838 |  | 5082 |  | 26030 | 0.487 |  | 4.29 | 3.0583 |  | 1.7782 | 83.43% | 95.86% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0 |  |  |  |  | 930
LG Electronics Canada, Inc. | LG | Prestige (Canada) | 6233140 | LAU120HYV | LAN120HYV | HRCU-A-CB-O | 11.5 | 25.5 | 14.1 | 12000 | Yes | Ductless | Single-Zone | Non-ducted indoor units (Mini-splits) | 1023 | 13600 | 22178 | 0.06 | 0.86 | 1.98 | 4.9969 | 4.6346 | 3.2827 |  | 676 | 8350 | 14650 | 0.07 | 0.69 | 1.5 | 2.8302 | 3.5466 | 2.8623 |  | 633 |  | 13720 | 0.07 |  | 1.47 | 2.6502 |  | 2.7353 | 61.86% | 93.65% | Integrated | 90 | Heater on when ambient temperature is equal and less than 0C; Heater off when ambient temperature is equal and greater than 1C; 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A | [7 empty] | 3040
LG Electronics Canada, Inc. | LG | Prestige (Canada) | 8584525 | LAU180HYV1 | LAN180HYV1 | HRCU-A-CB-O | 12.5 | 24 | 13.5 | 18200 | Yes | Ductless | Single-Zone | Non-ducted indoor units (Mini-splits) | 3070 | 22000 | 30709 | 0.55 | 1.69 | 2.49 | 1.6359 | 3.8151 | 3.6144 |  | 2333 | 13000 | 22340 | 0.24 | 1.37 | 2.44 | 2.8489 | 2.781 | 2.6833 |  | 1929 |  | 19300 | 0.24 |  | 2.39 | 2.3556 |  | 2.3666 | 62.85% | 86.39% | Integrated | 121 | Heater on when ambient temperature is equal and less than 0C; Heater off when ambient temperature is equal and greater than 1C; 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A | [7 empty] | 3720
LG Electronics Canada, Inc. | LG | Prestige (Canada) | 8584526 | LAU240HYV1 | LAN240HYV1 | HRCU-A-CB-O | 12 | 22 | 12.5 | 22000 | Yes | Ductless | Single-Zone | Non-ducted indoor units (Mini-splits) | 3070 | 27000 | 35200 | 0.55 | 2.2 | 3.24 | 1.6359 | 3.5968 | 3.184 |  | 2333 | 17200 | 27410 | 0.24 | 1.8 | 3.16 | 2.8489 | 2.8005 | 2.5421 |  | 1929 |  | 23690 | 0.24 |  | 3.1 | 2.3556 |  | 2.2396 | 67.3% | 86.43% | Integrated | 120 | Heater on when ambient temperature is equal and less than 0C; Heater off when ambient temperature is equal and greater than 1C; 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A | [7 empty] | 6502
LG Electronics USA, Inc | LG |  | 7180062 | LMU24CHV | Non-Ducted Indoor Units | HMSV-A-CB | 10.6 | 21.7 | 13.5 | 20000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 9240 | 24000 | 28800 | 1.092 | 1.8 | 2.52 | 2.5 | 3.9 | 3.3 |  | 5580 | 14500 | 21097 | 0.945 | 1.56 | 1.71 | 1.7 | 2.7 | 3.6 |  | 4332 |  | 14595 | 0.917 |  | 1.65 | 1.4 |  | 2.6 | 50.68% | 69.18% | Optional Accessory #PQSH1200 | 120W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z | [5 empty] | 7048
LG Electronics USA, Inc | LG |  | 7180063 | LMU36CHV | Non-Ducted Indoor Units | HMSV-A-CB | 10 | 22 | 13 | 32000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 9240 | 36000 | 41600 | 1.127 | 2.74 | 3.836 | 2.4 | 3.9 | 3.2 |  | 5658 | 20000 | 29105 | 0.924 | 2.24 | 2.79 | 1.8 | 2.6 | 3.1 |  | 4446 |  | 22057 | 0.868 |  | 2.6 | 1.5 |  | 2.5 | 53.02% | 75.78% | Optional Accessory #PQSH1200 | 120W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z | [5 empty] | 6285
LG Electronics USA, Inc | LG |  | 7184507 | LMU24CHV | Mixed | HMSV-A-CB | 10.2 | 19.6 | 12.5 | 18900 | Yes | Ductless | Multi-zone | Mixed Ducted and Non-ducted indoor units | 10230 | 23250 | 27900 | 1.171 | 1.859 | 2.6 | 2.6 | 3.7 | 3.1 |  | 6270 | 14250 | 20394 | 1.008 | 1.61 | 1.76 | 1.8 | 2.6 | 3.4 |  | 4932 |  | 14109 | 0.973 |  | 1.7 | 1.5 |  | 2.4 | 50.57% | 69.18% | Optional Accessory #PQSH1200 | 120W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z | [5 empty] | 6117
LG Electronics USA, Inc | LG |  | 8111355 | LMU30CHV | Non-Ducted Indoor Units | HMSV-A-CB | 10 | 22 | 13 | 30000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 9240 | 32000 | 38400 | 1.043 | 2.49 | 3.486 | 2.6 | 3.8 | 3.2 |  | 5658 | 19600 | 26739 | 0.882 | 2.1 | 2.55 | 1.9 | 2.7 | 3.1 |  | 4446 |  | 20622 | 0.84 |  | 2.42 | 1.6 |  | 2.5 | 53.7% | 77.12% | Optional Accessory #PQSH1200 | 120W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z | [5 empty] | 10114
LG Electronics USA, Inc | LG |  | 8111358 | LMU480HV | Non-Ducted Indoor Units | HMSV-A-CB | 10 | 19.5 | 12.5 | 48000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 15840 | 54000 | 61000 | 1.419 | 4.32 | 6.02 | 3.3 | 3.7 | 3 |  | 9996 | 34080 | 49014 | 0.993 | 3.02 | 5.07 | 3 | 3.3 | 2.8 |  | 8076 |  | 38900 | 0.851 |  | 4.52 | 2.8 |  | 2.5 | 63.77% | 79.37% | Optional Accessory #PQSH1200 | 120W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z | [5 empty] | 3059
LG Electronics USA, Inc | LG |  | 5859619 | LUU187HV | LCN187HV | HRCU-A-CB-O | 10.1 | 20 | 15 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 9300 | 20000 | 22000 | 0.74 | 1.5 | 1.78 | 3.7 | 3.9 | 3.6 |  | 6820 | 12500 | 14330 | 0.69 | 1.27 | 1.54 | 2.9 | 2.9 | 2.7 |  | 4550 |  | 11271 | 0.55 |  | 1.47 | 2.4 |  | 2.2 | 51.23% | 78.65% | N/A |  |  | N/A |  | z | [5 empty] | 3800
LG Electronics USA, Inc | LG |  | 6236101 | LSU240HSV3 | LSN240HSV3 | HRCU-A-CB-O | 10.2 | 20 | 12.5 | 22000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3070 | 27600 | 38900 | 0.3 | 2.38 | 4.1 | 3 | 3.4 | 2.8 |  | 2250 | 16940 | 28020 | 0.26 | 1.92 | 3.42 | 2.6 | 2.6 | 2.4 |  | 1500 |  | 24220 | 0.2 |  | 3.36 | 2.2 |  | 2.1 | 62.26% | 86.44% | N/A |  |  | N/A |  | z | [5 empty] | 3720
LG Electronics USA, Inc | LG |  | 7012586 | LSU240HLV | LSN240HLV | HRCU-A-CB-O | 11 | 21.5 | 12.5 | 22000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3070 | 27000 | 38898 | 0.3 | 2.38 | 4.1 | 3 | 3.3 | 2.8 |  | 2250 | 16570 | 27410 | 0.26 | 1.92 | 3.42 | 2.5 | 2.5 | 2.3 |  | 1500 |  | 23690 | 0.2 |  | 3.36 | 2.2 |  | 2.1 | 60.9% | 86.43% | N/A |  |  | N/A |  | z | [5 empty] | 1510
LG Electronics USA, Inc | LG |  | 7484109 | LSU090HSV4 | LAN090HSV4 | HRCU-A-CB-O | 10.8 | 21.5 | 13.3 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1023 | 10800 | 17061 | 0.075 | 0.7 | 1.43 | 4 | 4.5 | 3.5 |  | 750 | 6630 | 11080 | 0.06 | 0.56 | 1.02 | 3.5 | 3.6635 | 3.2 |  | 500 |  | 9570 | 0.05 |  | 1 | 2.9 |  | 2.8 | 56.09% | 86.37% | Integrated | 90W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z | [5 empty] | 1510
LG Electronics USA, Inc | LG |  | 7484110 | LSU090HSV4 | LSN090HSV4 | HRCU-A-CB-O | 10.8 | 21.5 | 13.3 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1023 | 10800 | 17061 | 0.07 | 0.7 | 1.35 | 4.3 | 4.5 | 3.7 |  | 750 | 6630 | 11080 | 0.06 | 0.56 | 1.02 | 3.5 | 3.6635 | 3.2 |  | 500 |  | 9570 | 0.05 |  | 1 | 2.9 |  | 2.8 | 56.09% | 86.37% | Integrated | 90W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z | [5 empty] | 1830
LG Electronics USA, Inc | LG |  | 7484111 | LSU120HSV4 | LAN120HSV4 | HRCU-A-CB-O | 11 | 21.5 | 12.5 | 11200 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1023 | 13300 | 22178 | 0.08 | 1 | 1.9 | 3.7 | 3.9 | 3.4 |  | 750 | 8160 | 13500 | 0.07 | 0.81 | 1.44 | 3 | 3.1402 | 2.7 |  | 500 |  | 11670 | 0.054 |  | 1.41 | 2.7 |  | 2.4 | 52.62% | 86.44% | Integrated | 90W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z | [5 empty] | 1830
LG Electronics USA, Inc | LG |  | 7484112 | LSU120HSV4 | LSN120HSV4 | HRCU-A-CB-O | 11 | 21.5 | 12.5 | 11200 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1023 | 13300 | 22178 | 0.08 | 1 | 1.9 | 3.7 | 3.9 | 3.4 |  | 750 | 8160 | 13500 | 0.07 | 0.81 | 1.44 | 3 | 3.1402 | 2.7 |  | 500 |  | 11670 | 0.054 |  | 1.41 | 2.7 |  | 2.4 | 52.62% | 86.44% | Integrated | 90W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z | [5 empty] | 930
LG Electronics USA, Inc | LG |  | 7849625 | LAU120HYV1 | LAN120HYV1 | HRCU-A-CB-O | 12 | 25.5 | 13.8 | 11000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1023 | 12000 | 22178 | 0.06 | 0.75 | 1.39 | 5 | 4.7 | 4.7 |  | 676 | 7360 | 14650 | 0.07 | 0.61 | 1.5 | 2.8 | 2.8303 | 2.9 |  | 633 |  | 13720 | 0.07 |  | 1.47 | 2.7 |  | 2.7 | 61.86% | 93.65% | Integrated | 90W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A | [7 empty] | 720
LG Electronics USA, Inc | LG |  | 7947563 | LAU090HYV1 | LAN090HYV1 | HRCU-A-CB-O | 12 | 27.5 | 15.65 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1023 | 11000 | 20472 | 0.07 | 0.71 | 1.32 | 4.3 | 4.5 | 4.5 |  | 597 | 6750 | 11940 | 0.06 | 0.57 | 1.16 | 2.9 | 2.9162 | 3 |  | 561 |  | 11220 | 0.06 |  | 1.14 | 2.7 |  | 2.9 | 54.81% | 93.97% | Integrated | 90W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z | [5 empty] | 3040
LG Electronics USA, Inc | LG |  | 9680934 | LAU180HYV2 | LAN180HYV2 | HRCU-A-CB-O | 12 | 22 | 12.5 | 18200 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3070 | 22000 | 32000 | 0.38 | 1.79 | 2.71 | 2.3677 | 3.602 | 3.4606 |  | 1810 | 13500 | 25640 | 0.36 | 1.44 | 2.84 | 1.4735 | 1.4736 | 2.6459 |  | 1350 |  | 22600 | 0.34 |  | 2.79 | 1.1637 |  | 2.374 | 70.62% | 88.14% | INTEGRATED | 120 WATT | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A | [7 empty] | 2030
LG Electronics USA, Inc | LG |  | 9680935 | LAU150HYV2 | LAN150HYV2 | HRCU-A-CB-O | 12.5 | 24 | 13.5 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3070 | 18000 | 25200 | 0.38 | 1.385 | 1.99 | 2.3677 | 3.8089 | 3.7113 |  | 1810 | 11000 | 20970 | 0.36 | 1.12 | 2.2 | 1.4735 | 1.4736 | 2.7935 |  | 1350 |  | 18940 | 0.34 |  | 2.16 | 1.1637 |  | 2.5698 | 75.16% | 90.32% | INTEGRATED | 120 WATT | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A | [7 empty] | 4950
LG Electronics USA, Inc. | LG |  | 10443471 | LMU420HHV | NON- DUCTED INDOOR UNITS | HMSV-A-CB | 11 | 20.5 | 14 | 42000 | Yes | Ductless | Multi-zone | WALL/CEILING CASSETTE | 13455 | 45000 | 55260 | 0.96 | 3.3 | 4.48 | 4.1076 | 3.9964 | 3.615 |  | 9466 | 29000 | 49950 | 0.91 | 3.04 | 5.62 | 3.0486 | 3.0487 | 2.6048 |  | 7688 |  | 45000 | 0.87 |  | 6.14 | 2.5898 |  | 2.1479 | 81.43% | 90.09% | Integrated | 120 W | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0 |  |  |  |  | 1600
LG Electronics USA, Inc. | LG |  | 10445372 | LMU180HHV | NON- DUCTED INDOOR UNITS | HMSV-A-CB | 10 | 21 | 13.5 | 18000 | Y | Ductless | Multi-zone | WALL/CEILING CASSETTE | 10248 | 22000 | 24000 | 1.25 | 2.22 | 3.11 | 2.4027 | 2.9043 | 2.2616 |  | 7511 | 14700 | 23600 | 1.02 | 1.72 | 3.31 | 2.1581 | 2.1582 | 2.0896 |  | 6262 |  | 22000 | 0.91 |  | 3.48 | 2.0167 |  | 1.8527 | 91.67% | 93.22% | Integrated | 120 W | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0 |  |  |  |  | 2500
LG Electronics USA, Inc. | LG |  | 10445374 | LMU240HHV | NON- DUCTED INDOOR UNITS | HMSV-A-CB | 10.7 | 21 | 13.5 | 24000 | Y | Ductless | Multi-zone | WALL/CEILING CASSETTE | 10248 | 26000 | 31200 | 1.26 | 2.12 | 2.96 | 2.3836 | 3.5943 | 3.0891 |  | 7511 | 17400 | 28500 | 1.04 | 1.82 | 3.45 | 2.1166 | 2.1167 | 2.421 |  | 6262 |  | 26000 | 0.94 |  | 3.63 | 1.9524 |  | 2.0991 | 83.33% | 91.23% | Integrated | 120 W | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0 |  |  |  |  | 3000
LG Electronics USA, Inc. | LG |  | 10445376 | LMU300HHV | NON- DUCTED INDOOR UNITS | HMSV-A-CB | 11 | 20 | 12.5 | 28400 | Y | Ductless | Multi-zone | WALL/CEILING CASSETTE | 10248 | 28600 | 34200 | 1.3 | 2.33 | 3.26 | 2.3103 | 3.5974 | 3.0745 |  | 7511 | 18900 | 31600 | 1.08 | 1.98 | 3.69 | 2.0382 | 2.0383 | 2.5098 |  | 6262 |  | 28600 | 0.97 |  | 3.88 | 1.892 |  | 2.1603 | 83.63% | 90.51% | Integrated | 120 W | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0 |  |  |  |  | 4400
LG Electronics USA, Inc. | LG |  | 10443475 | LMU360HHV | DUCTED INDOOR UNITS | HMSV-A-CB | 10.5 | 17.5 | 13.5 | 34000 | Y | Ductless | Multi-zone | Ducted Indoor Units | 13127 | 40000 | 49200 | 1.17 | 3.55 | 4.48 | 3.2882 | 3.3022 | 3.2185 |  | 9239 | 27000 | 44400 | 1.11 | 3.16 | 5.32 | 2.4394 | 2.4395 | 2.4459 |  | 7483 |  | 40000 | 1.07 |  | 5.84 | 2.0496 |  | 2.0073 | 81.3% | 90.09% | Integrated | 120 W | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0 |  |  |  |  | 4510
LG Electronics USA, Inc. | LG |  | 10443472 | LMU360HHV | NON- DUCTED INDOOR UNITS | HMSV-A-CB | 11.5 | 21 | 15 | 36000 | Y | Ductless | Multi-zone | WALL/CEILING CASSETTE | 13455 | 41000 | 50200 | 0.96 | 2.93 | 3.94 | 4.1076 | 4.101 | 3.7341 |  | 9466 | 28000 | 45510 | 0.91 | 2.83 | 5.2 | 3.0486 | 3.0487 | 2.5649 |  | 7688 |  | 41000 | 0.87 |  | 5.69 | 2.5898 |  | 2.1118 | 81.67% | 90.09% | Integrated | 120 W | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0 |  |  |  |  | 4510
LG Electronics USA, Inc. | LG |  | 10443472 | LMU360HHV | NON- DUCTED INDOOR UNITS | HMSV-A-CB | 11.5 | 21 | 15 | 36000 | Y | Ductless | Multi-zone | WALL/CEILING CASSETTE | 13455 | 41000 | 50200 | 0.96 | 2.93 | 3.94 | 4.1076 | 4.101 | 3.7341 |  | 9466 | 28000 | 45510 | 0.91 | 2.83 | 5.2 | 3.0486 | 3.0487 | 2.5649 |  | 7688 |  | 41000 | 0.87 |  | 5.69 | 2.5898 |  | 2.1118 | 81.67% | 90.09% | Integrated | 120 W | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0 |  |  |  |  | 4950
LG Electronics USA, Inc. | LG |  | 10443474 | LMU420HHV | DUCTED INDOOR UNITS | HMSV-A-CB | 10.5 | 19 | 13 | 42000 | Y | Ductless | Multi-zone | Ducted Indoor Units | 13455 | 45000 | 54900 | 1.07 | 3.66 | 4.81 | 3.6853 | 3.6033 | 3.345 |  | 9466 | 29000 | 49950 | 1.02 | 3.14 | 5.84 | 2.7198 | 2.7199 | 2.5067 |  | 7688 |  | 45000 | 0.98 |  | 6.38 | 2.2991 |  | 2.0671 | 81.97% | 90.09% | Integrated | 120 W | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0 |  | 4.8 | 2.81 | 2.2 | 4950
LG Electronics USA, Inc. | LG |  | 10444103 | LMU420HHV | MIXED DUCTED AND DUCTLESS | HMSV-A-CB | 10.75 | 19.75 | 13.5 | 42000 | N | Ductless | Multi-zone | Mixed Ducted and Non-ducted indoor units | 13445 | 45000 | 55080 | 1.02 | 3.47 | 4.65 | 3.8631 | 3.8006 | 3.4715 |  | 9466 | 29000 | 49950 | 1.01 | 3.09 | 5.73 | 2.7467 | 2.7469 | 2.5548 |  | 7688 |  | 45000 | 0.93 |  | 6.26 | 2.4227 |  | 2.1067 | 81.7% | 90.09% | Integrated | 121 W | Heater on when ambient temperatrure is equal and less than 0C- Heater off when ambient temperature is equal and greater than 1C - 1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reached 1C. Heater not used in "cool" mode | N/A | 0 |  | 0 |  |  |  |  | 0
LG Electronics USA, Inc. | LG |  | 10513887 | LUU248HV | LVN240HV4 | HRCU-A-CB-O | Yes | 10 | 18 | 12.5 | YES | Ducted | Single-zone | N/A | 10000 | 27000 | 30000 | 0.75 | 2.26 | 2.8 | 3.9076 | 3.5013 | 3.14 |  | 6000 | 18000 | 22000 | 0.72 | 1.9 | 3 | 2.4423 | 2.7765 | 2.1492 |  | 4800 |  | 20000 | 0.69 |  | 3.2 | 2.0388 |  | 1.8317 | 66.67% | 90.91% |  |  |  | -4 |  |  | 21660 | 0 | 4.35 | #DIV/0! | 1.528
LG Electronics USA, Inc. | LG |  | 10399150 | LUU368HV | LVN360HV4 | HRCU-A-CB-O | Yes | 10 | 18 | 12.5 | YES | Ducted | Single-zone | N/A | 15000 | 40000 | 47000 | 1.35 | 3.39 | 5.5 | 3.2563 | 3.4581 | 2.5044 |  | 8900 | 25600 | 32000 | 1.22 | 2.75 | 4.5 | 2.138 | 2.7282 | 2.0841 |  | 7000 |  | 30000 | 1.11 |  | 4.4 | 1.8482 |  | 1.9982 | 63.83% | 93.75% |  |  |  | -4 |  |  | 21660 | 0 | 4.35 | #DIV/0! | 1.4593
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7434477 | MXZ-5C42NAHZ | Non-Ducted Indoor Units | HMSV-A-CB | 11 | 19 | 13.4 | 42000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 24000 | 48000 | 48000 | 1.17 | 3.43 | 3.43 | 6.01 | 4.1 | 4.1 |  | 24000 | 35800 | 48000 | 1.66 | 3.65 | 4.87 | 4.23 | 2.87 | 2.89 |  | 24000 |  | 48000 | 1.91 |  | 5.61 | 3.69 |  | 2.51 | 100% | 100% | Integrated | 150W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 24000 | z | 36000 | 2.5 | 4.68 | 2.83 | 2.12 | 0
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7434482 | MXZ-4C36NAHZ | Non-Ducted Indoor Units | HMSV-A-CB | 11.3 | 19.1 | 14 | 36000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 22500 | 45000 | 45000 | 1.09 | 3.34 | 3.34 | 6.05 | 3.95 | 3.95 |  | 22500 | 34000 | 45000 | 1.55 | 3.5 | 4.74 | 4.26 | 2.85 | 2.78 |  | 22500 |  | 45000 | 1.78 |  | 5.46 | 3.71 |  | 2.41 | 100% | 100% | Integrated | 150W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 22500 | z | 33800 | 2.33 | 5.32 | 2.1 | 1.89 | 0
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7434486 | MXZ-4C36NAHZ | Mixed | HMSV-A-CB | 10.7 | 17.45 | 12.65 | 36000 | Yes | Ductless | Multi-zone | Mixed Ducted and Non-ducted indoor units | 22500 | 45000 | 45000 | 1.3 | 3.8 | 3.8 | 5.07 | 3.48 | 3.48 |  | 22500 | 35000 | 45000 | 2.15 | 4.05 | 5.35 | 3.07 | 2.54 | 2.47 |  | 22500 |  | 45000 | 2.62 |  | 6.21 | 2.52 |  | 2.16 | 100% | 100% | N/A |  |  | -13 | 22500 | z | 33800 | 3.14 |  |  |  | 4400
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 10091325 | MXZ-2C20NA2 | Non-ducted | HMSV-A-CB | 10 | 20 | 12.7 | 18000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 7400 | 22000 | 25500 | 0.67 | 1.641 | 2.455 | 3.2369 | 3.929 | 3.0441 |  | 12500 | 12500 | 15500 | 1.5 | 1.3 | 1.75 | 2.4423 | 2.818 | 2.5958 |  | 10500 |  | 11100 | 1 |  | 1.6 | 3.0772 |  | 2.0332 | 43.53% | 66.67% | MAC-646BH-E | 120 W | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | [7 empty] | 6000
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8953943 | PUMY-P36NKMU1 | Non-ducted | HMSV-A-CB | 11.5 | 21 | 14.2 | 36000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 13313 | 42000 | 42000 | 0.62 | 3.16 | 3.16 | 6.293 | 3.8952 | 3.8952 |  | 9690 | 26400 | 35000 | 0.726 | 2.59 | 3.799 | 3.9117 | 2.9873 | 2.7 |  | 6687 |  | 29000 | 0.582 |  | 3.695 | 3.3673 |  | 2.3002 | 69.05% | 80.17% | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | [7 empty] | 6600
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8953946 | PUMY-P48NKMU1 | Non-ducted | HMSV-A-CB | 11.7 | 20.2 | 12.6 | 48000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 15976 | 54000 | 54000 | 0.784 | 4.165 | 4.165 | 5.9721 | 3.7997 | 3.7997 |  | 11628 | 31400 | 43000 | 0.917 | 3.15 | 5.041 | 3.7163 | 2.9214 | 2.4999 |  | 8025 |  | 36400 | 0.735 |  | 4.849 | 3.1999 |  | 2.2 | 67.41% | 80.15% | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | [7 empty] | 8000
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8953947 | PUMY-P60NKMU1 | Non-ducted | HMSV-A-CB | 11.4 | 18.6 | 12.5 | 60000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 19526 | 66000 | 66000 | 1.027 | 5.53 | 5.53 | 5.5721 | 3.4978 | 3.4978 |  | 14121 | 41500 | 65000 | 1.201 | 4.68 | 8.283 | 3.446 | 2.5988 | 2.2998 |  | 9809 |  | 57000 | 0.963 |  | 8.353 | 2.9852 |  | 1.9999 | 86.36% | 80.18% | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | [7 empty] | 6500
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 9141022 | PUMY-P36NKMU1 | Mixed | HMSV-A-CB | 11 | 18.3 | 13.4 | 36000 | Yes | Ductless | Multi-zone | Mixed Ducted and Non-ducted indoor units | 13313 | 42000 | 42000 | 0.646 | 3.29 | 3.29 | 6.0397 | 3.7413 | 3.7413 |  | 9690 | 26500 | 35500 | 0.783 | 2.794 | 3.95 | 3.627 | 2.7797 | 2.6339 |  | 6687 |  | 29000 | 0.606 |  | 3.798 | 3.2339 |  | 2.2378 | 69.05% | 77.39% | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | [7 empty] | 8000
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 9722847 | MXZ-8C60NA | Non-ducted | HMSV-A-CB | 10.5 | 17.4 | 12.5 | 60000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 19526 | 66000 | 66000 | 1.053 | 1.053 | 1.053 | 5.4345 | 3.4114 | 3.4114 |  | 14212 | 41500 | 65000 | 1.232 | 4.87 | 9.525 | 3.3809 | 2.4974 | 2 |  | 9808 |  | 57000 | 0.987 |  | 8.1 | 2.9123 |  | 2.0624 | 86.36% | 80.11% | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A |  |  |  |  | 4.49 | 2.09 | 1.64 | 0
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 8993522 | MXZ-3C30NAHZ2 | Non-Ducted Indoor Units | HMSV-A-CB | 11 | 18 | 12.5 | 28400 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 11400 | 28600 | 28600 | 0.93 | 2.1 | 2.1 | 3.59 | 4 | 4 |  | 13100 | 18000 | 28600 | 1.5 | 1.99 | 4.19 | 2.5596 | 2.65 | 2 |  | 12500 |  | 28600 | 1.6 |  | 4.79 | 2.29 |  | 1.75 | 100% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 | z | 25225 | 1.4 | 3.52 | 2.09 | 1.83 | 0
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 8996108 | MXZ-3C24NAHZ2 | Non-Ducted Indoor Units | HMSV-A-CB | 10 | 19 | 13.5 | 22000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 11400 | 25000 | 25000 | 0.93 | 1.72 | 1.72 | 3.59 | 4.25 | 4.25 |  | 13100 | 14000 | 25000 | 1.5 | 1.62 | 3.56 | 2.5596 | 2.53 | 2.06 |  | 12500 |  | 25000 | 1.6 |  | 3.82 | 2.29 |  | 1.92 | 100% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 | z | 22050 | 1.4 |  |  |  | 6000
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8953944 | PUMY-P36NKMU1 | Ducted indoor units | HMSV-A-CB | 10.5 | 15.6 | 12.6 | 36000 | Yes | Ductless | Multi-zone | Ducted Indoor Units | 13313 | 42000 | 42000 | 0.671 | 3.42 | 3.42 | 5.8147 | 3.5991 | 3.5991 |  | 9690 | 26600 | 36000 | 0.84 | 2.998 | 4.1 | 3.3809 | 2.6003 | 2.5733 |  | 6687 |  | 30000 | 0.63 |  | 3.9 | 3.1107 |  | 2.2544 | 71.43% | 75% | PAC-SJ20BH-E | 150 | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A |  |  |  |  | 4.49 | 2.09 | 1.64 | 0
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7451794 | MXZ-3C30NAHZ | Non-Ducted Indoor Units | N/A | 11 | 18 | 12.5 |  | Yes | Ductless | Multi-zone | Non-ducted indoor units (Wall Mount) | 11400 | 28600 | 28600 | 0.93 | 2.1 | 2.1 | 3.59 | 4 | 4 |  | 13100 | 18000 | 28600 | 1.5 | 1.99 | 4.19 | 2.5596 | 2.65 | 2 |  | 12500 |  | 28600 | 1.6 |  | 4.79 | 2.29 |  | 1.75 | 100% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 | z | 25225 | 1.4 | 3.52 | 2.09 | 1.83 | 0
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 7451969 | MXZ-3C24NAHZ | Non-Ducted Indoor Units | N/A | 10 | 19 | 13.5 |  | Yes | Ductless | Multi-zone | Non-ducted indoor units (Wall Mount) | 11400 | 25000 | 25000 | 0.93 | 1.72 | 1.72 | 3.59 | 4.25 | 4.25 |  | 13100 | 14000 | 25000 | 1.5 | 1.62 | 3.56 | 2.5596 | 2.53 | 2.06 |  | 12500 |  | 25000 | 1.6 |  | 3.82 | 2.29 |  | 1.92 | 100% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 | z | 22050 | 1.4 |  |  |  | 3400
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 3837467 | SUZ-KA12NA | SEZ-KD12NA | HRCU-A-CB | 10 | 16 | 12.5 | 11500 | Yes | Ductless | Single-zone | Ducted Indoor Units | 4800 | 13600 | 16400 | 0.34 | 1.14 | 1.52 | 4.1375 | 3.4963 | 3.1621 |  | 3100 | 9000 | 10800 | 0.36 | 0.92 | 1.2 | 2.5237 | 2.867 | 2.6376 |  | 2199 |  | 7400 | 0.27 |  | 0.9 | 2.3869 |  | 2.4097 | 45.12% | 75% | N/A |  |  | N/A | [7 empty] | 5100
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 3837470 | SUZ-KA18NA | SEZ-KD18NA | HRCU-A-CB | 10 | 17.5 | 12.5 | 17200 | Yes | Ductless | Single-zone | Ducted Indoor Units | 4800 | 21600 | 24900 | 0.26 | 1.7 | 2.15 | 5.4105 | 3.7237 | 3.3942 |  | 2900 | 13100 | 15000 | 0.31 | 1.35 | 1.8 | 2.7416 | 2.8439 | 2.4423 |  | 1900 |  | 9900 | 0.23 |  | 1.32 | 2.421 |  | 2.198 | 39.76% | 74.19% | N/A |  |  | N/A |  |  |  |  | 6.15 | 2.15 | 1.38 | 0
Mitsubishi Electric Cooling & Heating | Mitsubishi | P-Series | 8635969 | PUZ-HA36NHA5 | PVA-A36AA4 | HRCU-A-CB-O | 11 | 17.8 | 12.5 | 33000 | Yes | Centrally Ducted | N/A | N/A | 18000 | 38000 | 40000 | 1.14 | 3.04 | 3.36 | 4.63 | 3.66 | 3.49 |  | 19000 | 25000 | 38000 | 2.03 | 3.33 | 5.4 | 2.74 | 2.2 | 2.06 |  | 15000 |  | 38000 | 1.73 |  | 6.1 | 2.54 |  | 1.82 | 95% | 100% | N/A |  |  | -13 | 13000 | z | 29000 | 1.77 |  |  |  | 0
Mitsubishi Electric Cooling & Heating | Mitsubishi | P-Series Hyper Heat | 8635970 | PUZ-HA36NHA5 | PEAD-A36AA* | HRCU-A-CB-O | 10.4 | 16.8 | 12.5 | 33000 | Yes | Ductless | Multi-zone | Ducted Indoor Units | 18000 | 38000 | 40000 | 1.16 | 3.15 | 3.27 | 4.54 | 3.53 | 3.58 |  | 14000 | 27000 | 38000 | 1.54 | 3.25 | 5.4 | 2.66 | 2.43 | 2.06 |  | 10000 |  | 38000 | 1.21 |  | 6.1 | 2.42 |  | 1.82 | 95% | 100% | Integrated | 120W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32°F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2°F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A
Mitsubishi Electric Cooling & Heating | Mitsubishi | P-Series Hyper Heat | 8635971 | PUZ-HA36NHA5 | PLA-A36BA* | HRCU-A-CB-O | 10 | 17 | 12.6 | 34000 | Yes | Ductless | Multi-zone | Ducted Indoor Units | 18000 | 38000 | 40000 | 1.19 | 3.13 | 3.75 | 4.43 | 3.55 | 3.14 |  | 14000 | 28000 | 38000 | 1.38 | 3.59 | 5.3 | 2.97 | 2.28 | 2.12 |  | 9000 |  | 38000 | 0.97 |  | 5.79 | 2.71 |  | 1.92 | 95% | 100% | Integrated | 120W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32°F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2°F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | [7 empty] | 4400
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8715786 | MUZ-GL24NA-U1 | MSZ-GL24NA-U1 | HRCU-A-CB-O | 10 | 20.5 | 12.5 | 22400 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7500 | 27600 | 36900 | 0.52 | 2.34 | 3.65 | 4.227 | 3.4567 | 2.9628 |  | 4900 | 16000 | 24600 | 0.72 | 1.77 | 3.29 | 1.9945 | 2.6492 | 2.1914 |  | 4380 |  | 20200 | 0.64 |  | 2.99 | 2.0057 |  | 1.9799 | 54.74% | 88.89% | MAC-642BH-U1 | 120 W | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | [7 empty] | 1600
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 4908219 | MUZ-FE09NA | MSZ-FE09NA | HRCU-A-CB-O | 10 | 26 | 15.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 10900 | 18000 | 0.15 | 0.71 | 2.25 | 5.8617 | 4.5 | 2.34 |  | 1700 | 6700 | 12500 | 0.11 | 0.65 | 1.73 | 4.53 | 3.02 | 2.12 |  | 1200 |  | 10900 | 0.08 |  | 1.46 | 4.4 |  | 2.19 | 60.56% | 87.2% | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A |  | z | [5 empty] | 0
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 4934170 | MUZ-FE12NA | MSZ-FE12NA | HRCU-A-CB-O | 10.5 | 23 | 12.9 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 13600 | 21000 | 0.15 | 0.95 | 2.25 | 5.8617 | 4.2 | 2.74 |  | 1700 | 8300 | 13600 | 0.11 | 0.8 | 1.78 | 4.53 | 3.04 | 2.24 |  | 1200 |  | 13600 | 0.08 |  | 1.62 | 4.4 |  | 2.46 | 64.76% | 100% | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A |  | z |  |  | 1.25 | 2.34 | 1.71 | 1300
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7002062 | MUZ-FH09NA | MSZ-FH09NA | HRCU-A-CB-O | 13.5 | 30.5 | 16.1 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1600 | 10900 | 18000 | 0.11 | 0.71 | 1.47 | 4.263 | 4.5 | 3.59 |  | 920 | 6700 | 12200 | 0.08 | 0.6 | 1.44 | 3.37 | 3.27 | 2.48 |  | 640 |  | 10900 | 0.06 |  | 1.35 | 3.13 |  | 2.32 | 60.56% | 89.34% | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 240 | z | 7300 | 0.03 | 1.6 | 2.3 | 1.81 | 0
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 7002063 | MUZ-FH12NA | MSZ-FH12NA | HRCU-A-CB-O | 12.5 | 26.1 | 13.8 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3700 | 13600 | 21000 | 0.28 | 0.95 | 2.3 | 3.8729 | 4.2 | 2.68 |  | 2100 | 8000 | 13600 | 0.2 | 0.72 | 1.9 | 3.08 | 3.26 | 2.1 |  | 1450 |  | 13600 | 0.15 |  | 1.8 | 2.83 |  | 2.21 | 64.76% | 100% | Accessory (MAC-640BH-U) | 106W @208V; 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 550 | z | 9900 | 0.07 | 2.35 | 2 | 1.82 | 0
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 7002444 | MUZ-FH15NA | MSZ-FH15NA | HRCU-A-CB-O | 12 | 22 | 12.5 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5150 | 18000 | 24000 | 0.43 | 1.3 | 3.36 | 3.5102 | 4.06 | 2.09 |  | 2950 | 11000 | 18000 | 0.31 | 1.02 | 2.48 | 2.79 | 3.16 | 2.13 |  | 2050 |  | 18000 | 0.23 |  | 2.95 | 2.61 |  | 1.79 | 75% | 100% | Accessory (MAC-642BH-U) | 98W @208V; 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 750 | z | 14600 | 0.11 | 1.73 | 0.81 | 1.68 | 0
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr.Slim FH Series | 8703451 | MUZ-FH12NAH | MSZ-FH12NAH | HRCU-A-CB-O | 11.5 | 26.1 | 13.8 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3700 | 13600 | 21000 | 0.28 | 0.95 | 2.3 | 3.8729 | 4.2 | 2.68 |  | 2100 | 8100 | 13600 | 0.33 | 0.84 | 1.96 | 1.87 | 2.83 | 1.96 |  | 1450 |  | 13600 | 0.28 |  | 1.93 | 1.52 |  | 2.07 | 64.76% | 100% | Integrated | 106W @208V; 130W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | 550 |  | 9900 | 0.2 | 1.06 | 0.24 | 2.02 | 1300
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr.Slim FH Series | 8737963 | MUZ-FH09NAH | MSZ-FH09NAH | HRCU-A-CB-O | 12.5 | 30.5 | 16.1 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1600 | 10900 | 18000 | 0.11 | 0.55 | 1.27 | 4.263 | 5.86 | 4.15 |  | 920 | 6700 | 12200 | 0.34 | 0.72 | 1.26 | 0.79 | 2.73 | 2.84 |  | 640 |  | 10900 | 0.32 |  | 1.17 | 0.59 |  | 2.73 | 60.56% | 89.34% | Integrated | 106W @208V; 130W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | 240 |  | 7300 | 0.29 | 2.54 | 1.3659 | 1.6961 | 1900
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8737964 | MUZ-FH15NAH | MSZ-FH15NA | HRCU-A-CB-O | 11 | 22 | 12.5 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) | 4280 | 18540 | 24200 | 0.61 | 1.33 | 3.4 | 2.0564 | 4.0854 | 2.086 | 3570 | 3570 | 11070 | 20200 | 0.6 | 0.95 | 3.36 | 1.7438 | 3.415 | 1.7619 | 3240 | 3240 | 8550 | 18300 | 0.55 | 0.74 | 2.98 | 1.7265 | 3.3862 | 1.7997 | 75.62% | 91.67% | Integrated | 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 2610 |  | 14700 | 0.56 |  |  |  | 2500
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8737968 | MUZ-FE09NAH | MSZ-FE09NA | HRCU-A-CB-O | 10 | 26 | 15.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) | 3000 | 10900 | 18000 | 0.15 | 0.71 | 2.25 | 5.8614 | 4.4993 | 2.3446 | 1840 | 1840 | 6700 | 13700 | 0.26 | 0.67 | 1.89 | 2.074 | 2.9307 | 2.1244 | 1430 | 1430 | 11200 | 11200 | 0.25 | 1.59 | 1.59 | 1.6764 | 2.0644 | 2.7709 | 62.22% | 81.75% | Integrated | 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | [7 empty] | 2600
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8737969 | MUZ-FE12NAH | MSZ-FE12NA | HRCU-A-CB-O | 10.1 | 23 | 12.9 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) | 3000 | 13600 | 21000 | 0.15 | 0.95 | 2.25 | 5.8614 | 4.1955 | 2.7353 | 1840 | 1840 | 8400 | 15100 | 0.26 | 0.84 | 1.89 | 2.074 | 2.9307 | 2.3415 | 1430 | 1430 | 6500 | 12500 | 0.25 | 0.68 | 1.59 | 1.6764 | 2.8014 | 2.304 | 59.52% | 96.15% | Integrated | 130W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | [7 empty] | 2200
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 10095215 | MUZ-GL09NA-U1 | MSZ-GL09NA-U1 | HRCU-A-CB-O | 12.8 | 24.6 | 15.4 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4500 | 10900 | 15900 | 0.23 | 0.72 | 1.25 | 5.734 | 4.4368 | 3.7279 |  | 2830 | 6700 | 10200 | 0.28 | 0.63 | 1.06 | 2.9621 | 3.1168 | 2.8201 |  | 2280 |  | 8000 | 0.24 |  | 0.85 | 2.7842 |  | 2.7583 | 50.31% | 85.71% | MAC-640BH-U | 130 W | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | [7 empty] | 1800
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8715783 | MUZ-GL12NA-U1 | MSZ-GL12NA-U1 | HRCU-A-CB-O | 12.5 | 23.1 | 13 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2000 | 14400 | 18100 | 0.11 | 1.1 | 1.62 | 5.3286 | 3.8366 | 3.2744 |  | 1150 | 9200 | 12000 | 0.13 | 0.87 | 1.24 | 2.5926 | 3.0991 | 2.8362 |  | 1040 |  | 10200 | 0.1 |  | 1.02 | 3.0479 |  | 2.9307 | 56.35% | 76.92% | MAC-640BH-U | 130 W | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | [7 empty] | 2300
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8715784 | MUZ-GL15NA-U1 | MSZ-GL15NA-U1 | HRCU-A-CB-O | 11.7 | 21.6 | 13 | 14000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4800 | 18000 | 20900 | 0.2 | 1.6 | 2.01 | 7.0337 | 3.297 | 3.0474 |  | 2150 | 12200 | 16400 | 0.2 | 1.6 | 2.01 | 3.1505 | 2.2347 | 2.3912 |  | 2080 |  | 14100 | 0.24 |  | 1.57 | 2.5399 |  | 2.632 | 67.46% | 120% | MAC-640BH-U | 130 W | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | [7 empty] | 3100
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8715785 | MUZ-GL18NA-U1 | MSZ-GL18NA-U1 | HRCU-A-CB-O | 11.2 | 20.5 | 13.4 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5400 | 21600 | 25000 | 0.32 | 1.68 | 2.5 | 4.9456 | 3.7681 | 2.9307 |  | 2780 | 13800 | 18200 | 0.37 | 1.48 | 2.15 | 2.202 | 2.7327 | 2.4809 |  | 2590 |  | 15100 | 0.32 |  | 1.88 | 2.372 |  | 2.3539 | 60.4% | 86.49% | MAC-642BH-U1 | 120 W | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | [7 empty] | 3600
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 10053547 | PUZ-A24NHA7 | PLA-A24EA7 | HRCU-A-CB-O | 11.2 | 24.2 | 14.3 | 24000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 9000 | 26000 | 29000 | 0.45 | 1.75 | 2.07 | 5.8614 | 4.3542 | 4.1058 |  | 5100 | 14900 | 16600 | 0.42 | 1.6 | 1.9 | 3.5587 | 2.7292 | 2.5605 |  | 4500 |  | 13000 | 0.4 |  | 1.4 | 3.297 |  | 2.7214 | 44.83% | 95.24% | N/A |  |  | N/A | [7 empty] | 2400
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 10054648 | PUZ-A36NKA7 | PLA-A36EA7 | HRCU-A-CB-O | 10.4 | 21.8 | 12.9 | 36000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 18000 | 38000 | 42000 | 0.94 | 3.54 | 3.02 | 5.612 | 3.146 | 4.0758 |  | 10000 | 22000 | 24000 | 0.93 | 2.49 | 3 | 3.1513 | 2.5894 | 2.3446 |  | 9200 |  | 21600 | 0.83 |  | 2.6 | 3.2485 |  | 2.4347 | 51.43% | 89.25% | N/A |  |  | N/A |  |  |  |  | 2.46 | 1.4328 | 1.7751 | 3400
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8797134 | MUZ-FH18NAH2 | MSZ-FH18NA | HRCU-A-CB-O | 11 | 21 | 12.5 | 17200 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) | 7540 | 20300 | 30400 | 0.85 | 1.77 | 3.4 | 2.5997 | 3.3612 | 2.6204 | 4300 | 4300 | 12480 | 24300 | 0.6 | 1.25 | 3.39 | 2.1003 | 2.926 | 2.1008 | 3700 | 3700 | 9640 | 20900 | 0.53 | 0.98 | 2.98 | 2.046 | 2.8829 | 2.0554 | 68.75% | 88.33% | Integrated | 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 2640 |  | 14900 | 0.54 |  |  |  | 2000
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr Slim | 8854558 | MUFZ-KJ15NAHZ | MFZ-KJ15NA | HRCU-A-CB-O | 11.6 | 21.8 | 13.5 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Floor Mount) | 5100 | 18000 | 25000 | 0.7 | 1.41 | 3.41 | 2.1352 | 3.7413 | 2.1486 | 3540 | 3540 | 14400 | 20000 | 0.44 | 1.19 | 3.04 | 2.3579 | 3.5464 | 1.9281 | 3190 | 3190 |  | 18000 | 0.4 |  | 2.83 | 2.3372 |  | 1.8641 | 72% | 90.91% | Integrated | 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A |  |  |  |  | 0.8 | 2.34 | 2.34 | 2000
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series H2i | 8797130 | MUZ-FH06NA | MSZ-FH06NA | HRCU-A-CB-O | 13.5 | 33.1 | 19 | 6000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1600 | 8700 | 14000 | 0.11 | 0.55 | 1.27 | 4.26 | 4.68 | 3.23 |  | 920 | 5900 | 10700 | 0.08 | 0.5 | 1 | 3.37 | 3.46 | 3.13 |  | 640 |  | 8700 | 0.06 |  | 0.91 | 3.13 |  | 2.8 | 62.14% | 81.31% | Accessory (MAC-640BH-U) | 106W @208V; 130W @230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 240 | z | 6400 | 0.03 | 0.93 | 0.44 | 2.02 | 2000
Mitsubishi Electric Cooling & Heating | Mitsubishi | Mr.Slim FH Series | 8797132 | MUZ-FH06NAH | MSZ-FH06NAH | HRCU-A-CB-O | 12.5 | 33.1 | 19 | 6000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 1600 | 8700 | 14000 | 0.11 | 0.55 | 1.27 | 4.26 | 4.68 | 3.23 |  | 920 | 5900 | 10700 | 0.21 | 0.628 | 1.13 | 1.28 | 2.75 | 2.78 |  | 640 |  | 8700 | 0.19 |  | 1.04 | 0.99 |  | 2.45 | 62.14% | 81.31% | Integrated | 106W @208V; 130W @ 230V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A | 240 |  | 2100 | 0.16 | 2.35 | 2 | 1.74 | 0
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 8797133 | MUZ-FH18NA2 | MSZ-FH18NA2 | HRCU-A-CB-O | 12 | 21 | 12.5 | 17200 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5150 | 20300 | 30000 | 0.43 | 1.72 | 3.39 | 3.51 | 3.46 | 2.59 |  | 2950 | 13700 | 20300 | 0.31 | 1.32 | 2.8 | 2.79 | 3.04 | 2.12 |  | 2050 |  | 20300 | 0.23 |  | 2.96 | 2.61 |  | 2.01 | 67.67% | 100% | Accessory (MAC-642BH-U) | 98W @208V; 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | -13 | 750 | z | 14000 | 0.11 | 1.28 | 1.76 | 1.83 | 1800
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series; KJ-Series | 8849446 | MUFZ-KJ12NAHZ | MFZ-KJ12NA | HRCU-A-CB-O | 12 | 25.5 | 13.6 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2900 | 13000 | 22800 | 0.27 | 0.9 | 2.39 | 3.15 | 4.23 | 2.8 |  | 1650 | 8800 | 14800 | 0.2 | 0.93 | 1.89 | 2.42 | 2.77 | 2.29 |  | 1150 |  | 13000 | 0.15 |  | 1.81 | 2.25 |  | 2.1 | 57.02% | 87.84% | Integrated | 106W @208V; 130W @ 230 V |  | -13 | 420 | z | 8000 | 0.07 | 1.27 | 1.76 | 1.62
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 8854557 | MUFZ-KJ09NAHZ | MFZ-KJ09NA | HRCU-A-CB-O | 13 | 28.2 | 15.8 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2900 | 11000 | 19000 | 0.27 | 0.75 | 2.37 | 3.15 | 4.3 | 2.35 |  | 1650 | 7500 | 13400 | 0.2 | 0.8 | 1.86 | 2.42 | 2.75 | 2.11 |  | 1150 |  | 11000 | 0.15 |  | 1.6 | 2.25 |  | 2.01 | 57.89% | 82.09% | Integrated | 106W @208V; 130W @ 230 V |  | -13 | 420 | z | 7000 | 0.07 | 2.3 | 1.89 | 2
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 8854559 | MUFZ-KJ18NAHZ | MFZ-KJ18NA | HRCU-A-CB-O | 11.3 | 21 | 12.6 | 17000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5700 | 21000 | 29000 | 0.48 | 1.73 | 3.43 | 3.48 | 3.56 | 2.48 |  | 3250 | 12800 | 23000 | 0.35 | 1.43 | 3.21 | 2.72 | 2.62 | 2.1 |  | 2260 |  | 21000 | 0.26 |  | 3 | 2.55 |  | 2.05 | 72.41% | 91.3% | Integrated | 98W @208V; 120W @ 230 V |  | -13 | 840 | z | 15700 | 0.13
Mitsubishi Electric Cooling & Heating | Mitsubishi | M-Series | 4217888 | MUZ-FE18NA | MSZ-FE18NA | N/A | 10.3 | 20.2 | 14.2 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) | 7500 | 21600 | 29700 | 0.52 | 1.54 | 2.42 | 4.23 | 4.11 | 3.6 |  | 4300 | 11700 | 25850 | 0.37 | 1.24 | 3.28 | 3.41 | 2.76 | 2.31 |  | 3000 |  | 21830 | 0.28 |  | 3.15 | 3.14 |  | 2.03 | 73.5% | 84.45% | Accessory (MAC-642BH-U) | 98W @208V; 120W @ 230 V | A.) Heat mode is selected. B.) The ambient temperature thermistor reads 32F or less for 5 minutes continuously. C.) The defrost thermistor reads 30.2F or less for 5 minutes. D.) Outdoor fan motor is turned ON. | N/A |  | z | [5 empty] | 3200
Nortek Global | Maytag | M1200 | 5597453 | PSH4BG024K | B6VMAX024K-B | HRCU-A-CB | 10 | 19 | 13.9 | 24600 | Yes | Centrally Ducted | N/A | N/A | 10200 | 22400 | 24700 | 0.7 | 1.7 | 2.2 | 4.2705 | 3.8616 | 3.2904 |  | 6100 | 14200 | 15800 | 0.7 | 1.5 | 1.9 | 2.5539 | 2.7744 | 2.4371 |  | 4700 |  | 12600 | 0.6 |  | 1.8 | 2.2957 |  | 2.0515 | 51.01% | 79.75% | N/A |  |  | N/A |  | z | [5 empty] | 3800
Nortek Global | Maytag | M1200 | 5597457 | PSH4BG036K | B6VMAX036K-B | HRCU-A-CB | 10 | 19 | 12.9 | 34800 | Yes | Centrally Ducted | N/A | N/A | 16500 | 34400 | 36800 | 1 | 2.7 | 3.2 | 4.8357 | 3.7339 | 3.3703 |  | 9900 | 21800 | 23900 | 1 | 2.4 | 2.7 | 2.9014 | 2.6621 | 2.5942 |  | 7500 |  | 20100 | 0.9 |  | 2.6 | 2.4423 |  | 2.2657 | 54.62% | 84.1% | N/A |  |  | N/A |  | z | [5 empty] | 3200
Nortek Global | Maytag | M1200 | 10296728 | PSH1BG4CVRX24K | B6VMAX24K-B | HRCU-A-CB | 10 | 19 | 13.9 | 24600 | Yes | Centrally Ducted | N/A | N/A | 10200 | 22400 | 24700 | 0.7 | 1.7 | 2.2 | 4.2705 | 3.8616 | 3.2904 |  | 6100 | 14200 | 15800 | 0.7 | 1.5 | 1.9 | 2.5539 | 2.7744 | 2.4371 |  | 4700 |  | 12600 | 0.6 |  | 1.8 | 2.2957 |  | 2.0515 | 51.01% | 79.75% | N/A | 0 | 0 | N/A | [7 empty] | 3800
Nortek Global | Maytag | M1200 | 10296733 | PSH1BG4CVRX36K | B6VMAX36K-B | HRCU-A-CB | 10 | 19 | 12.6 | 34800 | Yes | Centrally Ducted | N/A | N/A | 16500 | 34400 | 36800 | 1 | 2.7 | 3.2 | 4.8357 | 3.7339 | 3.3703 |  | 9900 | 21800 | 23900 | 1 | 2.4 | 2.7 | 2.9014 | 2.6621 | 2.5942 |  | 7500 |  | 20100 | 0.9 |  | 2.6 | 2.4423 |  | 2.2657 | 54.62% | 84.1% | N/A | 0 | 0 | N/A |  |  |  |  | 1.85 | 2.26 | 1.66 | 1900
Panasonic | Panasonic | RAC Multi E | 10221199 | CU-3E19RBU-5 | Non-Ducted Indoor Unit | HMSV-A-CB | 10.5 | 22 | 12.55 | 19000 | Yes | Ductless | Multi-zone | Non-ducted indoor units | 5500 | 26000 | 28400 | 0.32 | 2.06 | 2.3 | 5 | 3.7 | 3.61 |  | 4100 | 19800 | 20800 | 0.37 | 2.37 | 2.85 | 3.2496 | 2.45 | 2.1402 |  | 3800 |  | 18900 | 0.37 |  | 2.64 | 3.01 |  | 2.1 | 66.55% | 90.87% | Accessory for outdoor unit CU-3E19RBU-5; Wind Baffle # WINDB-M1 |  |  | -5°F | 2000 |  | 10500 | 0.26 | 1.31 | 3.6093 | 1.567 | 1200
Panasonic | Panasonic | Exterios-Series | 7958198 | CS-E9RKUA | CU-E9RKUAW | HRCU-A-CB-O | 11 | 23 | 13 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4100 | 12000 | 14100 | 0.2 | 1.12 | 1.5 | 6 | 3.14 | 2.76 |  | 3200 | 8100 | 9500 | 0.19 | 0.99 | 1.33 | 4.939 | 2.3994 | 2.1 |  | 2400 |  | 8300 | 0.16 |  | 1.32 | 4.3988 |  | 1.844 | 58.87% | 87.37% | N/A |  |  | -5°F | 1600 |  | 7000 | 0.13 | 1.6 | 3.6093 | 1.4479 | 1400
Panasonic | Panasonic | Exterios-Series | 7958199 | CS-E12RKUA | CU-E12RKUAW | HRCU-A-CB-O | 11 | 22.5 | 12.5 | 11500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4100 | 13800 | 16300 | 0.2 | 1.25 | 1.71 | 6 | 3.24 | 2.79 |  | 3200 | 8900 | 10500 | 0.19 | 1.05 | 1.44 | 4.939 | 2.4857 | 2.14 |  | 2400 |  | 9100 | 0.16 |  | 1.51 | 4.3988 |  | 1.7673 | 55.83% | 86.67% | N/A |  |  | -5°F | 1600 |  | 7900 | 0.13 | 1.29 | 2.143 | 1.8641 | 1900
Panasonic | Panasonic | Exterios E:Deluxe | 7958200 | CS-E18RKUA | CU-E18RKUAW | HRCU-A-CB-O | 10 | 19.5 | 13.2 | 17200 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 5800 | 21600 | 22000 | 0.38 | 1.75 | 1.8 | 4.47 | 3.62 | 3.57 |  | 3400 | 11600 | 12000 | 0.34 | 1.3 | 1.35 | 2.9326 | 2.6167 | 2.6 |  | 2600 |  | 10100 | 0.3 |  | 1.32 | 2.5415 |  | 2.2438 | 45.91% | 84.17% | N/A |  |  | -5°F | 1900 |  | 8200 | 0.26 | 1.72 | 3.8123 | 1.7732 | 0
Panasonic | Panasonic | Exterios XE | 8860533 | CU-XE9SKUA | CS-XE9SKUA | HRCU-A-CB-O | 14 | 30.6 | 17.05 | 8700 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 10900 | 18000 | 0.15 | 0.67 | 1.65 | 5.93 | 4.78 | 3.21 |  | 2100 | 8000 | 11000 | 0.14 | 0.75 | 1.38 | 4.3988 | 3.1261 | 2.34 |  | 1700 |  | 11000 | 0.12 |  | 1.73 | 4.1544 |  | 1.86 | 61.11% | 100% | included with outdoor unit CU-XE9SKUA | 510 | Heater Energizes 1) Outdoor Ambient lower than or equal to 37 F 2) Heating Operations 3) During defrost cycle Control content 1) Base pan heater will start to heat up when defrost operation starts. 2) Base pan heater will stop heating 10 minutes after defrost stops. Heater won't Energize 1) Outdoor ambient higher than 37 F | -5°F | 1300 |  | 10400 | 0.1 | 2.01 | 3.8123 | 1.7216 | 0
Panasonic | Panasonic | Exterios XE | 8861565 | CU-XE12SKUA | CS-XE12SKUA | HRCU-A-CB-O | 12.5 | 26.2 | 14.7 | 11500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 13600 | 23000 | 0.15 | 0.95 | 2.1 | 5.93 | 4.1955 | 3.2 |  | 2100 | 10400 | 12500 | 0.14 | 1.05 | 1.6662 | 4.3988 | 2.9028 | 2.2 |  | 1700 |  | 12500 | 0.12 |  | 1.99 | 4.1544 |  | 1.84 | 54.35% | 100% | included with outdoor unit CU-XE12SKUA | 780 | Heater Energizes 1) Outdoor Ambient lower than or equal to 37 F 2) Heating Operations 3) During defrost cycle Control content 1) Base pan heater will start to heat up when defrost operation starts. 2) Base pan heater will stop heating 10 minutes after defrost stops. Heater won't Energize 1) Outdoor ambient higher than 37 F | -5°F | 1300 |  | 11800 | 0.1 | 1.1 | 2.9326 | 1.7862 | 1200
Panasonic | Panasonic | Low-Profile Ducted | 9125308 | CU-E9SD3UA | CS-E9SD3UAW | HRCU-A-CB-O | 10 | 20.5 | 13 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4100 | 9000 | 10200 | 0.25 | 0.69 | 0.85 | 4.8 | 3.82 | 3.53 |  | 3200 | 7900 | 9000 | 0.23 | 0.91 | 1.12 | 4.0801 | 2.5458 | 2.36 |  | 2400 |  | 7800 | 0.2 |  | 1.11 | 3.5191 |  | 2.0607 | 76.47% | 86.67% | N/A |  |  | -5°F | 1600 |  | 6700 | 0.16 | 1.6 | 2.9326 | 1.5029 | 1400
Panasonic | Panasonic | Low-Profile Ducted | 9125309 | CU-E12SD3UA | CS-E12SD3UAW | HRCU-A-CB-O | 10 | 20 | 12.5 | 11500 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 4100 | 11500 | 13300 | 0.25 | 0.92 | 1.15 | 4.8 | 3.64 | 3.39 |  | 3200 | 9500 | 11000 | 0.23 | 1.15 | 1.44 | 4.0801 | 2.4225 | 2.24 |  | 2400 |  | 9600 | 0.2 |  | 1.52 | 3.5191 |  | 1.8521 | 72.18% | 87.27% | N/A |  |  | -5°F | 1600 |  | 8200 | 0.16 | 2.34 | 2.4814 | 1.8673 | 800
Panasonic | Panasonic | Wall Mounted | 9571162 | CU-XE15SKUA | CS-XE15SKUA | HRCU-A-CB-O | 12 | 22.1 | 12.5 | 15000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3300 | 18000 | 24000 | 0.2 | 1.3 | 2.65 | 4.9 | 4.06 | 2.65 |  | 2000 | 11000 | 16500 | 0.16 | 1.02 | 2.3 | 3.6657 | 3.16 | 2.1 |  | 1500 |  | 15700 | 0.15 |  | 2.32 | 2.9326 |  | 1.98 | 65.42% | 95.15% | included with outdoor unit (Replacement part # CWA341072) | 100 | Heater Energizes 1) Outdoor Ambient lower than or equal to 37 F 2) Heating Operations 3) During defrost cycle Control content 1) Base pan heater will start to heat up when defrost operation starts. 2) Base pan heater will stop heating 10 minutes after defrost stops. Heater won't Energize 1) Outdoor ambient higher than 37 F | -5°F | 1100 |  | 14900 | 0.13 | 3.8 | 1.4654 | 1.5425 | 0
SAMSUNG ELECTRONCS CO., LTD. | SAMSUNG | FJM | 10298668 | AJ030MCS4CH/AA | Non-ducted | HMSV-A-CB | 11 | 18 | 12.5 | 28400 | Yes | Ductless | Multi-zone | Non-ducted indoor units (Wall Mount) | 7600 | 28600 | 28600 | 0.45 | 2.09 | 2.09 | 4.9496 | 4.0104 | 4.0104 |  | 13100 | 18500 | 28600 | 1.65 | 1.95 | 4 | 2.3268 | 2.7804 | 2.0955 |  | 13100 |  | 28600 | 1.9 |  | 4.65 | 2.0206 |  | 1.8025 | 100% | 100% | Integrated | 150W @230V | (Starting Conditions) 1. Outdoor Air temp ≤ 33.8℉ And 2. Heating Operation. (Stop Conditions) It will be checked every 5 minutes after Base heater operation. 1. Outdoor Air temp ≥ 35.6℉ Or 2. Heating Operation is finished. | -13°F | 10000 |  | 20000 | 2 | 3.9 | 1.5029 | 1.5029 | 0
SAMSUNG ELECTRONCS CO., LTD. | SAMSUNG | FJM | 10298670 | AJ024MCS4CH/AA | Non-ducted | HMSV-A-CB | 10 | 19 | 12.5 | 25000 | Yes | Ductless | Multi-zone | Non-ducted indoor units (Wall Mount) | 7600 | 25000 | 25000 | 0.45 | 1.83 | 1.83 | 4.9496 | 4.0037 | 4.0037 |  | 13000 | 14000 | 25000 | 1.5 | 1.55 | 3.45 | 2.5399 | 2.6471 | 2.1237 |  | 12000 |  | 25000 | 1.7 |  | 4 | 2.0687 |  | 1.8317 | 100% | 100% | Integrated | 150W @230V | (Starting Conditions) 1. Outdoor Air temp ≤ 33.8℉ And 2. Heating Operation. (Stop Conditions) It will be checked every 5 minutes after Base heater operation. 1. Outdoor Air temp ≥ 35.6℉ Or 2. Heating Operation is finished. | -13°F | 10000 |  | 20000 | 1.95 | 4 | 1.5029 | 1.4654 | 0
SAMSUNG ELECTRONCS CO., LTD. | SAMSUNG | FJM | 10348192 | AJ020MCS3CH/AA | Non-ducted | HMSV-A-CB | 10 | 18 | 12.5 | 21000 | Yes | Ductless | Multi-zone | Non-ducted indoor units (Wall Mount) | 7600 | 22000 | 22000 | 0.45 | 1.61 | 1.61 | 4.9496 | 4.0047 | 4.0047 |  | 13000 | 13000 | 22000 | 1.6 | 1.45 | 2.9 | 2.3812 | 2.6275 | 2.2233 |  | 12000 |  | 22000 | 1.8 |  | 3.3 | 1.9538 |  | 1.9538 | 100% | 100% | Integrated | 150W @230V | (Starting Conditions) 1. Outdoor Air temp ≤ 33.8℉ And 2. Heating Operation. (Stop Conditions) It will be checked every 5 minutes after Base heater operation. 1. Outdoor Air temp ≥ 35.6℉ Or 2. Heating Operation is finished. | -13°F | 10000 |  | 20000 | 1.95 |  |  |  | 2052
SAMSUNG ELECTRONCS CO., LTD. | SAMSUNG | Smart Whisper Series | 8677407 | AR09KSWSJWKX | AR09KSWSJWKN | HRCU-A-CB-O | 10.5 | 23 | 15 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3378 | 12000 | 12360 | 0.19 | 0.88 | 0.93 | 5.2105 | 3.9964 | 3.895 |  | 3220 | 5600 | 12612 | 0.27 | 0.62881 | 1.62 | 3.4951 | 2.61 | 2.2816 |  | 3157 |  | 10560 | 0.3 |  | 1.71 | 3.0841 |  | 1.8098 | 85.44% | 83.73% | N/A | N/A | N/A | N/A |  |  |  |  | 5.88 | 2.0566 | 1.3956 | 4000
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | CAC Max Heat HSP | 8203117 | AC030JXSCCH/AA | AC030JNHDCH/AA | HRCU-A-CB | 10.1 | 21 | 13 | 30000 | Yes | Centrally Ducted | N/A | N/A | 13000 | 32000 | 37000 | 0.92 | 2.468 | 3.18 | 4.1412 | 3.7999 | 3.4099 |  | 12500 | 20800 | 36000 | 1.11 | 2.33 | 5.38 | 3.3003 | 2.6163 | 1.9611 |  | 12000 |  | 32000 | 1.44 |  | 5.22 | 2.4423 |  | 1.7966 | 86.49% | 88.89% | Integrated | 150W @230V | [Operation condition - (1)&(2)&(3)&(4)] (1) Heating mode (2) Compressor must be turned on (3) Outside temperature is below 30F for more than 5 minutes. (4) Outdoor fan motor is turned ON. | -13°F | 12000 |  | 28000 | 1.71 | 7.02 | 1.865 | 1.3359 | 4000
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | CAC Max Heat HSP | 8203122 | AC036JXSCCH/AA | AC036JNHDCH/AA | HRCU-A-CB | 10.4 | 20 | 12.8 | 36000 | Yes | Centrally Ducted | N/A | N/A | 14000 | 40000 | 46000 | 1.12 | 3.51 | 4.52 | 3.6634 | 3.3398 | 2.9826 |  | 13500 | 25600 | 44000 | 1.48 | 2.94 | 7.02 | 2.6733 | 2.5519 | 1.8369 |  | 14000 |  | 40000 | 1.88 |  | 6.66 | 2.1824 |  | 1.7602 | 86.96% | 90.91% | Integrated | 150W @230V | [Operation condition - (1)&(2)&(3)&(4)] (1) Heating mode (2) Compressor must be turned on (3) Outside temperature is below 30F for more than 5 minutes. (4) Outdoor fan motor is turned ON. | -13 | 14000 |  | 32000 | 2.2 | 1.52 | 1.7017 | 1.5425 | 1300
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | CAC Slim Duct | 8717080 | AC009KXADCH | AC009KNLDCH | HRCU-A-CB | 10.5 | 21 | 13.95 | 9000 | Yes | Centrally Ducted | N/A | N/A | 2900 | 12000 | 14000 | 0.25 | 1.127 | 1.5 | 3.3996 | 3.1205 | 2.7353 |  | 2720 | 7800 | 12000 | 0.31 | 0.921 | 1.54 | 2.5715 | 2.482 | 2.2837 |  | 2200 |  | 10700 | 0.34 |  | 1.62 | 1.8963 |  | 1.9357 | 76.43% | 89.17% | N/A |  |  | -4°F | 1800 |  | 8000 | 0.31 | 5.62 | 2.2259 | 1.4601 | 4000
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | CAC Max Heat 4 Way | 8203107 | AC030JXSCCH/AA | AC030JN4DCH/AA | HRCU-A-CB-O | 10.1 | 21 | 13.1 | 30000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 13000 | 32000 | 37000 | 0.9 | 2.468 | 3.16 | 4.2332 | 3.7999 | 3.4315 |  | 12500 | 20800 | 36000 | 1.01 | 2.21 | 5.28 | 3.6271 | 2.7583 | 1.9982 |  | 12000 |  | 32000 | 1.32 |  | 5.02 | 2.6643 |  | 1.8682 | 86.49% | 88.89% | Integrated | 150W @230V | [Operation condition - (1)&(2)&(3)&(4)] (1) Heating mode (2) Compressor must be turned on (3) Outside temperature is below 30F for more than 5 minutes. (4) Outdoor fan motor is turned ON. | -13°F | 12000 |  | 28000 | 1.58 | 6.88 | 2.0515 | 1.3631 | 4000
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | CAC Max Heat 4 Way | 8203116 | AC036JXSCCH/AA | AC036JN4DCH/AA | HRCU-A-CB-O | 10.4 | 20 | 12.9 | 36000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 14000 | 40000 | 46000 | 1.02 | 3.238 | 4.2 | 4.0225 | 3.6204 | 3.2098 |  | 13500 | 25000 | 44000 | 1.34 | 2.64 | 6.72 | 2.9526 | 2.7753 | 1.9189 |  | 14000 |  | 40000 | 1.72 |  | 6.6 | 2.3855 |  | 1.7762 | 86.96% | 90.91% | Integrated | 150W @230V | [Operation condition - (1)&(2)&(3)&(4)] (1) Heating mode (2) Compressor must be turned on (3) Outside temperature is below 30F for more than 5 minutes. (4) Outdoor fan motor is turned ON. | -13 | 14000 |  | 32000 | 2 |  |  |  | 2779
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | Smart Pearl Series | 8677405 | AR09KSWDHWKX | AR09KSWDHWKN | HRCU-A-CB-O | 12 | 28.1 | 15.8 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2730 | 12600 | 12978 | 0.17 | 0.85 | 0.9 | 4.7064 | 4.3443 | 4.2261 |  | 2708 | 5600 | 13867 | 0.32 | 0.62881 | 1.79 | 2.4801 | 2.61 | 2.2704 |  | 2700 |  | 11088 | 0.38 |  | 1.81 | 2.0823 |  | 1.7953 | 85.44% | 79.96% | N/A | N/A | N/A | N/A | [7 empty] | 3015
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | Smart Pearl Series | 8677406 | AR12KSWDHWKX | AR12KSWDHWKN | HRCU-A-CB-O | 11.5 | 26.1 | 14.1 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2730 | 13600 | 14008 | 0.17 | 0.93 | 0.9765 | 4.7064 | 4.2858 | 4.2041 |  | 2726 | 7800 | 14983 | 0.32 | 0.88603 | 1.92 | 2.4966 | 2.58 | 2.287 |  | 2724 |  | 11968 | 0.37 |  | 1.92 | 2.1576 |  | 1.8268 | 85.44% | 79.88% | N/A | N/A | N/A | N/A | [7 empty] | 4422
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | Smart Whisper Series | 8677410 | AR24KSWSJWKX | AR24KSWSJWKN | HRCU-A-CB-O | 10.7 | 21.6 | 12.5 | 21000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 7506 | 27000 | 27810 | 0.48 | 2.52 | 2.646 | 4.5829 | 3.14 | 3.0802 |  | 6427 | 17000 | 28182 | 0.49 | 1.8051 | 3.84 | 3.844 | 2.76 | 2.1509 |  | 5996 |  | 23760 | 0.49 |  | 3.89 | 3.5862 |  | 1.7901 | 85.44% | 84.31% | N/A | N/A | N/A | N/A |  |  |  |  | 1.67 | 2.4618 | 1.7549 | 1490
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | Max Heat RAC Series | 9035283 | AR09KSWSPWKX | AR09KSWSPWKN | HRCU-A-CB-O | 10.5 | 23.5 | 14.05 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2730 | 12000 | 12360 | 0.17 | 0.77 | 0.81 | 4.7064 | 4.5673 | 4.472 |  | 3105 | 6500 | 13990 | 0.27 | 0.8211 | 1.63 | 3.3703 | 2.32 | 2.5154 |  | 2730 |  | 12500 | 0.31 |  | 1.96 | 2.5809 |  | 1.8691 | 101.1% | 89.35% | Integrated | 230VAC 150W | Temp. below 0 degrees | -13°F | 2184 |  | 10000 | 0.26 | 1.67 | 2.4618 | 1.9936 | 2000
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | Max Heat RAC Series | 9035284 | AR12KSWSPWKX | AR12KSWSPWKN | HRCU-A-CB-O | 10 | 21.5 | 12.5 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2730 | 14000 | 14420 | 0.17 | 0.97 | 1.0185 | 4.7064 | 4.2299 | 4.1493 |  | 3095 | 7500 | 16200 | 0.29 | 0.90454 | 1.9 | 3.1278 | 2.43 | 2.4988 |  | 2730 |  | 14200 | 0.33 |  | 2.25 | 2.4245 |  | 1.8496 | 98.47% | 87.65% | Integrated | 230VAC 150W | Temp. below 0 degrees | -13°F | 2184 |  | 11360 | 0.26 |  |  |  | 1120
SAMSUNG ELECTRONICS CO., LTD. | SAMSUNG | Wind Free RAC Series | 10103172 | AR09MSWXCWKX | AR09MSWXCWKN | HRCU-A-CB-O | 10 | 21 | 14.05 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 11000 | 11330 | 0.16 | 0.86 | 0.903 | 5.4951 | 3.7486 | 3.6772 |  | 3310.9091 | 5500 | 10800 | 0.2586 | 0.62476 | 1.4426 | 3.7522 | 2.58 | 2.1941 |  | 3435.2727 |  | 9680 | 0.29805 |  | 1.6116 | 3.3779 |  | 1.7603 | 85.44% | 89.63% | N/A | N/A | N/A | N/A |  |  |  |  | 0.787 | 2.52 | 1.64 | 3032
Toshiba Carrier | Carrier |  | 6960758 | RAS-09EAV-UL | RAS-09EKV-UL | N/A | 10 | 20 | 13 | N/A | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3070 | 10800 | 16350 | 0.17 | 0.8 | 1.4 | 5.29 | 3.95 | 3.42 |  | 1795 | 6313 | 9551 | 0.127 | 0.61 | 1.042 | 4.14 | 3.03 | 2.69 |  | 1224 |  | 6519 | 0.109 |  | 0.895 | 3.29 |  | 2.13 | 39.87% | 68.25% | N/A |  |  | -4 | 828 | z | 4409 | 0.096 | 1.067 | 2.72 | 1.59 | 3801
Toshiba Carrier | Carrier |  | 6960762 | RAS-15EAV-UL | RAS-15EKV-UL | N/A | 10 | 20 | 13 | N/A | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) | 2750 | 18000 | 21500 | 0.143 | 1.4 | 1.9 | 5.64 | 3.77 | 3.32 |  | 1608 | 10400 | 12553 | 0.106 | 1.042 | 1.415 | 4.444 | 2.93 | 2.6 |  | 1096 |  | 8752 | 0.091 |  | 1.215 | 3.52 |  | 2.11 | 40.71% | 69.72% | N/A |  |  | -4 | 742 | z | 5798 | 0.08 | 1.073 | 2.59 | 1.58 | 3981
Toshiba Carrier | Carrier |  | 6960764 | RAS-17EAV-UL | RAS-17EKV-UL | N/A | 10 | 19 | 12.6 | N/A | Yes | Ductless | Single-zone | Non-ducted indoor units (Wall Mount) | 2750 | 20200 | 21500 | 0.15 | 1.63 | 1.91 | 5.37 | 3.63 | 3.3 |  | 1608 | 10500 | 12553 | 0.112 | 1.214 | 1.422 | 4.2 | 2.53 | 2.59 |  | 1096 |  | 8572 | 0.096 |  | 1.221 | 3.35 |  | 2.06 | 39.87% | 68.29% | N/A |  |  | -4 | 742 | z | 5798 | 0.084 |  |  |  | 3800
Trane | Trane |  | 6749942 | 4TWV0024A1 | *AM8C0B30V21 | HRCU-A-CB | 10 | 19.25 | 13.75 | 24200 | Yes | Centrally Ducted | N/A | N/A | 7800 | 20200 | 21900 | 0.5 | 1.64 | 1.56 | 4.58 | 3.61 | 4.12 |  | 11430 | 16800 | 16800 | 1.18 | 1.97 | 1.91 | 2.84 | 2.5 | 2.58 |  | 11176 |  | 13000 | 1.58 |  | 1.84 | 2.08 |  | 2.08 | 59.36% | 77.38% | N/A |  |  | N/A | [7 empty] | 7680
Trane | Trane |  | 6749944 | 4TWV0048A1 | *AM8C0C48V41 | HRCU-A-CB | 10 | 19.25 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 11800 | 42500 | 42600 | 0.74 | 4.15 | 3.65 | 4.68 | 3 | 3.42 |  | 21530 | 34000 | 34400 | 2.61 | 4.74 | 4.66 | 2.42 | 2.1 | 2.16 |  | 22446 |  | 26720 | 3.72 |  | 4.44 | 1.76 |  | 1.76 | 62.72% | 77.67% | N/A |  |  | N/A | [7 empty] | 5720
Trane | Trane |  | 6750234 | 4TWV8036A1 | *AM8C0C36V31 | HRCU-A-CB | 10 | 18 | 13 | 35000 | Yes | Centrally Ducted | N/A | N/A | 8200 | 32200 | 32200 | 0.47 | 3.04 | 2.6 | 5.12 | 3.1 | 3.62 |  | 15710 | 25200 | 25400 | 1.85 | 3.36 | 3.33 | 2.48 | 2.2 | 2.24 |  | 16488 |  | 19680 | 2.66 |  | 3.18 | 1.82 |  | 1.82 | 61.12% | 77.48% | N/A |  |  | N/A | [7 empty] | 7720
Trane | Trane |  | 6750235 | 4TWV8048A1 | *AM8C0C48V41 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 11800 | 41000 | 43000 | 0.74 | 3.88 | 3.64 | 4.68 | 3.1 | 3.46 |  | 21860 | 34400 | 34800 | 2.57 | 4.58 | 4.61 | 2.5 | 2.2 | 2.22 |  | 22792 |  | 27080 | 3.66 |  | 4.38 | 1.82 |  | 1.82 | 62.98% | 77.82% | N/A |  |  | N/A |  | z | [5 empty] | 3800
Trane | Trane |  | 6750459 | 4TWV8024A1 | *AM8C0B30V21 | HRCU-A-CB | 10 | 18 | 13 | 23800 | Yes | Centrally Ducted | N/A | N/A | 7800 | 20000 | 21900 | 0.5 | 1.63 | 1.56 | 4.58 | 3.6 | 4.12 |  | 11430 | 16800 | 16800 | 1.18 | 1.97 | 1.91 | 2.84 | 2.5 | 2.58 |  | 11176 |  | 13000 | 1.58 |  | 1.84 | 2.08 |  | 2.08 | 59.36% | 77.38% | N/A |  |  | N/A | [7 empty] | 7680
Trane | Trane |  | 6750461 | 4TWV8049A1 | *AM8C0C48V41 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 11800 | 41500 | 42600 | 0.74 | 4.05 | 3.65 | 4.68 | 3 | 3.42 |  | 21530 | 34000 | 34400 | 2.61 | 4.74 | 4.66 | 2.42 | 2.1 | 2.16 |  | 22446 |  | 26720 | 3.72 |  | 4.44 | 1.76 |  | 1.76 | 62.72% | 77.67% | N/A |  |  | N/A |  | z | [5 empty] | 6100
Trane | Trane |  | 6796600 | 4TWV0036A1 | *UD2C080ACV4 4TXCC007CC3 | HRCU-A-CB | 10 | 20 | 13 | 34600 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32000 | 33100 | 0.49 | 2.93 | 2.57 | 4.96 | 3.2 | 3.78 |  | 15710 | 25800 | 25900 | 1.88 | 3.44 | 3.35 | 2.44 | 2.2 | 2.26 |  | 16488 |  | 19800 | 2.7 |  | 3.22 | 1.78 |  | 1.8 | 59.82% | 76.45% | N/A |  |  | N/A | [7 empty] | 6000
Trane | Trane |  | 6796602 | 4TWV0036A1 | *UD2C100ACV5 4TXCC007CC3 | HRCU-A-CB | 10 | 20 | 13 | 34800 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 33100 | 0.49 | 2.91 | 2.59 | 4.96 | 3.2 | 3.74 |  | 15710 | 25600 | 25900 | 1.88 | 3.41 | 3.35 | 2.44 | 2.2 | 2.26 |  | 16588 |  | 19900 | 2.7 |  | 3.2 | 1.8 |  | 1.82 | 60.12% | 76.83% | N/A |  |  | N/A | [7 empty] | 5800
Trane | Trane |  | 6796604 | 4TWV0036A1 | *UD2C080ACV4 4TXFH036CZ3 | HRCU-A-CB | 10 | 20 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8100 | 31200 | 32400 | 0.5 | 2.86 | 2.51 | 4.74 | 3.2 | 3.78 |  | 15710 | 25600 | 25700 | 1.86 | 3.41 | 3.28 | 2.48 | 2.2 | 2.3 |  | 16628 |  | 19900 | 2.66 |  | 3.16 | 1.84 |  | 1.84 | 61.42% | 77.43% | N/A |  |  | N/A | [7 empty] | 6240
Trane | Trane |  | 6796635 | 4TWV8037A1 | *AM8C0B30V21 | HRCU-A-CB | 10 | 18 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32600 | 33900 | 0.5 | 2.81 | 2.55 | 4.92 | 3.4 | 3.9 |  | 15930 | 26200 | 26400 | 1.85 | 3.34 | 3.3 | 2.52 | 2.3 | 2.34 |  | 16688 |  | 20160 | 2.66 |  | 3.16 | 1.84 |  | 1.86 | 59.47% | 76.36% | N/A |  |  | N/A | [7 empty] | 5860
Trane | Trane |  | 6796636 | 4TWV8037A1 | *UD2B080ACV3 4TXCB004CC3 | HRCU-A-CB | 10 | 18 | 12.5 | 34800 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32000 | 33300 | 0.5 | 3.02 | 2.68 | 4.86 | 3.1 | 3.64 |  | 16040 | 25800 | 26100 | 1.95 | 3.44 | 3.46 | 2.42 | 2.2 | 2.22 |  | 16934 |  | 20240 | 2.8 |  | 3.32 | 1.78 |  | 1.78 | 60.78% | 77.55% | N/A |  |  | N/A | [7 empty] | 6100
Trane | Trane |  | 6796638 | 4TWV8037A1 | *UD2C080ACV4 4TXCC007CC3 | HRCU-A-CB | 10 | 18 | 13 | 34600 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32000 | 33100 | 0.49 | 2.93 | 2.57 | 4.96 | 3.2 | 3.78 |  | 15710 | 25800 | 25900 | 1.88 | 3.44 | 3.36 | 2.44 | 2.2 | 2.26 |  | 16488 |  | 19800 | 2.7 |  | 3.22 | 1.78 |  | 1.8 | 59.82% | 76.45% | N/A |  |  | N/A | [7 empty] | 6000
Trane | Trane |  | 6796639 | 4TWV8037A1 | *UD2C100ACV5 4TXCC007CC3 | HRCU-A-CB | 10 | 18 | 13 | 34800 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 33100 | 0.49 | 2.91 | 2.6 | 4.96 | 3.2 | 3.74 |  | 15710 | 25600 | 25900 | 1.88 | 3.41 | 3.35 | 2.44 | 2.2 | 2.26 |  | 16588 |  | 19900 | 2.7 |  | 3.2 | 1.8 |  | 1.82 | 60.12% | 76.83% | N/A |  |  | N/A | [7 empty] | 5800
Trane | Trane |  | 6796641 | 4TWV8037A1 | *UD2C080ACV4 4TXFH036CZ3 | HRCU-A-CB | 10 | 18 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8100 | 31200 | 32400 | 0.5 | 2.86 | 2.52 | 4.74 | 3.2 | 3.76 |  | 15710 | 25600 | 25700 | 1.86 | 3.41 | 3.28 | 2.48 | 2.2 | 2.3 |  | 16628 |  | 19900 | 2.66 |  | 3.16 | 1.84 |  | 1.84 | 61.42% | 77.43% | N/A |  |  | N/A | [7 empty] | 6240
Trane | Trane |  | 6992578 | 4TWV0036A1 | *AM8C0B30V21 | HRCU-A-CB | 10 | 20 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32600 | 33900 | 0.5 | 2.81 | 2.55 | 4.92 | 3.4 | 3.9 |  | 15930 | 26200 | 26400 | 1.85 | 3.34 | 3.3 | 2.52 | 2.3 | 2.34 |  | 16688 |  | 20160 | 2.64 |  | 3.16 | 1.86 |  | 1.86 | 59.47% | 76.36% | N/A |  |  | N/A | [7 empty] | 6100
Trane | Trane |  | 7035765 | 4TWV8036A1 | *DD2C100ACV5 4NXCC005AS3 | HRCU-A-CB | 10 | 18 | 12.5 | 35800 | Yes | Centrally Ducted | N/A | N/A | 8400 | 31600 | 32600 | 0.5 | 2.99 | 2.54 | 4.92 | 3.1 | 3.76 |  | 16040 | 26200 | 26300 | 1.89 | 3.49 | 3.42 | 2.48 | 2.2 | 2.26 |  | 16828 |  | 20200 | 2.7 |  | 3.26 | 1.82 |  | 1.82 | 61.96% | 76.81% | N/A |  |  | N/A | [7 empty] | 6000
Trane | Trane |  | 7125586 | 4TWV0036A1 | *UHMB060ACV3 4TXCB004CC3 | HRCU-A-CB | 10 | 18.5 | 12.5 | 34800 | Yes | Centrally Ducted | N/A | N/A | 8500 | 31000 | 33500 | 0.55 | 2.93 | 2.73 | 4.52 | 3.1 | 3.6 |  | 16150 | 26000 | 26300 | 1.98 | 3.46 | 3.51 | 2.38 | 2.2 | 2.2 |  | 16934 |  | 20300 | 2.82 |  | 3.36 | 1.76 |  | 1.78 | 60.6% | 77.19% | N/A |  |  | N/A | [7 empty] | 5860
Trane | Trane |  | 7125587 | 4TWV0036A1 | *UHMB060ACV3 4TXFH036CZ3 | HRCU-A-CB | 10 | 18.75 | 12.5 | 34800 | Yes | Centrally Ducted | N/A | N/A | 8300 | 30400 | 32700 | 0.56 | 2.87 | 2.68 | 4.34 | 3.1 | 3.58 |  | 15930 | 25600 | 25900 | 1.96 | 3.41 | 3.45 | 2.38 | 2.2 | 2.2 |  | 16788 |  | 20040 | 2.78 |  | 3.32 | 1.76 |  | 1.76 | 61.28% | 77.37% | N/A |  |  | N/A | [7 empty] | 5760
Trane | Trane |  | 7125588 | 4TWV0036A1 | *DHMB060BCV3 4TXFH036CZ3 | HRCU-A-CB | 10 | 19.5 | 12.5 | 34800 | Yes | Centrally Ducted | N/A | N/A | 8300 | 30800 | 33200 | 0.52 | 2.82 | 2.65 | 4.68 | 3.2 | 3.68 |  | 16150 | 25800 | 26100 | 1.94 | 3.44 | 3.41 | 2.44 | 2.2 | 2.24 |  | 17034 |  | 20340 | 2.78 |  | 3.28 | 1.8 |  | 1.82 | 61.27% | 77.93% | N/A |  |  | N/A | [7 empty] | 5760
Trane | Trane |  | 7125597 | 4TWV8037A1 | *DHMB060BCV3 4TXFH036CZ3 | HRCU-A-CB | 10 | 18 | 12.5 | 34800 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31800 | 33200 | 0.52 | 2.91 | 2.66 | 4.68 | 3.2 | 3.66 |  | 16150 | 25800 | 26100 | 1.95 | 3.44 | 3.41 | 2.42 | 2.2 | 2.24 |  | 17034 |  | 20340 | 2.78 |  | 3.28 | 1.8 |  | 1.82 | 61.27% | 77.93% | N/A |  |  | N/A | [7 empty] | 7920
Trane | Trane |  | 7161152 | 4TWV0048A1 | *AM8C0C60V51 | HRCU-A-CB | 10 | 19.25 | 12.5 | 46500 | Yes | Centrally Ducted | N/A | N/A | 11800 | 43000 | 43100 | 0.74 | 3.94 | 3.53 | 4.68 | 3.2 | 3.58 |  | 21640 | 34200 | 34700 | 2.56 | 4.55 | 4.54 | 2.48 | 2.2 | 2.24 |  | 22486 |  | 26780 | 3.64 |  | 4.34 | 1.8 |  | 1.8 | 62.13% | 77.18% | N/A |  |  | N/A | [7 empty] | 5900
Trane | Trane |  | 7599437 | 4TWV0036A1 | *AM8C0C48V41 | HRCU-A-CB | 10 | 20.75 | 13.5 | 36000 | Yes | Centrally Ducted | N/A | N/A | 8400 | 33800 | 32800 | 0.5 | 2.83 | 2.38 | 4.92 | 3.5 | 4.04 |  | 15820 | 25400 | 25700 | 1.78 | 3.1 | 3.12 | 2.6 | 2.4 | 2.42 |  | 16548 |  | 19800 | 2.54 |  | 3 | 1.9 |  | 1.94 | 60.37% | 77.04% | N/A |  |  | N/A | [7 empty] | 6580
Trane | Trane | TruComfort XV20i | 8761409 | 4TWV0036A1 | *UHMB060ACV3 & 4TXCB006DS3 | HRCU-A-CB | 10 | 19.25 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8700 | 32800 | 33700 | 0.61 | 2.28 | 2.65 | 4.18 | 4.215 | 3.72 |  | 16260 | 26400 | 27100 | 1.99 | 2.28 | 3.49 | 2.4 | 3.3926 | 2.28 |  | 16994 |  | 20520 | 2.8 |  | 3.34 | 1.78 |  | 1.80 | 60.89% | 75.72% | N/A | [10 empty] | 6480
Trane | Trane | TruComfort XV20i | 8761420 | 4TWV0036A1 | *UHMC100ACV4 & 4TXCC007DS3 | HRCU-A-CB | 10 | 20 | 13 | 36800 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33200 | 33400 | 0.55 | 2.44 | 2.41 | 4.52 | 3.9867 | 4.06 |  | 16040 | 26800 | 26900 | 1.85 | 2.44 | 3.24 | 2.54 | 3.2182 | 2.44 |  | 16894 |  | 20420 | 2.62 |  | 3.1 | 1.88 |  | 1.95 | 61.14% | 75.91% | N/A | [10 empty] | 5860
Trane | Trane | TruComfort XV18 | 8761470 | 4TWV8036A1 | *UHMB080ACV3 & 4TXCC007DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36200 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33000 | 33100 | 0.56 | 2.4 | 2.44 | 4.44 | 4.0287 | 3.98 |  | 16700 | 26800 | 26900 | 1.89 | 2.4 | 3.28 | 2.58 | 3.2718 | 2.4 |  | 17640 |  | 21040 | 2.68 |  | 3.16 | 1.92 |  | 1.95 | 63.56% | 78.22% | N/A | [10 empty] | 6100
Trane | Trane | TruComfort XV18 | 8761473 | 4TWV8036A1 | *UHMC100ACV4 & 4TXCC007DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36400 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32800 | 32900 | 0.53 | 2.46 | 2.35 | 4.64 | 3.9066 | 4.1 |  | 16370 | 26600 | 26700 | 1.81 | 2.46 | 3.18 | 2.64 | 3.1682 | 2.46 |  | 17194 |  | 20600 | 2.56 |  | 3.04 | 1.96 |  | 2.00 | 62.61% | 77.15% | N/A | [10 empty] | 6480
Trane | Trane | TruComfort XV18 | 8761492 | 4TWV8037A1 | *UHMC100ACV4 & 4TXCC007DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 36800 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33200 | 33400 | 0.55 | 2.44 | 2.41 | 4.52 | 3.9867 | 4.06 |  | 16040 | 26800 | 26900 | 1.85 | 2.44 | 3.24 | 2.54 | 3.2182 | 2.44 |  | 16894 |  | 20420 | 2.62 |  | 3.1 | 1.88 |  | 1.95 | 61.14% | 75.91% | N/A | [10 empty] | 8360
Trane | Trane | TruComfort XV18 | 8761505 | 4TWV8048A1 | *UHMC100ACV4 & 4TXCC009DS3 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 12400 | 43500 | 44800 | 0.85 | 2.36 | 3.57 | 4.28 | 5.4006 | 3.68 |  | 23400 | 36600 | 37500 | 2.66 | 2.36 | 4.67 | 2.58 | 4.5439 | 2.36 |  | 24456 |  | 29140 | 3.72 |  | 4.44 | 1.92 |  | 1.90 | 65.04% | 77.71% | N/A | [10 empty] | 4180
Trane | Trane | TruComfort XV20i | 10093494 | 4TWV0024A1 | TAM9A0B30V31 | HRCU-A-CB | 10 | 19.25 | 13.75 | 24200 | Yes | Centrally Ducted | N/A | N/A | 8000 | 20200 | 21300 | 0.54 | 2.6 | 1.51 | 4.34 | 2.2764 | 4.14 |  | 11430 | 17100 | 17100 | 1.21 | 2.6 | 1.93 | 2.76 | 1.927 | 2.6 |  | 11036 |  | 12920 | 1.62 |  | 1.86 | 2.00 |  | 2.05 | 60.66% | 75.56% | N/A | [10 empty] | 6380
Trane | Trane | TruComfort XV20i | 10093495 | 4TWV0036A1 | TAM9A0B30V31 | HRCU-A-CB | 10 | 20 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8600 | 32600 | 33200 | 0.54 | 2.42 | 2.44 | 4.66 | 3.947 | 3.98 |  | 16040 | 26200 | 26600 | 1.82 | 2.42 | 3.22 | 2.58 | 3.1721 | 2.42 |  | 16748 |  | 20220 | 2.58 |  | 3.08 | 1.90 |  | 1.90 | 60.9% | 76.02% | N/A | [10 empty] | 6240
Trane | Trane | TruComfort XV20i | 10093496 | 4TWV0036A1 | TAM9A0C36V31 | HRCU-A-CB | 10 | 21 | 13.5 | 35000 | Yes | Centrally Ducted | N/A | N/A | 8500 | 33400 | 32800 | 0.52 | 2.38 | 2.43 | 4.78 | 4.1118 | 3.96 |  | 15820 | 25800 | 26100 | 1.83 | 2.38 | 3.22 | 2.54 | 3.1762 | 2.38 |  | 16448 |  | 19860 | 2.58 |  | 3.08 | 1.86 |  | 1.90 | 60.55% | 76.09% | N/A | [10 empty] | 5760
Trane | Trane | TruComfort XV20i | 10093497 | 4TWV0036A1 | TAM9A0C42V41 | HRCU-A-CB | 10 | 21 | 13.5 | 35600 | Yes | Centrally Ducted | N/A | N/A | 8400 | 33600 | 31200 | 0.51 | 2.2 | 2.53 | 4.82 | 4.4749 | 3.62 |  | 15600 | 24800 | 25200 | 1.9 | 2.2 | 3.36 | 2.4 | 3.3029 | 2.2 |  | 16242 |  | 19440 | 2.7 |  | 3.22 | 1.76 |  | 1.75 | 62.31% | 77.14% | N/A | [10 empty] | 7960
Trane | Trane | TruComfort XV20i | 10093500 | 4TWV0048A1 | TAM9A0C60V51 | HRCU-A-CB | 10 | 19.5 | 12.5 | 46500 | Yes | Centrally Ducted | N/A | N/A | 12000 | 43000 | 42700 | 0.78 | 2.26 | 3.56 | 4.5 | 5.5747 | 3.52 |  | 22630 | 35600 | 36100 | 2.65 | 2.26 | 4.67 | 2.5 | 4.6154 | 2.26 |  | 23644 |  | 28140 | 3.74 |  | 4.46 | 1.86 |  | 1.85 | 65.9% | 77.95% | N/A | [10 empty] | 4180
Trane | Trane | TruComfort XV18 | 10093502 | 4TWV8024A1 | TAM9A0B30V31 | HRCU-A-CB | 10 | 18 | 13 | 23800 | Yes | Centrally Ducted | N/A | N/A | 8000 | 20000 | 21000 | 0.54 | 2.6 | 1.55 | 4.34 | 2.2538 | 3.96 |  | 11430 | 17100 | 17100 | 1.21 | 2.6 | 1.93 | 2.76 | 1.927 | 2.6 |  | 11036 |  | 12920 | 1.62 |  | 1.86 | 2.00 |  | 2.05 | 61.52% | 75.56% | N/A | [10 empty] | 4120
Trane | Trane | TruComfort XV18 | 10093503 | 4TWV8024A1 | TAM9A0C36V31 | HRCU-A-CB | 10 | 18 | 13 | 24000 | Yes | Centrally Ducted | N/A | N/A | 8000 | 21000 | 21400 | 0.54 | 2.52 | 1.52 | 4.34 | 2.4416 | 4.12 |  | 11320 | 16900 | 16900 | 1.23 | 2.52 | 1.96 | 2.7 | 1.9649 | 2.52 |  | 10830 |  | 12780 | 1.64 |  | 1.9 | 1.94 |  | 1.95 | 59.72% | 75.62% | N/A | [10 empty] | 6040
Trane | Trane | TruComfort XV18 | 10093504 | 4TWV8036A1 | TAM9A0B30V31 | HRCU-A-CB | 10 | 18 | 12.5 | 34400 | Yes | Centrally Ducted | N/A | N/A | 8400 | 32000 | 43900 | 0.53 | 2.4 | 3.45 | 4.64 | 3.9066 | 3.72 |  | 16370 | 26600 | 26800 | 1.84 | 2.4 | 3.27 | 2.6 | 3.2474 | 2.4 |  | 17340 |  | 20760 | 2.6 |  | 3.12 | 1.96 |  | 1.95 | 47.29% | 77.46% | N/A
Trane | Trane | TruComfort XV18 | 10093505 | 4TWV8036A1 | TAM9A0C36V31 | HRCU-A-CB | 10 | 18 | 13 | 35000 | Yes | Centrally Ducted | N/A | N/A | 8300 | 32200 | 43400 | 0.52 | 2.36 | 3.36 | 4.68 | 3.9977 | 3.78 |  | 16260 | 26200 | 26400 | 1.85 | 2.36 | 3.27 | 2.58 | 3.2528 | 2.36 |  | 17134 |  | 20500 | 2.64 |  | 3.14 | 1.90 |  | 1.90 | 47.24% | 77.65% | N/A
Trane | Trane | TruComfort XV18 | 10093506 | 4TWV8036A1 | TAM9A0C42V41 | HRCU-A-CB | 10 | 18 | 12.5 | 35800 | Yes | Centrally Ducted | N/A | N/A | 8400 | 30000 | 31200 | 0.51 | 2.22 | 2.54 | 4.82 | 3.9594 | 3.6 |  | 16040 | 25400 | 25700 | 1.91 | 2.22 | 3.39 | 2.46 | 3.3523 | 2.22 |  | 16894 |  | 20040 | 2.72 |  | 3.24 | 1.82 |  | 1.80 | 64.23% | 77.98% | N/A
Trane | Trane | TruComfort XV18 | 10093507 | 4TWV8037A1 | TAM9A0B30V31 | HRCU-A-CB | 10 | 18 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8600 | 32600 | 33200 | 0.54 | 2.42 | 2.44 | 4.66 | 3.947 | 3.98 |  | 16040 | 26200 | 26600 | 1.82 | 2.42 | 3.22 | 2.58 | 3.1721 | 2.42 |  | 16748 |  | 20220 | 2.58 |  | 3.08 | 1.90 |  | 1.90 | 60.9% | 76.02% | N/A
Trane | Trane | TruComfort XV18 | 10093508 | 4TWV8037A1 | TAM9A0C36V31 | HRCU-A-CB | 10 | 18 | 13 | 35000 | Yes | Centrally Ducted | N/A | N/A | 8500 | 32800 | 32200 | 0.52 | 2.38 | 2.3 | 4.78 | 4.0379 | 4.1 |  | 15820 | 25800 | 26100 | 1.83 | 2.38 | 3.22 | 2.54 | 3.1762 | 2.38 |  | 16448 |  | 19860 | 2.58 |  | 3.08 | 1.86 |  | 1.90 | 61.68% | 76.09% | N/A
Trane | Trane | TruComfort XV18 | 10093509 | 4TWV8037A1 | TAM9A0C42V41 | HRCU-A-CB | 10 | 18 | 12.5 | 35800 | Yes | Centrally Ducted | N/A | N/A | 8400 | 30800 | 33300 | 0.51 | 2.2 | 2.68 | 4.82 | 4.102 | 3.64 |  | 15600 | 24800 | 25200 | 1.9 | 2.2 | 3.36 | 2.4 | 3.3029 | 2.2 |  | 16242 |  | 19440 | 2.7 |  | 3.22 | 1.76 |  | 1.75 | 58.38% | 77.14% | N/A
Trane | Trane | TruComfort XV18 | 10093510 | 4TWV8048A1 | TAM9A0C42V41 | HRCU-A-CB | 10 | 18 | 12.5 | 46500 | Yes | Centrally Ducted | N/A | N/A | 12300 | 41500 | 42600 | 0.76 | 2.14 | 3.8 | 4.74 | 5.682 | 3.28 |  | 23290 | 36200 | 36600 | 2.81 | 2.14 | 5 | 2.42 | 4.9563 | 2.14 |  | 24456 |  | 28920 | 4.04 |  | 4.8 | 1.78 |  | 1.75 | 67.89% | 79.02% | N/A
Trane | Trane | TruComfort XV18 | 10093511 | 4TWV8048A1 | TAM9A0C48V41 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 11900 | 41000 | 43000 | 0.76 | 2.36 | 3.46 | 4.58 | 5.0902 | 3.64 |  | 22960 | 36400 | 36800 | 2.59 | 2.36 | 4.57 | 2.6 | 4.5191 | 2.36 |  | 24190 |  | 28780 | 3.68 |  | 4.38 | 1.92 |  | 1.95 | 66.93% | 78.21% | N/A
Trane | Trane | TruComfort XV18 | 10093512 | 4TWV8048A1 | TAM9A0C60V51 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 11900 | 41500 | 42600 | 0.77 | 2.32 | 3.54 | 4.52 | 5.2411 | 3.52 |  | 22850 | 36200 | 36600 | 2.62 | 2.32 | 4.64 | 2.56 | 4.5718 | 2.32 |  | 24150 |  | 28680 | 3.72 |  | 4.42 | 1.90 |  | 1.90 | 67.32% | 78.36% | N/A
Trane | Trane | TruComfort XV18 | 10093515 | 4TWV8049A1 | TAM9A0C60V51 | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 12000 | 41000 | 31700 | 0.78 | 2.26 | 2.5 | 4.5 | 5.3154 | 3.72 |  | 22630 | 35600 | 36100 | 2.65 | 2.26 | 4.67 | 2.5 | 4.6154 | 2.26 |  | 23644 |  | 28140 | 3.74 |  | 4.46 | 1.86 |  | 1.85 | 88.77% | 77.95% | N/A
Trane | Trane | TruComfort XV18 | 10093516 | 4TWV8060A1 | TAM9A0C60V51 | HRCU-A-CB | 10 | 18 | 12.5 | 54000 | Yes | Centrally Ducted | N/A | N/A | 18400 | 50500 | 32300 | 1.21 | 2.1 | 2.55 | 4.46 | 7.0459 | 3.72 |  | 33510 | 49500 | 51100 | 3.94 | 2.1 | 7.14 | 2.5 | 6.9064 | 2.1 |  | 34860 |  | 40780 | 5.6 |  | 6.76 | 1.82 |  | 1.75 | 126.3% | 79.8% | N/A
Trane | Trane | TruComfort XV20i | 10153696 | 4TWV0036A1 | TEM8A0C36V31+TDR | HRCU-A-CB | 10 | 20 | 13 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31800 | 32700 | 0.51 | 2.44 | 2.37 | 4.72 | 3.8186 | 4.04 |  | 15380 | 25600 | 25500 | 1.75 | 2.44 | 3.06 | 2.58 | 3.0741 | 2.44 |  | 16182 |  | 19500 | 2.48 |  | 2.94 | 1.92 |  | 1.95 | 59.63% | 76.47% | N/A
Trane | Trane | TruComfort XV20i | 10153698 | 4TWV0036A1 | TEM8A0C42V41+TDR | HRCU-A-CB | 10 | 20 | 13 | 35600 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31400 | 32700 | 0.52 | 2.32 | 2.41 | 4.68 | 3.9656 | 3.98 |  | 15490 | 25200 | 25400 | 1.82 | 2.32 | 3.2 | 2.5 | 3.1826 | 2.32 |  | 16182 |  | 19400 | 2.58 |  | 3.06 | 1.84 |  | 1.85 | 59.33% | 76.38% | N/A
Trane | Trane | TruComfort XV20i | 10153699 | 4TWV0036A1 | TEM8A0C48V41+TDR | HRCU-A-CB | 10 | 20 | 13 | 35600 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31000 | 31100 | 0.52 | 2.4 | 2.52 | 4.62 | 3.7845 | 3.62 |  | 15600 | 25200 | 25600 | 1.78 | 2.4 | 3.12 | 2.56 | 3.0765 | 2.4 |  | 16382 |  | 19700 | 2.52 |  | 2.98 | 1.90 |  | 1.95 | 63.34% | 76.95% | N/A
Trane | Trane | TruComfort XV20i | 10153700 | 4TWV0036A1 | TEM8A0D48V41+TDR | HRCU-A-CB | 10 | 19.5 | 13 | 35800 | Yes | Centrally Ducted | N/A | N/A | 8400 | 31800 | 33100 | 0.51 | 2.48 | 2.65 | 4.82 | 3.757 | 3.66 |  | 15930 | 25800 | 26100 | 1.77 | 2.48 | 3.08 | 2.64 | 3.0481 | 2.48 |  | 16688 |  | 20000 | 2.52 |  | 2.98 | 1.94 |  | 1.95 | 60.42% | 76.63% | N/A
Trane | Trane | TruComfort XV20i | 10153703 | 4TWV0048A1 | TEM8A0C48V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 47500 | Yes | Centrally Ducted | N/A | N/A | 11900 | 42000 | 33100 | 0.76 | 2.36 | 2.65 | 4.58 | 5.2144 | 3.66 |  | 22410 | 35600 | 36000 | 2.56 | 2.36 | 4.48 | 2.56 | 4.4198 | 2.36 |  | 23504 |  | 27980 | 3.62 |  | 4.28 | 1.90 |  | 1.90 | 84.53% | 77.72% | N/A
Trane | Trane | TruComfort XV20i | 10153704 | 4TWV0048A1 | TEM8A0C60V51+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 12200 | 43500 | 32100 | 0.78 | 2.34 | 2.35 | 4.58 | 5.4467 | 4 |  | 22520 | 36200 | 36600 | 2.61 | 2.34 | 4.57 | 2.52 | 4.5327 | 2.34 |  | 23504 |  | 28100 | 3.68 |  | 4.38 | 1.88 |  | 1.90 | 87.54% | 76.78% | N/A
Trane | Trane | TruComfort XV18 | 10153714 | 4TWV8036A1 | TEM8A0C36V31+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 35200 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31600 | 42600 | 0.51 | 2.4 | 3.37 | 4.72 | 3.8578 | 3.7 |  | 15930 | 25600 | 25800 | 1.8 | 2.4 | 3.16 | 2.6 | 3.1253 | 2.4 |  | 16728 |  | 20040 | 2.56 |  | 3.02 | 1.92 |  | 1.95 | 47.04% | 77.67% | N/A
Trane | Trane | TruComfort XV18 | 10153716 | 4TWV8036A1 | TEM8A0C42V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31600 | 43900 | 0.51 | 2.32 | 3.45 | 4.72 | 3.9908 | 3.72 |  | 15820 | 25600 | 25800 | 1.84 | 2.32 | 3.25 | 2.52 | 3.2331 | 2.32 |  | 16688 |  | 19940 | 2.62 |  | 3.12 | 1.86 |  | 1.85 | 45.42% | 77.29% | N/A
Trane | Trane | TruComfort XV18 | 10153717 | 4TWV8036A1 | TEM8A0C48V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 36200 | Yes | Centrally Ducted | N/A | N/A | 8000 | 31000 | 43600 | 0.52 | 2.42 | 3.38 | 4.5 | 3.7533 | 3.78 |  | 15820 | 25400 | 25700 | 1.78 | 2.42 | 3.11 | 2.6 | 3.0753 | 2.42 |  | 16788 |  | 20040 | 2.52 |  | 3 | 1.96 |  | 1.95 | 45.96% | 77.98% | N/A
Trane | Trane | TruComfort XV18 | 10153718 | 4TWV8036A1 | TEM8A0D48V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31600 | 43200 | 0.51 | 2.46 | 3.43 | 4.76 | 3.7637 | 3.7 |  | 15930 | 25800 | 26100 | 1.78 | 2.46 | 3.11 | 2.62 | 3.0729 | 2.46 |  | 16788 |  | 20100 | 2.52 |  | 3 | 1.96 |  | 1.95 | 46.53% | 77.01% | N/A
Trane | Trane | TruComfort XV18 | 10153721 | 4TWV8037A1 | TEM8A0C36V31+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 35400 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31800 | 31200 | 0.51 | 2.44 | 2.38 | 4.72 | 3.8186 | 3.84 |  | 15380 | 25600 | 25500 | 1.75 | 2.44 | 3.06 | 2.58 | 3.0741 | 2.44 |  | 16182 |  | 19500 | 2.48 |  | 2.94 | 1.92 |  | 1.95 | 62.5% | 76.47% | N/A
Trane | Trane | TruComfort XV18 | 10153722 | 4TWV8037A1 | TEM8A0C42V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 35600 | Yes | Centrally Ducted | N/A | N/A | 8300 | 31400 | 31300 | 0.52 | 2.32 | 2.35 | 4.68 | 3.9656 | 3.9 |  | 15490 | 25200 | 25400 | 1.82 | 2.32 | 3.2 | 2.5 | 3.1826 | 2.32 |  | 16182 |  | 19400 | 2.58 |  | 3.06 | 1.84 |  | 1.85 | 61.98% | 76.38% | N/A
Trane | Trane | TruComfort XV18 | 10153724 | 4TWV8037A1 | TEM8A0C48V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 35600 | Yes | Centrally Ducted | N/A | N/A | 8200 | 31000 | 32300 | 0.52 | 2.4 | 2.31 | 4.62 | 3.7845 | 4.1 |  | 15600 | 25200 | 25600 | 1.78 | 2.4 | 3.12 | 2.56 | 3.0765 | 2.4 |  | 16382 |  | 19700 | 2.52 |  | 2.98 | 1.90 |  | 1.95 | 60.99% | 76.95% | N/A
Trane | Trane | TruComfort XV18 | 10153725 | 4TWV8037A1 | TEM8A0D48V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 35800 | Yes | Centrally Ducted | N/A | N/A | 8400 | 31800 | 31700 | 0.51 | 2.48 | 2.49 | 4.82 | 3.757 | 3.74 |  | 15930 | 25800 | 26100 | 1.77 | 2.48 | 3.08 | 2.64 | 3.0481 | 2.48 |  | 16688 |  | 20000 | 2.52 |  | 2.98 | 1.94 |  | 1.95 | 63.09% | 76.63% | N/A
Trane | Trane | TruComfort XV18 | 10153728 | 4TWV8048A1 | TEM8A0C48V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 46500 | Yes | Centrally Ducted | N/A | N/A | 11900 | 42500 | 43400 | 0.81 | 2.24 | 3.5 | 4.3 | 5.5591 | 3.64 |  | 21310 | 34200 | 35100 | 2.62 | 2.24 | 4.61 | 2.38 | 4.4734 | 2.24 |  | 21900 |  | 26460 | 3.68 |  | 4.4 | 1.74 |  | 1.75 | 60.97% | 75.38% | N/A
Trane | Trane | TruComfort XV18 | 10153729 | 4TWV8048A1 | TEM8A0C60V51+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 47500 | Yes | Centrally Ducted | N/A | N/A | 12100 | 44500 | 44000 | 0.78 | 2.4 | 3.47 | 4.54 | 5.4327 | 3.72 |  | 22630 | 36800 | 37200 | 2.58 | 2.4 | 4.56 | 2.56 | 4.4926 | 2.4 |  | 23744 |  | 28520 | 3.64 |  | 4.36 | 1.92 |  | 1.90 | 64.82% | 76.67% | N/A
Trane | Trane | TruComfort XV18 | 10153734 | 4TWV8049A1 | TEM8A0C48V41+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 47500 | Yes | Centrally Ducted | N/A | N/A | 11900 | 42000 | 32700 | 0.76 | 2.36 | 2.42 | 4.58 | 5.2144 | 3.96 |  | 22410 | 35600 | 36000 | 2.56 | 2.36 | 4.48 | 2.56 | 4.4198 | 2.36 |  | 23504 |  | 27980 | 3.62 |  | 4.28 | 1.90 |  | 1.90 | 85.57% | 77.72% | N/A
Trane | Trane | TruComfort XV18 | 10153735 | 4TWV8049A1 | TEM8A0C60V51+TDR | HRCU-A-CB | 10 | 18 | 12.5 | 47000 | Yes | Centrally Ducted | N/A | N/A | 12200 | 43500 | 31000 | 0.78 | 2.34 | 2.5 | 4.58 | 5.4467 | 3.64 |  | 22520 | 36200 | 36600 | 2.61 | 2.34 | 4.57 | 2.52 | 4.5327 | 2.34 |  | 23504 |  | 28100 | 3.68 |  | 4.38 | 1.88 |  | 1.90 | 90.65% | 76.78% | N/A
Trane | Trane |  | 7151531 | 4TXK2709A10N0AA | 4MXW2709A10N0AA | HRCU-A-CB-O | 10 | 27 | 14.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2200 | 9800 | 11000 | 0.1 | 0.65 | 1.25 | 6.4476 | 4.4186 | 2.579 |  | 1989 | 5800 | 10630.675 | 0.12 | 0.62822 | 1.2595 | 4.8577 | 2.7058 | 2.4736 |  | 1480 |  | 8000 | 0.15 |  | 1.095 | 2.8916 |  | 2.1412 | 72.73% | 75.25% | Integrated | 72W | Heater on below 34°F | N/A |  | z
Trane | Trane |  | 7151533 | 4TXK2712A10NAA | 4MXW2712A10N0AA | HRCU-A-CB-O | 10 | 25 | 13 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2400 | 13000 | 14000 | 0.1 | 0.96 | 1.35 | 7.0337 | 3.9687 | 3.0393 |  | 2200 | 8000 | 8700 | 0.09 | 0.75 | 1.01 | 7.164 | 3.1261 | 2.5245 |  | 2100 |  | 8300 | 0.085 |  | 1.131 | 7.2406 |  | 2.1507 | 59.29% | 95.4% | Integrated | 72W | Heater on below 34°F | N/A
Trane | Trane |  | 7151535 | 4TXK2718A10N0AA | 4MXW2718A10N0AA | HRCU-A-CB-O | 10 | 21 | 12.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3412 | 19000 | 23202 | 0.4 | 1.58 | 2.5 | 2.4999 | 3.5243 | 2.7199 |  | 2729 | 12100 | 19674 | 0.41 | 1.26 | 2.57 | 1.9507 | 2.8144 | 2.2435 |  | 2388 |  | 15400 | 0.42 |  | 2.29 | 1.6663 |  | 1.9709 | 66.37% | 78.28% | Integrated | 160W | Heater on below 34°F | N/A
Trane | Trane |  | 9150121 | 4TXK3809A10NUAA | 4MXW3809A10NUAA | HRCU-A-CB-O | 15 | 38 | 16.5 | 9000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 2300 | 9000 | 13600 | 0.2 | 0.59 | 1.5 | 3.3703 | 4.4706 | 2.6572 |  | 3545 | 5600 | 14610.8 | 0.365 | 0.74596 | 1.7826 | 2.8464 | 2.2001 | 2.4021 |  | 1745 |  | 12210 | 0.28 |  | 1.72 | 1.8265 |  | 2.0805 | 89.78% | 83.57% | Integrated | 72W | Heater on below 34°F | N/A
Trane | Trane |  | 9150123 | 4TXK3812A10NUAA | 4MXW3812A10NUAA | HRCU-A-CB-O | 14 | 30.5 | 15.25 | 12000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 |  | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 |  | 2600 |  | 13304 | 0.22 |  | 1.789 | 3.4636 |  | 2.1794 | 71.14% | 147.8% | Integrated | 72W | Heater on below 34°F | N/A
Trane | Trane |  | 9150125 | 4TXK3818A10NUAA | 4MXW3818A10NUAA | HRCU-A-CB-O | 12 | 24.5 | 13.5 | 18000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 3700 | 18000 | 24400 | 0.35 | 1.5 | 2.5 | 3.0982 | 3.5169 | 2.8604 |  | 3070 | 14200 | 23100 | 0.36 | 1.455 | 3.25 | 2.4992 | 2.8602 | 2.0831 |  | 2388 |  | 20634 | 0.37 |  | 3.3 | 1.8915 |  | 1.8325 | 84.57% | 89.32% | Integrated | 160W | Heater on below 34°F | N/A
Trane | Trane |  | 9150127 | 4TXK3824A10NUAA | 4MXW3824A10NUAA | HRCU-A-CB-O | 12 | 21.5 | 13 | 22000 | Yes | Ductless | Single-zone | Non-ducted indoor units (Mini-splits) | 6800 | 24000 | 32400 | 0.38 | 2 | 3.7 | 5.2444 | 3.5169 | 2.5664 |  | 3396 | 15500 | 26263 | 0.344 | 1.57 | 3.381 | 2.8932 | 2.8934 | 2.2765 |  | 2887 |  | 24233 | 0.33 |  | 3.175 | 2.5639 |  | 2.2368 | 74.79% | 92.27% | Integrated | 160W | Heater on below 34°F | N/A

## Sheet1 (hidden)
Manufacturer | Brand (if applicable) | Model Name | AHRI Certificate No. | Outdoor Unit Model | Indoor Unit Model(s) | AHRI Type | HSPF (Region IV): | SEER | EER (@ 95°F) | Cooling Capacity (Btuh) | ENERGY STAR Certified | Ductless or Centrally Ducted | If Ductless, Multi-zone or Single-zone? | Ductless Indoor Type | Minimum Capacity 47°F | Rated Capacity 47°F | Maximum Capacity 47°F | Input Power at Min. Capcaity 47°F | Rated Input Power 47°F | Input Power at Max. Capacity 47°F | COP at Min. Capacity 47°F | COP at Rated Capacity 47°F | COP at Max. Capacity 47°F | Minimum Capacity 17°F | Rated Capacity 17°F | Maximum Capacity 17°F | Input Power at Min. Capacity 17°F | Input Power at Rated Capacity 17°F | Input Power at Max. Capacity 17°F | COP at Min. Capacity 17°F | COP at Rated Capacity 17°F | COP at Max. Capacity 17°F | Minimum Capacity 5°F | Maximum Capacity 5°F | Input Power at Min. Capacity 5°F | Input Power at Max. Capacity 5°F | COP at Min. Capacity 5°F | COP at Max. Capacity 5°F | Maintenance Capacity (Max 5°F/Max 47°F) | Maintenance Capacity (Max 5°F/Max 17°F) | Integrated or Accessory (provide model #) | Input Power (W) | What determines when heater operates? | Outdoor Dry Bulb (°F) | Minimum Capactity X°F |  | Maximum Capacity X°F | Input Power at Min. Capacity X°F | Input Power at Max. Capacity X°F | COP at Min. Capacity X°F | COP at Max. Capacity X°F | 15 max cap- 5 max cap
American Standard | American Standard |  | 9150124 | 4TXK3812A10NUAA | 4MXW3812A10NUAA | HRCU-A-CB-O | 14 | 30.5 | 15.25 | 12000 | Yes | Ductless | Single-zone | Mini-Splits | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 | 2600 | 13304 | 0.22 | 1.79 | 3.4636 | 2.1782 | 0.71144 | 1.4782 | Integrated | 72W | Heater on below 34°F | N/A | [7 empty] | -4304
Bryant | Bryant | Evolution Series | 9893607 | 280ANV036000 | FE4ANF002L | HRCU-A-CB | 10.5 | 18.5 | 12.5 | 33000 | Yes | Centrally Ducted | N/A | N/A | 14140.4 | 35404 | 35400 | 1.083 | 2.3598 | 2.3598 | 3.8265 | 4.3969 | 4.3964 | 14045 | 33496 | 30600 | 2.0862 | 3.762 | 3.762 | 1.9731 | 2.6094 | 2.6094 | 11310.2 | 33496 | 2.1432 | 3.5796 | 1.5466 | 2.7424 | 0.94621 | 1.0946 | N/A |  |  | N/A | [7 empty] | -2896
Carrier | Carrier |  | 9892658 | 25VNA036A030 | FE4ANF002L | HRCU-A-CB | 10.5 | 18.5 | 12.5 | 33000 | Yes | Centrally Ducted | N/A | N/A | 14140.4 | 35404 | 35400 | 1.083 | 2.3598 | 2.3598 | 3.8265 | 4.3969 | 4.3964 | 14045 | 33496 | 30600 | 2.0862 | 3.762 | 3.762 | 1.9731 | 2.6094 | 2.3838 | 11310.2 | 33496 | 2.1432 | 3.5796 | 1.5466 | 2.7424 | 0.94621 | 1.0946 | N/A |  |  | N/A | [7 empty] | -2896
Carrier | Bryant | Preferred Series | 9854627 | 38MGRQ30D--3 | Non-Ducted Indoor Units | HMSV-A-CB | 10 | 23.8 | 12.5 | 30000 | Yes | Ductless | Multi-zone | Non-Ducted Indoor Units | 6350 | 28000 | 37210 | 0.76 | 2.15 | 3.21 | 2.4487 | 3.8167 | 3.3973 | 5834 | 17400 | 27670 | 0.82 | 1.83 | 3.85 | 2.0851 | 2.7866 | 2.1063 | 5164 | 28220 | 0.86 | 4.05 | 1.7598 | 2.0421 | 0.7584 | 1.0199 | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | [7 empty] | -550
Carrier | Carrier |  | 9854626 | 38MGRQ30D--3 | Non-Ducted Indoor Units | HMSV-A-CB | 10 | 23.8 | 12.5 | 30000 | Yes | Ductless | Multi-zone | Non-Ducted Indoor Units | 6350 | 28000 | 37210 | 0.76 | 2.15 | 3.21 | 2.4487 | 3.8167 | 3.3973 | 5834 | 17400 | 27670 | 0.82 | 1.83 | 3.85 | 2.0851 | 2.7866 | 2.1063 | 5164 | 28220 | 0.86 | 4.05 | 1.7598 | 2.0421 | 0.7584 | 1.0199 | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | -550
GD Midea Air-Conditioning Equipment Co.,Ltd | Willis |  | 9038628 | WSM18MH20S/O | WSM18MH20S/I | HRCU-A-CB-O | 10 | 22 | 13 | 18000 | Yes | Ductless | Single-zone | Mini-Splits | 6093 | 18000 | 19146 | 0.37915 | 1.6695 | 1.5896 | 4.7097 | 3.1599 | 3.5299 | 11100 | 11100 | 12396 | 1.1787 | 1.1787 | 1.5013 | 2.7599 | 2.7599 | 2.4199 | 10460.09 | 12500 | 1.5252 | 2.0816 | 2.0099 | 1.7599 | 0.65288 | 1.0084 | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z | [5 empty] | -104
Trane | Trane |  | 9150123 | 4TXK3812A10NUAA | 4MXW3812A10NUAA | HRCU-A-CB-O | 14 | 30.5 | 15.25 | 12000 | Yes | Ductless | Single-zone | Mini-Splits | 3000 | 12200 | 18700 | 0.25 | 0.94 | 1.6 | 3.5169 | 3.8037 | 3.4253 | 2800 | 8100 | 9000 | 0.23 | 0.74 | 1 | 3.5678 | 3.2079 | 2.6376 | 2600 | 13304 | 0.22 | 1.789 | 3.4636 | 2.1794 | 0.71144 | 1.4782 | Integrated | 72W | Heater on below 34°F | N/A | [7 empty] | -4304

## Delisted (on 1.1.17)
Manufacturer | Brand (if applicable) | AHRI Certificate No. | Outdoor Unit Model | Indoor Unit Model(s) | HSPF (Region IV): | SEER | EER (@ 95°F) | ENERGY STAR Certified | Ductless or Ducted | If Ductless, Multi-zone or Single-zone? | Minimum Capacity 47°F | Rated Capacity 47°F | Maximum Capacity 47°F | Minimum Input Power 47°F | Rated Input Power 47°F | Maximum Input Power 47°F | Minimum COP 47°F | Rated COP 47°F | Maximum COP 47°F | Minimum Capacity 17°F | Rated Capacity 17°F | Maximum Capacity 17°F | Minimum Input Power 17°F | Rated Input Power 17°F | Maximum Input Power 17°F | Minimum COP 17°F | Rated COP 17°F | Maximum COP 17°F | Minimum Capacity 5°F | Maximum Capacity 5°F | Minimum Input Power 5°F | Maximum Input Power 5°F | Minimum COP 5°F | Maximum COP 5°F | Maintenance Capacity (Max 5°F/Max 47°F) | Maintenance Capacity (Max 5°F/Max 17°F) | Integrated or Accessory (provide model #) | Input Power (W) | What determines when heater operates? | Outdoor Dry Bulb (°F) | Minimum Capactity X°F |  | Maximum Capacity X°F | Minimum Input Power X°F | Maximum Input Power X°F | Minimum COP X°F | Maximum COP X°F
LG |  | 7180060 | LMU18CHV | Non-Ducted Indoor Units | 9.7 | 22 | 13 | Yes | Ductless | Multi-zone | 10248 | 22000 | 24000 | 1.155 | 2.04 | 2.42 | 2.6 | 3.2 | 2.9 | 6288 | 13500 | 19161 | 0.924 | 1.63 | 2.03 | 2 | 2.4 | 2.8 | 4950 | 14807 | 0.861 | 1.86 | 1.7 | 2.3 | 61.7% | 77.28% | Optional Accessory #PQSH1200 | 120W | Heater on when ambient temperature is equal and less than 0C - Heater off when ambient temperature is equal and greater than 1C -1C deadband between on and off, heater is always turned on from 0C down if the unit is "on" and in "heat". Heater turns off when outdoor temperature reaches 1C. Heater is not used in "cool" mode. | N/A |  | z
Carrier | Bryant | 9854623 | 38MGRQ24C--3 | Non-Ducted Indoor Units | 9.8 | 23 | 12.5 | Yes | Ductless | Multizone | 6010 | 23000 | 36220 | 0.72 | 1.72 | 3.04 | 2.4463 | 3.919 | 3.4918 | 5721 | 13600 | 25150 | 0.76 | 1.48 | 2.79 | 2.2061 | 2.6931 | 2.6418 | 5556 | 24170 | 0.84 | 3.9 | 1.9385 | 1.8163 | 66.73% | 96.1% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Carrier | Carrier | 9854622 | 38MGRQ24C--3 | Non-Ducted Indoor Units | 9.8 | 23 | 12.5 | Yes | Ductless | Multizone | 6010 | 23000 | 36220 | 0.72 | 1.72 | 3.04 | 2.4463 | 3.919 | 3.4918 | 5721 | 13600 | 25150 | 0.76 | 1.48 | 2.79 | 2.2061 | 2.6931 | 2.6418 | 5556 | 24170 | 0.84 | 3.9 | 1.9385 | 1.8163 | 66.73% | 96.1% | Integrated | 150 | 1.When the unit power on and changed in heating mode,and if the outdoor temperature continue lower than 3C for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.If be on the defrost mode and the outdoor temperature lower 1C for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A |  | z
Lennox Industries, Inc. | Lennox | 8994419 | MLA018S4M-1P | non-ducted indoor units | 9.8 | 21.5 | 12.5 | Yes | Ductless | Multizone | 6020 | 20000 | 28500 | 0.715 | 1.72 | 2.7 | 2.4675 | 3.4078 | 3.0935 | 5743 | 12600 | 26457 | 0.804 | 1.388 | 3.978 | 2.0934 | 2.6604 | 1.9492 | 5516 | 24120 | 0.832 | 3.892 | 1.943 | 1.8163 | 84.63% | 91.17% | Integrated | 150 | 1.When the unit power is on/in heating mode,and if the outdoor temperature drops below 3oC for 30 seconds,after running for 25mins, the base pan heater will be actived for 5 minutes. 2.In defrost mode and the outdoor temperature lower 1oC for 10 seconds the base pan heater will be actived and will be 5 mins delay inactive after defrost. | N/A | 0 | z | 0
Mitsubishi |  | 7451974 | MXZ-2C20NAHZ | Non-Ducted Indoor Units | 9.8 | 17 | 13.5 | Yes | Ductless | Multi-zone | 11400 | 22000 | 25500 | 0.93 | 1.61 | 1.61 | 3.59 | 4 | 4 | 13100 | 13700 | 22000 | 1.5 | 1.45 | 3.07 | 2.83 | 2.77 | 2.1 | 12500 | 22000 | 1.6 | 3.11 | 2.29 | 2.07 | 86.27% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 | z | 19404 | 1.4 | 2.87 | 2.09 | 1.98
Mitsubishi |  | 8996530 | MXZ-2C20NAHZ2 | Non-Ducted Indoor Units | 9.8 | 17 | 13.5 | Yes | Ductless | Multi-zone | 11400 | 22000 | 25500 | 0.93 | 1.61 | 1.61 | 3.59 | 4 | 4 | 13100 | 13700 | 22000 | 1.5 | 1.45 | 3.07 | 2.83 | 2.77 | 2.1 | 12500 | 22000 | 1.6 | 3.11 | 2.29 | 2.07 | 86.27% | 100% | Integrated | 120W @230V | (Starting condition) A) Compressor must be turned on to activate base heater. B) Outside temp is below 32F for 5 minutes. C) Defrost thermistor reads under 30.2F for 5 minutes -All of these must be satisfied to activate. (Stop condition) A) Outside temp is over 46.4F for 5 minutes. B) Defrost thermistor reads over 59F for 5 minutes | -13 | 10000 | z | 19404 | 1.4 | 2.87 | 2.09 | 1.98

## Sheet2
Manufacturer | Brand (if applicable) | Model | AHRI Certificate No. | Outdoor Unit Model | Indoor Unit Model(s) | AHRI Type | HSPF (Region IV): | SEER | EER (@ 95°F) | Cooling Capacity (Btuh) | ENERGY STAR Certified | Ducted or Ductless | If Ductless, "Multizone or Singlezone" | Ductless Indoor type | Capacity (btu/hr) |  |  | Input Power (kW) |  |  | COP |  |  | Capacity (btu/hr) |  |  | Input Power (kW) |  |  | COP |  |  | Capacity (btu/hr) |  | Input Power (kW) |  | COP |  | Integrated or Accessory (provide model #) | Input Power (W) | What determines when heater operates? | Outdoor Dry Bulb (°F) | Capacity (btu/hr) |  | Input Power (kW) |  | COP
[15 empty] | Minimum | Rated | Maximum | Minimum | Rated | Maximum | Minimum | Rated | Maximum | Minimum | Rated | Maximum | Minimum | Rated | Maximum | Minimum | Rated | Maximum | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum |  |  |  |  | Minimum | Maximum | Minimum | Maximum | Minimum | Maximum
Carrier | Carrier;Bryant |  | 10056166 | 38MAQB18R--3 | 40MBCQ18---3 | HRCU-A-CB-O | 10.5 | 20 | 12.5 | 16000 | Yes | Ductless | Singlezone | Non-ducted indoor units (Mini-splits) | 4700 | 18000 | 24630 | 0.27 | 1.53 | 2.53 | 5.1 | 3.43 | 2.85 | 3750 | 12000 | 20590 | 0.25 | 1.38 | 2.93 | 4.4 | 2.55 | 2.06 | 2660 | 19010 | 0.23 | 3.18 | 3.39 | 1.75 | Integrated | 3 | The heater will operated based on temperature, it will activate at 37F outdoor ambient and below. | 0 | 0 | 0 | 0 | 0 | 0 | 0