## Revision Tracker
This tab will be hidden or deleted for final deliverable.
Changes to Occur | Changes that occurred
· High level comments | Added fuel type to measure characterization section
o The order in which the information is listed and how they are referred to should be the same across all the documents with the rare acceptation of a few that can’t easily do that. For example the information should be listed: | ADDED ICS 1, 2 to index.
§ Base Cost Factor (FIXED) | Added measure characterization section to ICS1 and 2 REAMEs
§ Regional Specific Costs (FIXED) | Reformatted ICS1 and 2 to match ICS3
§ Regional Adjustment Factors (FIXED) | Added CPI and PPI links to intro tab
§ Titles should be the same across all (FIXED) | Indexed all measure by sector (commercial and residential) followed by alphabetical ordering.
o ? did we do on demand tank less WH (condensing?) not listed. (FIXED - ADDED WORDING TO INDICATE "STANDARD" AND "CONDENSING" ARE INCLUDED) | Added vintage of data in both README and Results tabs as well as the in the measure index
o For residential in particular, need to verify that labor hours included correspond with what is listed “yes or no”–found a few that didn’t seem to match up. (KL: I think I fixed all these. ) | Drop Down options have now been highlighted blue
o Commercial | Tried to add index by region per Denise's request. This is possible, but made the index section very complicated. Another option would be to create a "master" workbook for each region, although I think that would make matters more complicated.
§ Air Compressors—has 2 market 5 and no market 6 (FIXED) | Cleaned README Tabs (removed references to other workbook tabs)
§ Air Source Heat Pump—BCG is at the end on this one not at the beginning as most of the others (FIXED) | Added hyperlinks to regional results for each measure
§ Anti-Sweat Door Heater Controls—you have a column “outliners removed” There should be a note at the top about what this really is. (FIXED - removed middle column and removed "outliers removed" from column label) | Added dedicated index sheets for Commercial and Residential
§ Chillers—Market 1 take out code and uses same names. Follow other format. Regional adjustment put at end. (FIXED) | Arranged introduction tab to flow vertically rather than horizontally
§ Steam Traps—BCF put first. Reference drop down box maybe in () so folks see it. Same with other analysis types where they switch. (FIXED) | OCH: Added content to ICS1 and ICS2 measure characterization tables on README tabs
§ Unitary Air conditioning --2 #5 and no #6 and put BCF up front. (FIXED-KL) | OCH: Added Yes/No for 'Incremental Labor Cost' question on RESULTS tabs
o Residential | ADDED ICS4 DATA
§ Air Sealing—says labor hours 12 yet says “ no” labor included on chart (CAN"T OPEN THE ORIGINAL FILE - CORRUPTED) KL: changed "No" to "Yes - full labor cost" on Characterization chart. | COMPLETED MEASURE CHARACTERIZATION TABLES FOR ICS2 AND 1
§ ASHP –adjust order (FIXED) | ADDED NAVIGANT CONTACT INFORMATION
§ Boilers—label BCF (FIXED) | ADDED NEEP CONTACT INFORMATION
§ CHW –confirm-- seams that full material and labor are included but only says material included. Is the BCF added to labor? (FIXED ms) THERE'S A LABOR INCREMENT BETWEEN BASELINE AND EFFICIENCT BUT IT'S CONSTANT - ADDED CLARIFYING NOTE | ADDED A COST VOLATILITY TAB WITH TABLES FOR PHASES 2 THROUGH 4.
§ Furnaces—in title should say “including EMC” (FIXED) | ADDED LABOR DATA (CELL C8 in ICS4 MEASURE RESULTS TABS AND TO README TABS)
§ IHWH—Looks like labor costs are included but the charts says “no” labor costs. (FIXED-ms) Full costs include Labor THERE'S NO INCREMENTAL LABOR. | ADDED PUBLISHING DATE FOR PHASE I AND III MEASURES (ON READ ME TAB)
§ Insulation –labor costs look like they are included but the chart says “no” labor costs. (CHANGED WORDING OF LABOR QUESTION)
§ Minisplit—need index at the end. Does this include labor? (FIXED-ms) LABOR IS A CONSTANT REGHARDLESS OF SIZE OR EFFICIENCY
§ ODWH-indicate (drop down box) (FIXED)
§ Ventilation fans—depends on the scenario—if so should specific. (FIXED-ms) DESCRIBED SCENARIOS ON RESULTS AND README TABS -ADDED FULL COST TABLES NOT PREVIOUSLY INCLUDED.

## Introduction
`
Introduction
This workbook presents the results of the four phases of incremental cost research commissioned by the Evaluation, Measurement and Verification (EM&V) Forum Research Subcommittee (Subcommittee) to investigate and update incremental costs for a number of common prescriptive measures employed in energy efficiency programs.
The study’s overall goal was to determine baseline and efficient measure costs for a series of energy efficiency measures of interest to the Subcommittee as well as the incremental costs of moving from baseline to efficient measures. The incremental cost is relevant for new construction and replace on burnout scenarios. The full cost was also calculated for measures that are used in retrofit scenarios.
Indices of measure level results are available in the Commercial Measure Index tab or the Residential Measure Index tab. Measure level results and background can be viewed by clicking on the README link and for a summary of the results refer to the Results link.
Complete measure level workbooks, including analysis tabs which users may download and customize or update cost data are available for review (at http://www.neep.org/resources/reports).
Key Definitions Retrofit (RET) – replacing a working system with a new technology or installing a technology that was not there before
Replace-on-burnout (ROB) – replacing a technology at the end of its useful life
New construction (NEW or NC) – installing a technology in a new construction or major renovation project.
Incremental measure cost = (efficient material cost + efficient labor cost) - (baseline material cost +baseline labor costs)
Regional Differences The nine states and District of Columbia involved in the ICS covered six markets identified by the project team, using data from R.S. Means. The study included New England, New York, and the Mid-Atlantic States of Maryland and Delaware, as well as the District of Columbia. The Figure below shows the six markets identified.
Using the Master Summary Workbook Measure level results are available by following the hyperlink provided in this Commercial Measure Index and Residential Measure Index tabs.
Results are presented in alphabetical order by sector, commercial followed by residential. Commercial measure tabs are colored green, while residential measure tabs are colored orange.
Data vintage is provided in both the README and RESULTS worksheets for each measure. Data vintages vary among the measures and it is the responsibility of the USER to apply producer price indices (PPIs) or consumer price indices (CPI) appropriately in order to achieve a more current estimation of incremental costs.
CPI Indices are available at: http://www.bls.gov/cpi/
PPI Indices are available at: http://www.bls.gov/ppi/
Please note, certain measures, such as Steam Traps have the ability to toggle analysis options. When a measure has this option, the cell will be highlighted in BLUE.
Contact Information:
NEEP
Elizabeth Titus
Office Phone: (781) 860-9177 ext. 111
Email: etitus@neep.org
Navigant
Keith Levenson, Managing Consultant
Office Phone: (802) 526-5109
Email: keith.levenson@navigant.com
Incremental Cost Study Summary Measure Workbooks

## Commercial Measure Index
Commercial Measure Level Results | Regional Results
Air Compressors (2014)
Air Compressors - README
Air Compressors - Results | 1 | 2 | 3 | 4 | 5 | 6
Air Source Heat Pumps (2013)
Air Source Heat Pump - README
Air Source Heat Pump - Results | 1 | 2 | 3 | 4 | 5 | 6
Anti-Sweat Door Heater Controls (2014)
Anti-Sweat Door Heater Controls - README
Anti-Sweat Door Heater Controls - Results | 1 | 2 | 3 | 4 | 5 | 6
Chillers (2012)
Chillers - README
Chillers - Results | 1 | 2 | 3 | 4 | 5 | 6
Commercial Boilers (2011)
Commercial Boilers - README
Commercial Boilers - Results | 1 | 2 | 3 | 4 | 5 | 6
Commercial Convection Oven (2014)
Commercial Convection Oven - README
Commercial Convection Oven - Results | 1 | 2 | 3 | 4 | 5 | 6
Commercial Fryers (2014)
Commercial Fryers - README
Commercial Fryers - Results | 1 | 2 | 3 | 4 | 5 | 6
Commercial Infrared Heater (2014)
Commercial Infrared Heater - README
Commercial Infrared Heater - Results | 1 | 2 | 3 | 4 | 5 | 6
Commercial Lighting Controls (2011)
Commercial Lighting Controls - README
Commercial Lighting Controls - Results | 1 | 2 | 3 | 4 | 5 | 6
Dual Enthalpy Economizers (2012)
Dual Enthalpy Economizers - README
Dual Enthalpy Economizers - Results | 1 | 2 | 3 | 4 | 5 | 6
Evaporative Fan Controls (2014)
Evaporative Fan Controls - README
Evaporative Fan Controls - Results | 1 | 2 | 3 | 4 | 5 | 6
LED Refrigeration Lighting (2013)
LED Refrigeration Lighting - README
LED Refrigeration Lighting - Results | 1 | 2 | 3 | 4 | 5 | 6
Steam Traps (2013)
Steam Traps - README
Steam Traps - Results | 1 | 2 | 3 | 4 | 5 | 6
Unitary Air Conditioning (2013)
Unitary Air Conditioning - README
Unitary Air Conditioning - Results | 1 | 2 | 3 | 4 | 5 | 6
Variable Frequency Drives (2012)
Variable Frequency Drives - README
Variable Frequency Drives - Results | 1 | 2 | 3 | 4 | 5 | 6

## Residential Measure Index
Residential Measure Level Results | Regional Results
Air Sealing (2011)
Air Sealing - README
Air Sealing - Results | 1 | 2 | 3 | 4 | 5 | 6
Air Source Heat Pumps (2011)
Air Source Heat Pumps - README
Air Source Heat Pumps - Results | 1 | 2 | 3 | 4 | 5 | 6
Boilers (2011)
Boilers - README
Boilers - Results | 1 | 2 | 3 | 4 | 5 | 6
Central Air Conditioners (2011)
Central Air Conditioners - README
Central Air Conditioners - Results | 1 | 2 | 3 | 4 | 5 | 6
Combination Heat Hot Water (2012)
Combination Heat Hot Water - README
Combination Heat Hot Water - Results | 1 | 2 | 3 | 4 | 5 | 6
Furnaces (2011)
Furnaces - README
Furnaces - Results | 1 | 2 | 3 | 4 | 5 | 6
Heat Pump Water Heater (2013)
Heat Pump Water Heater - README
Heat Pump Water Heater - Results | 1 | 2 | 3 | 4 | 5 | 6
Indirect Hot Water Heater (2011)
Indirect Hot Water Heater - README
Indirect Hot Water Heater - Results | 1 | 2 | 3 | 4 | 5 | 6
Insulation (2012)
Insulation - README
Insulation - Results | 1 | 2 | 3 | 4 | 5 | 6
Minisplit (2012)
Minisplit - README
Minisplit - Results | 1 | 2 | 3 | 4 | 5 | 6
On Demand Water Heater Standard & Condensing (2012)
On Demand Water Heater - README
On Demand Water Heater - Results | 1 | 2 | 3 | 4 | 5 | 6
Ventilation Fans (2012)
Ventilation Fans - README
Ventilation Fans - Results | 1 | 2 | 3 | 4 | 5 | 6

## Cost Volatility
Incremental Cost Volatility
KEY:
Stable - No expected Market, Technology or Standards changes. Update for annual inflation only next 3-5 years.
Medium - Market conditions, Technology or Codes/Standards changes possible 1-3 years.
Volatile - Changes in Market conditions, Technology or Codes/Standards will affect measure costs in 1-3 years.
ICS Phase Two
Measure | Expected Cost Volatility | Comments
Combination Heat/Hot Water Units | Volatile | Expect increased penetration. Combination units are becoming an increasingly cost-effective option compared to conventional boiler/water heater systems for many homeowners.
Condensing On Demand Water Heaters | Medium | Surveyed products already meet 2015 standard.
Attic Insulation-Cellulose | Stable | No major changes expected in the next 3-5 years.
Residential Central Air Conditioning | Medium | Standards change may bring down manufacturing costs through increased scale.
Prescriptive Chillers | Medium
Dual Enthalpy Economizers | Medium
Variable Frequency Drives (VFDs) | Medium
Residential Ductless Mini-Splits | Volatile | Expect increased penetration of heating/cooling units in cold climates and multi-room units.
ENERGY STAR Ventilation Fans | Medium | No updated ENERGY STAR specs currently in development. The most recent ENERGY STAR spec, version 3.2, was updated April 2012.
ICS Phase Three
Measure | Expected Cost Volatility | Comments
Air Source Heat Pumps | Stable | ASHPs are on the current DOE Rulemaking Docket: Commercial Air Conditioners and Heat Pumps, Docket No. EERE-2013-BT-STD-0007. Early stage of process – no rule-making date established.
LED Refrigeration Case Lighting | Volatile | Robust technology gaining market share for retrofit. Technology is baseline for New Construction but could change as LED efficacy increases.
Unitary AC | Medium | Federal standards are scheduled to be amended in 2014 with an effective date in 2017.
Steam Traps | Stable | Established Steam Trap technologies should remain the same for foreseeable future. No breakthrough technologies are known that would disrupt the market.
Heat Pump Water Heaters | Stable | Standards changed recently (2009) to all but eliminate electric resistance Domestic Hot Water (DHW. ENERGY STAR no longer qualifies storage electric resistance water heaters.
ICS Phase Four
Measure | Expected Cost Volatility | Comments
VFD and Load/No Load Air Compressors | Stable | Established technology in a mature market
Commercial Kitchen Fryers | Stable | Mature market.
Commercial Kitchen Convection Ovens | Stable | Energy Star standards were recently enacted, but most manufacturers are able to meet the standards at little added cost. Many baseline models are being discontinued.
Refrigeration Anti-Sweat Door Heater Controls | Medium | Trend is toward microprocessor-based refrigeration management systems, but sensors for simple controls are getting less expensive.
Refrigeration Evaporator Fan Controls | Medium | Trend is toward microprocessor-based refrigeration management systems.
Commercial Infrared Heaters | Medium | Small market. DSM programs have low uptake
For ICS Phases 2 through 4, Navigant produced an estimate of price volatility for each measure investigated. These estimates are presented to help Program Administrators to estimate how quickly the accuracy of the incremental cost results will erode over time.

## Air Compressors - README
VFD Air Compressors
Return to Measure Index
Measure Characterization:
| Efficient Measure Description | VFD-equipped new Air Compressor
| Baseline Description | Air Compressor without VFD, Load/No-Load controls or Variable Displacement controls
| Measure Scenario(s) | RET, NC, ROB
| Baseline Efficiency Levels | N/A
| Measure Specifications | Single Compressor Systems Only
Massave: Maximum Discharge Pressure: 145 PSI
Massave: Minimum storage requirement is 2 gallons per acfm of compressor capacity
Efficiency Vermont: Rotary Screw or Rotary Vane only
Massave: Oil-flooded rotary screw only
Massave: must have a minimum 3% impedance series reactor in AC power input
| Sizes | Generally 10 to 100 HP Massave: 15 to 75 HP
Distinguishing Features
Single Compressor Systems Only
| Installation Scenarios | New VFD Air Compressor installed in New Construction, or replacement compressor in an existing single air compressor system
| Sources | Mass Save, Baltimore Gas & Electric, Con Edison, Efficiency Vermont, Energize CT, DC Sustainable Energy Utility, Cape Light Compact , Liberty Utilities, and PSEG Long Island
| Incremental Labor Cost | No - Labor cost is the same for efficient and baseline equipment.
| Cost Basis | Incremental
| Fuel Type | Electric
| Data Vintage | 2014
Incremental Cost Study Phase Four
Published: May, 2015
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the baseline (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = efficient measure cost (material and labor) - baseline (material and labor)
Qualifying Measure: A qualifying measure is defined as the energy efficient alternative to the baseline equipment. In this case, there were two Qualifying measures that were investigated: Air Compressors factory-equipped with a Variable Frequency Drive or Air Compressors equipped with Load/No-Load controls.
Baseline: The baseline equipment is defined as the standard equipment that would have been installed without the utility EE activity. The baseline equipment in this instance is an air compressor with neither a Variable Frequency Drive nor Load/No-Load controls. Most commonly this would be a modulating air compressor.
Summary of Results Tab
The 'Summary of Results' tab presents the incremental cost for these two types of Air Compressors. Total installed incremental costs are presented in seven categories allowing NEEP constituents to choose the market that best represents their service territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into six unique regions (seven including a Base Cost Factor category).
Two tables of results are presented. Table 1 presents the incremental cost of Load/No Load Air Compressors vs. baseline air compressors in the 2nd column, and VFD Air Compressors vs. baseline in the 3rd column. These results are presented for 5 horsepower levels from 15 to 75 horsepower. Table 2 presents the incremental cost of VFD Air Compressors vs. the aggregated cost of baseline and Load/No Load Air Compressors for the same five horsepower levels as Table 1. The data is presented this way due to a finding of this study that, especially at lower horsepower, the cost of baseline (modulating) air compressors is nearly the same as Load/No Load Air Compressors. This finding is discussed in more detail in the Results section, below. The data in Table 2 is presented as the incremental cost per machine in column 2, and the incremental cost per horsepower in column 3.
Alternative Data Integration
In addition to Program data provided by Program Administrators, additional cost data was obtained from the following sources:
- Installer / Sales Representative Interviews: Navigant completed four in-depth interviews with sales representatives at various vendors, including two manufacturers, to understand the typical installation practices and associated costs for installing or replacing Air Compressors. Interviewees provided qualitative information about the various Air Compressor technologies, ancillary material requirements, and installation scenarios, as well as quantitative data points on equipment, ancillary material, and labor costs. However, not all interviewees provided quantitative data for each of the three equipment types. Where necessary, the labor hour estimates from interviews were combined with prevailing labor rates from RS Means to generate labor cost estimates for other data points that were not broken out into labor and materials.
- Internet-derived equipment costs: Internet searches resulted in information about the variety of qualifying models available, but no useful equipment costs were found from these internet sites. No internet derived data points were used to generate the final incremental costs for this measure.
Data Analysis Tab
Raw Data
In addition to the above data sources, over 250 cost points for equipment, ancillary material, and labor costs were collected from program tracking data and program invoices. Data from all sources is listed in the Raw Data section.
Formatted Data
Primary cost data was collected from in-depth interviews and program tracking data across multiple states including MA, RI, NH, VT, and MD. Due to the inherent differences in cost from one region to another, (i.e. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent base cost factor (BCF) data using RSMeans CCI. Table 1 provides a regional break down of NEEP. For example, if the material cost provided from a contractor in New York Metro for an Air Compressor were $1,000, then the BCF cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $1,000 / 1.03
BCF = $968.29
The same method was used to adjust all labor costs.
Material Analysis
The analysis identified and removed any potential outlier data points by calculating the regression residuals of each data point. It was observed that Air Compressor Material Cost increased with increasing horsepower rating, and that Material Costs are highly correlated to Air Compressor technology type (i.e., VFD-equipped, Load/No-Load-equipped, etc.). Outliers were eliminated in each case based on the absolute value of the residuals from the best fit trend line of Material Cost vs. horsepower plot. This process is shown on the "Outliers" tab.
A linear regression was used to develop the material cost at various horsepower ratings for each technology type. The regression analysis was performed using data from the entire range of Air Compressor horsepower ratings for each technology; however, the regression results were used to generate cost estimates only in the horsepower range prescriptively rebated by most program administrators (15 - 75 HP). Labor Analysis
Contractor and sales representative interviews identified an incremental difference in the time to install Air Compressors of each technology type for each greater horsepower rating, when compared to the time to install Air Compressors of the lesser horsepower rating. This was verified by data found in program invoice data containing labor hours and costs. Installation times were also taken from one of the four in-depth interviews. Finally, the labor rate was calculated with a weighted average of all contractor labor rates ($/HR) collected from program invoice data and one of the four in-depth interviews.
Results and Findings
Results are presented for several horsepower ratings (15, 30, 45, 60, and 75 HP) at the BCF level on the "Summary of Results" tab, Table 1. Scatterplots of the data for different horsepower ranges are presented on the "15-20HP," "15-75HP" and "VFDs-75HP+" tabs. We were not able to obtain any Load/No-Load Air Compressor cost data in the highest range of the horsepower ratings, so only VFD Air Compressor cost data is presented in the scatterplot on the "VFDs-75HP+" tab.
The scatterplot on the "15-20HP" tab shows that for this segment of the market, Load / No Load air compressors and constant speed air compressors have nearly the same price trend line. This confirms a finding from the installer interview portion of the study that Load / No Load air compressors are now considered baseline equipment since they offer measureable efficiency gains at little added cost. For this reason, the incremental cost results are for VFD air compressors vs. Load / No Load and modulating air compressors combined as the baseline. The full incremental cost and cost per horsepower are calculated for each horsepower level.

## Air Compressors - Results
Commercial VFD and Load/No-Load Air Compressors
Data Vintage | 2014
Does this measure have incremental labor cost (Yes/No)? | NO
Return to Measure Index
Base Cost Factor Results:
Size Category (hp) | Base Cost Factor
| VFD ($) | VFD ($/HP)
15 | 5643.6647 | 376.2443
30 | 4802.1042 | 160.0701 |  |  |  | Massave: 15 to 75 HP
45 | 3960.5438 | 88.0121
60 | 3118.9833 | 51.9831
75 | 2277.4228 | 30.3656
Results by Market:
Size Category (hp) | Market 1 Northern New England Incremental Cost
| VFD ($) | VFD ($/HP)
15 | 5507.2762 | 367.1517
30 | 4686.0534 | 156.2018
45 | 3864.8306 | 85.8851
60 | 3043.6078 | 50.7268
75 | 2222.3851 | 29.6318
Size Category (hp) | Market 2 Central/Southern New England Incremental Cost
| VFD ($) | VFD ($/HP)
15 | 5551.1086 | 370.0739
30 | 4723.3497 | 157.445
45 | 3895.5908 | 86.5687
60 | 3067.832 | 51.1305
75 | 2240.0731 | 29.8676
Size Category (hp) | Market 3 New England City Incremental Cost
| VFD ($) | VFD ($/HP)
15 | 5688.814 | 379.2543
30 | 4840.5211 | 161.3507
45 | 3992.2281 | 88.7162
60 | 3143.9351 | 52.3989
75 | 2295.6422 | 30.6086
Size Category (hp) | Market 4 NY Metro Incremental Cost
| VFD ($) | VFD ($/HP)
15 | 5800.2764 | 386.6851
30 | 4935.3626 | 164.5121
45 | 4070.4488 | 90.4544
60 | 3205.5351 | 53.4256
75 | 2340.6213 | 31.2083
Size Category (hp) | Market 5 NY Upstate Incremental Cost
| VFD ($) | VFD ($/HP)
15 | 5567.4752 | 371.165
30 | 4737.2758 | 157.9092
45 | 3907.0764 | 86.8239
60 | 3076.877 | 51.2813
75 | 2246.6776 | 29.9557
Size Category (hp) | Market 6 NY Upstate Incremental Cost
| VFD ($) | VFD ($/HP)
15 | 5602.7481 | 373.5165
30 | 4767.289 | 158.9096
45 | 3931.8298 | 87.374
60 | 3096.3706 | 51.6062
75 | 2260.9115 | 30.1455
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.97583 | 0.81533 | 0.90417
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9836 | 1.1632 | 1.0628
New England City | 3 | Boston, Providence | 1.008 | 1.2795 | 1.1275
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT | 1.0278 | 1.5593 | 1.262
NY Upstate | 5 | Buffalo, Rochester etc. | 0.9865 | 1.0135 | 0.99825
Mid-Atlantic | 6 | MD, DE, DC | 0.99275 | 0.88775 | 0.94625
National Average | - | - | 1 | 1 | 1
Summary of incremental cost data analysis for VFD and Load / No Load Air Compressors, including both materials and labor. Regional adjustment factors are applied to national average incremental costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category .

## Air Source Heat Pump - README
Commercial Air Source Heat Pump
Return to Measure Index
Measure Characterization:
|  | Efficient Measure Description | Commercial Air Source Heat Pump
|  | Baseline Description | Standard Efficient Air Source Heat Pump
|  | Measure Scenario(s) | ROB, NC
|  | Baseline Efficiency Levels and Specifications | IECC IECC 2009 and/or jurisdiction-specific. (IECC 2012 did not make any substantial change to the baseline requirement.) Baseline efficiencies vary by size.
|  | Measure Specifications | High efficiency Split or Packaged Air Source Heat Pumps meeting CEE Tier requirements. CEE Tier 1 & Tier 2 (see CEE Criteria Tab). Tier 2 for units with capacities larger than 65,000 Btu/h are based on the Cool Choice program. DX or VRF, Ducted only, non-ducted (e.g., mini-splits) excluded.
|  | Sizes | <5.4 tons
5.4 - 11.25 tons
11.25 - 20 tons
20 - 63 tons
|  | Distinguishing Features | With or without electric resistance backup heating versus all other types of backup heat
|  | Installation Scenarios | Split System or Single Package
|  | Sources | NY TRM, Efficiency Maine TRM, Massachusetts TRM
|  | Incremental Labor Cost | No - Labor cost is the same for efficient and baseline equipment.
|  | Cost Basis | Incremental
|  | Fuel Type | Electric
|  | Data Vintage | 2013
0.75
Incremental Cost Study Phase Three
Published: May, 2014
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the standard (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = high efficient measure material cost - base case material cost
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as an air source heat pump with SEER in line with the CEE Criteria (see CEE Criteria Tab).
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity. The baseline equipment in this instance is an air source heat pump with SEER in line with the current minimum Federal standard.
WORKBOOK ELEMENTS
Summary of Result
The results tab presents the incremental cost for the commercial air source heat pumps. Incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis
Raw Data
A total of 38 cost points were collected through contractor interviews and invoices provided by NEEP constituents. Of the total number of cost points, 22 were commercial installations, while 16 were residential split ASHP systems. Only material costs were used from residential data. There are no differences in a commercial versus residential split ASHP systems in the sizes presented here. The residential data, however, does not include economizer costs, which is found in some installation scenarios.
The data collected from program administrator invoices points to smaller sized units being incentivized under their prescriptive programs. As such, Navigant developed incremental cost for air source heat pump units 3, 4, and 5 tons. Our contractor interview confirmed that not many units over 20 tons are being installed. Furthermore, Itron, in their February 28, 2014 Measure Cost Study for the California Public Utilities Commission notes that manufacturers have discontinued manufacturing packaged heat pump units over 20 tons.
Formatted Data
Primary cost data was collected from contractors across four states (MD, MA, RI, and NY). Due to the inherent differences in cost from one region to another, Navigant adjusted all material and labor cost points to represent Base Cost Factor (BCF) data using RSMeans CCI. For example, if the cost provided from a contractor in Pennsylvania for an air source heat pump was $5000, than the NRS cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $5000 / 0.99
BCF = $5050
The same method was used to adjust all labor cost.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data. Any assumed values were based on model information and further research.
A linear regression was used to develop the material cost for the measure. A regression was done for air source heat pump units up to 5 tons in size.
The regression analysis resulted in one incremental cost per size category. Although the actual material costs vary within a size category, the typical incremental costs does not.
Labor Analysis
Navigant conducted contractor interviews to identify no incremental difference in the time to install efficient versus base scenario equipment. In general, efficient equipment took just as much time to install as compared with base equipment. Per the contractor interview, labor required to install a baseline unit and an efficient unit is the same.
Results
Navigant defined the unit sizes based on program records provided by program administrator. This data shows too few units greater than 5 tons to complete a robust analysis for air source heat pump systems greater than 5 tons.

## Air Source Heat Pump - Results
Commercial Air Source Heat Pump
Data Vintage | 2013
Does this measure have incremental labor cost (Yes/No)? | No
Return to Measure Index
Base Cost Factor Results:
Size Category (Tons) | Base Cost Factor -BCF ($/Unit)
| CEE Tier 1 | CEE Tier 2
3 | 467.9896 | 935.9791
4 | 467.9896 | 935.9791
5 | 467.9896 | 935.9791
Results by Market:
Size Category (Tons) | Market 1 Northern New England Incremental Cost ($/Unit)
| CEE Tier 1 | CEE Tier 2
3 | 456.6798 | 913.3596
4 | 456.6798 | 913.3596
5 | 456.6798 | 913.3596
Size Category (Tons) | Market 2 Central/Southern New England Incremental Cost ($/Unit)
| CEE Tier 1 | CEE Tier 2
3 | 460.3145 | 920.6291
4 | 460.3145 | 920.6291
5 | 460.3145 | 920.6291
Size Category (Tons) | Market 3 New England City Incremental Cost ($/Unit)
| CEE Tier 1 | CEE Tier 2
3 | 471.7335 | 943.467
4 | 471.7335 | 943.467
5 | 471.7335 | 943.467
Size Category (Tons) | Market 4 NY Metro Incremental Cost ($/Unit)
| CEE Tier 1 | CEE Tier 2
3 | 480.9763 | 961.9525
4 | 480.9763 | 961.9525
5 | 480.9763 | 961.9525
Size Category (Tons) | Market 5 NY Upstate Incremental Cost ($/Unit)
| CEE Tier 1 | CEE Tier 2
3 | 461.6717 | 923.3434
4 | 461.6717 | 923.3434
5 | 461.6717 | 923.3434
Size Category (Tons) | Market 6 Mid-Atlantic Cost ($/Unit)
| CEE Tier 1 | CEE Tier 2
3 | 464.5966 | 929.1933
4 | 464.5966 | 929.1933
5 | 464.5966 | 929.1933
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.97583 | 0.81533 | 0.90417
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9836 | 1.1632 | 1.0628
New England City | 3 | Boston, Providence | 1.008 | 1.2795 | 1.1275
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT, | 1.0278 | 1.5593 | 1.262
NY Upstate | 5 | Buffalo, Rochester etc. | 0.9865 | 1.0135 | 0.99825
Mid-Atlantic | 6 | MD, DE, DC | 0.99275 | 0.88775 | 0.94625
National Average | - | - | 1 | 1 | 1
Summary of incremental cost data analysis for commercial Air Source Heat Pump. Regional adjustment factors are applied to national average incremental costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category.

## Anti-Sweat Door - README
Anti-Sweat Door Heater Controls
Return to Measure Index
Measure Characterization:
| Efficient Measure Description | Anti-Sweat Door Heater Controls installed on refrigerated cooler/freezer doors will turn off door heaters when the relative humidity of the ambient indoor air falls below the point where condensation will occur when the door is opened.
| Baseline Description | Reach-in Cooler or Freezer Doors with uncontrolled Anti-Sweat Door Heaters
| Measure Scenario(s) | RET only (This equipment is baseline in new construction per IECC 2015)
| Baseline Efficiency Levels and Specifications | Continuous, Uncontrolled Door Heater Operation
| Measure Description and Specifications | Anti-Sweat Door Heater Controls allow for 'on/off'* operation of heaters installed on refrigerated cooler/freezer doors. Without control these heaters are assumed to operate continuously for 8760 annual hours. Controlling anti-sweat door heaters also reduces building and cooler/freezer cooling load. 'Deemed savings from reduced heater run-time and reduced building and display case cooling load. Based on applicable TRMs, annual runtime is typically reduced to approximately 4,700 hrs for Freezers and 2,270 hrs for Coolers. Depending on control strategy, climate, and setting parameters, runtime may be reduced significantly further. Currently only Groton Utilities offers incentives for these additional energy savings. *Pulse-Width Modulation may be used by certain controllers to reduce thermal stress on heating elements.
| Sizes | Per Door (Standard Unit), Per Circuit (ME), Per Linear Ft. Case (NGRID MA/RI), Per kWh Saved (Groton Utilities, CT)
| Distinguishing Features and Incentive Approach | Two control approaches: (1) Door heaters are controlled based on the relative humidity of the air outside of the controlled display case. (2) Door heaters are controlled based on sensors that measure door glass conductivity, and activate heaters when condensation appears and conductivity drops below a set level. Incentive Approaches: VT (EVT): Must be a humidity based control. [1] NH (PSNH, Unitil, Liberty): No Prescriptive Incentive Offered; Custom only. ME (Efficiency Maine): No Control Approach Specified, Incentive offered per circuit. MA (National Grid Only): No Control Approach Specified RI (National Grid Only): No Control Approach Specified CT (Groton Utilities): No Control Approach Specified, Prescriptive incentive offered at $0.14 per kWh saved MD (BGE): Humidity based control, other strategies may qualify. [2] D.C. (D.C. SEU): Must be Humidity Based [3]
| Installation Scenarios | Typical Building Type: Grocery Store, Convenience Store (1) Central or decentralized control via indoor (exterior of cooler/freezer) relative humidity sensor(s). (2) Heaters controlled by door conductivity sensors.
| Sources | [1] https://www.efficiencyvermont.com/For-My-Business/Ways-To-Save-and-Rebates/Refrigeration-Controls/single-item/index/door-frame-heater-controls
[2] https://www.bgesmartenergy.com/sites/bge/files/BGE_IC_Application_Kitchen_Refrig_Incentives.pdf
[3] https://www.dcseu.com/docs/business/techspec/DCSEU-TECHSPEC-Refrigeration.pdf
NY TRM, Efficiency Maine TRM, Massachusetts TRM
| Incremental Labor Cost | Yes - Full labor cost
| Cost Basis | Full
| Fuel Type | Electric
| Data Vintage | 2014
Program data
Interview
Internet search
Incremental Cost Study Phase Four
Published: May, 2015
Incremental Cost Methodology
Incremental cost research on Anti-Sweat Door Heater Controls (ASDHC) was aimed at estimating the total installed cost since the baseline for this measure is uncontrolled door heaters at zero cost.
Qualifying Measure: A qualifying measure is defined as the energy-efficient alternative to the standard, or baseline equipment option. In this case, it is defined as a door heater control installed to turn off refrigerated cooler/freezer door heaters when the surface temperature of the cooler or freezer door is warm enough to prevent condensation when the door is opened.
Baseline: The baseline condition is defined as reach-in cooler or freezer doors with uncontrolled anti-sweat door heaters operating continuously.
Measure Characteristics
Cooler Door Heater Controls - Anti-sweat door heater controls will turn off (or modulate the pulse width* of) the anti-sweat door heaters on a given circuit when the heaters are not required to prevent condensation when the door is opened. The control can be activated either by a conductivity sensor when no condensation is detected, or by a humidity or dewpoint sensor when the dewpoint temperature of the ambient air falls below the door surface temperature.
Freezer Door Heater Controls - Anti-sweat Door Heaters on Freezer doors are typically installed on both the door frame and the mullion to prevent ice or frost from forming on the door gaskets. Since both of these heater circuits need to be controlled by the ASDHC, the control is only able to handle half the number of doors as a cooler controller due to amperage capacity limitations.
*Pulse-Width Modulation may be used by certain controllers as opposed to on/off control to reduce thermal stress on heating elements.
Note: Our research revealed that the only controls using the Pulse Width Modulation (PWM) technology were either larger, multi-channel controllers, or controllers installed as part of a contract price in certain utility territories. The multi-channel controller data points were discarded due to lack of reliable cost data and the inherent inaccuracies of trying to scale those units down to the scale of the other data points. The contract price data points were included after estimating and deducting the estimated marketing, outreach and overhead costs included in that contract price.
Summary of Results Tab
The Summary of Results tab presents the total installed cost for ASDHCs. These costs are presented for seven regions allowing NEEP members to choose the market that best represents their service territory.
The regions represent the results of analyzing RSMeans City Cost Index (CCI) for the NEEP territory. Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into six unique regions (seven including a Non-Regional Specific category).
Alternative Data Integration
The following alternative data sources were used to inform the final result of this study:
- Internet-derived equipment costs: Costs for rebate-eligible Anti-Sweat Door Heater Controls gathered through internet searches were marked up by 35% and average labor costs added under the assumption that no end-user would install such equipment themselves. Rather, a contractor / installer would purchase the equipment and apply a standard markup before invoicing the customer. Each price for each model of equipment was given the weight of one data point.
- Installer Interviews: Navigant conducted 3 interviews with knowledgeable installers for the study. Each of the interviews produced one data point, including estimates of equipment cost, labor hours, and average quantity of doors installed per circuit (split between coolers and freezers). Where necessary those labor hours were combined with prevailing state-specific labor rates from RS Means to generate labor cost estimates for other data points that were not broken out into labor and materials.
- Contract pricing: For some or all of the data from the NYC, MD, MA and RI regions, the pricing of ASDHC installations is predetermined by contract between an approved installer and the respective Program Administrator. These data sets were adjusted to account for the assumed portion of the contract price attributable to administration, marketing and outreach needed to fulfill the terms of the contract.
Data Analysis Tab
Raw Data
A total of 212 cost points were collected through contractor interviews, program data extracts and invoices provided by NEEP member Program Administrators.
Formatted Data
Primary cost data was collected from contractors across seven states (NY, CT, MA, RI, NH, VT, MD). Due to the inherent differences in cost from one region to another, Navigant adjusted all material and labor cost points to represent Base Cost Factor (BCF) data using RSMeans City Cost Indexes (CCI). For example, if the cost provided from a contractor in Pennsylvania for an air source heat pump was $5000, than the NRS cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $5000 / 0.99
BCF = $5050
The same method was used to adjust all labor costs.
Labor Analysis
Navigant conducted contractor interviews to identify average labor rates and hours for controls installation.
Scrubbing of data: Data points were removed for any of the following reasons (also see "Alternative Data Integration," above):
- cost data couldn't be disaggregated from overall invoice cost
- no clear cost data available
- costs were for equipment that was designed for use with three phase power [costs were generally 2 to 3 times higher for these units]
- cost data was for multifunctional controls that include EFC. (see Note, above)
Removal of outliers: Navigant used a standard deviation methodology for determining outliers which is presented in the Material and Labor Cost Analysis section of the Data Analysis tab. The standard deviation was determined using the full scrubbed data set, and data points two standard deviations either side of the arithmetic mean were removed.
Results
Navigant defined the total measure cost on a per controller basis as well as on a per door basis for two installation categories: cooler doors, and freezer doors. To prevent contract prices and internet-derived data from having undue weight in the final result, data from each source group (i.e. each state/region and internet data) was averaged before deriving the final result. Outliers were removed from each source group before averaging. Results are presented as a Base Cost Factor from which regional specific costs are derived using RS Means cost index data. These average costs are presented on the Summary of Results tab.
`

## Anti-Sweat Door - Results
Anti Sweat Door Heater Controls
Data Vintage | 2014
Does this measure have incremental labor cost (Yes/No)? | Yes
Return to Measure Index
Base Cost Factor Results:
Unit | Base Cost Factor -BCF ($/Unit)
Door Heater Controller | 1051.9075
Cooler Door | 130.527
Freezer Door | 231.15
Results by Market:
Unit | Market 1 Northern New England Installed Cost ($/Unit)
Door Heater Controller | 951.0997
Cooler Door | 118.0182
Freezer Door | 208.9981
Unit | Market 2 Central/Southern New England Installed Cost ($/Unit)
Door Heater Controller | 1117.9672
Cooler Door | 138.7241
Freezer Door | 245.6662
Unit | Market 3 New England City Installed Cost ($/Unit)
Door Heater Controller | 1186.0257
Cooler Door | 147.1692
Freezer Door | 260.6216
Unit | Market 4 NY Metro Installed Cost ($/Unit)
Door Heater Controller | 1327.5072
Cooler Door | 164.7251
Freezer Door | 291.7113
Unit | Market 5 NY Upstate Installed Cost ($/Unit)
Door Heater Controller | 1050.0666
Cooler Door | 130.2986
Freezer Door | 230.7455
Unit | Market 6 Mid-Atlantic Installed Cost ($/Unit)
Door Heater Controller | 995.3674
Cooler Door | 123.5112
Freezer Door | 218.7257
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.97583 | 0.81533 | 0.90417
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9836 | 1.1632 | 1.0628
New England City | 3 | Boston, Providence | 1.008 | 1.2795 | 1.1275
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT | 1.0278 | 1.5593 | 1.262
NY Upstate | 5 | Buffalo, Rochester etc. | 0.9865 | 1.0135 | 0.99825
Mid-Atlantic | 6 | MD, DE, DC | 0.99275 | 0.88775 | 0.94625
National Average | - | - | 1 | 1 | 1
* Since the baseline cost for this measure is zero, these costs are actually the full installed cost including both materials and labor.
Regional adjustment factors are applied to national average incremental costs. *Since the baseline cost for this measure is zero, these costs are the full installed cost including both materials and labor. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category.

## Chillers - README
Commercial Chillers
Return to Measure Index
Measure Characterization:
| Efficient Measure Description | Commercial Chillers
| Baseline Description | Standard chiller with lowest efficiency rating in NEEP market
| Measure Scenario(s) | ROB
| Baseline Efficiency Levels | Air-Cooled: 9.6 EER
Water-Cooled Scroll: 0.78 kW/ton (0-150 tons), 0.72 kW/ton (>150 tons)
Water-Cooled Centrifugal: 0.64 kW/ton
| Measure Specifications and Efficiency Levels | A Standard Chiller with an efficiency exceeding the baseline efficiency level for that chiller type.
Air-Cooled: 9.90, 10.20, 10.52, 10.70 EER
Water-Cooled Scroll: 0-150 tons: 0.72, 0.68 kW/ton;
>150 tons: 0.68, 0.64, 0.60 kW/ton
Water-Cooled Centrifugal: 0.60, 0.58, 0.54 kW/ton
| Sizes | Air-Cooled: 50, 100, 150, 200, 400 tons
Water-Cooled Scroll: 50, 100, 150, 200, 400 tons
Water-Cooled Centrifugal: 100, 150, 200, 300, 600 tons
| Distinguishing Features | Technology (Scroll vs. Centrifugal)
| Installation Scenarios | Air-Cooled: Old chiller removal, new chiller ground installation
Water-Cooled: Old chiller removal, new chiller rooftop installation, galvanized steel cooling tower
Water-Cooled: Old chiller removal, new chiller rooftop installation, stainless-steel cooling tower
| Sources | Installers and distributors. DEER 2008, RSMeans
| Incremental Labor Cost | No - Labor cost is the same for efficient and baseline equipment.
| Cost Basis | Incremental
| Fuel Type | Electric
| Data Vintage | 2012
Incremental Cost Study Phase Two
Published: January, 2013
Full Measure Costs are used where the scenario assumes that there is no alternative measure .
Incremental Measure Costs are used when an energy-efficient appliance or measure promoted through a program is installed in lieu of the standard (less efficient) appliance/measure. The incremental cost is the difference between the baseline energy efficiency measure (material and labor) and the standard efficiency model. The equation for calculating incremental measure costs is simply:
Incremental measure cost = energy efficient measure cost (material + labor) - standard efficient baseline cost (material + labor)
In some cases there is no difference in the installation cost between the standard and efficient measure and/or an efficient measure and a more efficient measure. In those cases only materials costs are provided in the incremental cost.
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as a standard chiller with efficiency ratings for which incentives are currently available through states, and utilities in the NEEP market.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity . The baseline equipment in this instance is a standard chiller with the lowest efficiency rating available in the NEEP market. The assumption is that the least efficient chillers will be the most economical to purchase.
Incremental path: Navigant found during all contractor and manufacturer interviews that the installation costs primarily depend on the technology type, and the capacity of the chiller, i.e. the installation costs does not change with efficiency rating of the unit. Therefore, the incremental path primarily analysis the additional equipment cost only to move from a low efficiency unit to a high efficiency unit. This analysis assumes that a owner's chiller fails and decides to either replace the existing chiller of the same technology type (air-cooled, water-cooled screw/scroll, or water -cooled centrifugal) with an efficient unit, or an inefficient unit currently available in the NEEP market.
Results Tab
The tab presents the incremental cost for air and water-cooled chillers. Material, labor, and installed incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory. Estimates of chiller removal costs, rooftop or ground-mount installation costs (rooftop for water-cooled, and ground-mount for air-cooled chillers), and cooling tower equipment and installation costs (for water-cooled chillers) are included in the analysis. It should be noted that installation costs (material and labor) were not found to be incremental over the range of efficiencies, yet changed with capacity of the HVAC unit.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis
Raw Data
A total of 14 contractor interviews and 2 distributor interviews were completed for the analysis of the measure. Additionally, 30 raw data points were collected from a 2008 DEER study. A total of 234 cost points were collected for chiller equipment and installation costs.
Formatted Data
Primary cost data was collected from contractors across three states (MA, MD, and RI). Due to the inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in MA than in MD), Navigant adjusted all material and labor cost points to represent the Base Cost Factors (BCF) using RSMeans CCI. Table 1 provides a regional break down of NEEP. For example, if the cost provided from a contractor in New York Metro for a combination unit was $2,000, than the BCF cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $2,000 / 1.26
BCF = $1,592.67
The same method was used to adjust all labor costs.
Additionally, distributor costs do not include contractor markup. Therefore and where available, estimated markups were gathered from contractors and distributors. This average markup was applied to the distributor costs to produce estimated contractor costs.
Similarly, once BCF costs were determined for each measure, the costs were then allocated to each market by multiplying the BCF cost by the individual market factor.
The R.S. Means recalculated CCI factors annually. For this study, Navigant used the 2012 CCI factors. Additionally, any older data, collected for the ICS Phase One Report or other sources , was updated with the 2012 factors to maintain comparability with data collected in 2012 for the ICS Phase Two.
Equipment and Installation Cost Analysis
The analysis identified and removed any potential outlier data points through a review of the data.
A linear regression was used to develop the material and equipment costs for the measures. A regression was done for the entire range of efficiencies and chiller capacities. Such analysis was done to determine the following costs:
a) Air-Cooled Chiller (Scroll) Equipment Costs
b) Air-Cooled Chiller Ground-mount Installation Costs - Material
c) Air -Cooled Chiller Ground-mount Installation Costs - Labor
d) Water-Cooled Screw/Scroll Chiller Equipment Costs
e) Water-Cooled Screw/Scroll Rooftop (Typically on top of a 3-storey building) Installation Costs - Material
f) Water-Cooled Screw/Scroll Rooftop Installation Costs - Labor
g) Water-Cooled Centrifugal Chiller Equipment Costs
h) Water-Cooled Centrifugal Rooftop (Typically on top of a 3-storey building) Installation Costs - Material
i) Water-Cooled Centrifugal Rooftop Installation Costs - Labor
j) Galvanized Steel Cooling Tower Equipment Costs
k) Galvanized Steel Cooling Tower Installation Costs
l) Stainless Steel Cooling Tower Equipment Costs
m) Stainless Steel Cooling Tower Installation Costs
Labor Analysis
Contractor interviews identified the estimated hourly labor costs for installing chillers and chiller-related equipment. A, the labor rate was calculated with a weighted average of all contractor labor rates ($/HR) collected.
Results
Through contractor and distributor interviews, Navigant defined the most common unit size ranges installed in buildings. As such, results are presented for each of those size ranges at a non-regional specific level.

## Chillers - Results
Chillers
Data Vintage | 2012
Does this measure have incremental labor cost (Yes/No)? | No
Return to Measure Index
Base Cost Factor Results:
Air-Cooled Chiller Incremental Cost/Ton Estimates (Categorized by Efficiency (EER) ) Baseline EER = 9.60 | [5 empty] | Water-Cooled Scroll/Screw Chiller Incremental Cost/Ton Estimates (Categorized by Efficiency (kW/Ton) Baseline Efficiency: 0.78 kW/Ton
Capacity (Tons) | 9.6 | 9.9 | 10.2 | 10.52 | 10.7 | Capacity (Tons) | 0.78 | 0.72 | 0.68 | 0.64 | 0.6 | Water-Cooled Centrifugal Chiller Incremental Cost Estimates (Categorized by Efficiency (kW / Ton) ) Baseline Efficiency: 0.64 kW / Ton
50 | 0 | 228.5371 | 457.0743 | 700.8472 | 837.9695 | 50 | 0 | 75.8285 | 126.3809 | n/a | n/a | Capacity (Tons) | 0.64 | 0.6 | 0.58 | 0.54
100 | 0 | 114.2686 | 228.5371 | 350.4236 | 418.9848 | 100 | 0 | 37.9143 | 63.1904 | n/a | n/a | 100 | 0 | 73.3498 | 110.0247 | 183.3745
150 | 0 | 76.179 | 152.3581 | 233.6157 | 279.3232 | 150 | 0 | 25.2762 | 42.127 | n/a | n/a | 150 | 0 | 48.8999 | 73.3498 | 122.2496
200 | 0 | 46.6011 | 93.2021 | 142.9099 | 170.8706 | 200 | n/a | 0 | 61.1202 | 122.2404 | 183.3606 | 200 | 0 | 36.6749 | 55.0123 | 91.6872
400 | 0 | 23.3005 | 46.6011 | 71.455 | 85.4353 | 400 | n/a | 0 | 30.5601 | 61.1202 | 91.6803 | 300 | 0 | 60.9263 | 91.3894 | 152.3157
[12 empty] | 600 | 0 | 30.4631 | 45.6947 | 76.1579
Results by Market:
Market 1 Air-Cooled Chiller Incremental Cost/Ton Estimates (Categorized by Efficiency (EER) ) Baseline EER = 9.60 | [5 empty] | Market 1 Water-Cooled Scroll/Screw Chiller Incremental Cost Estimates (Categorized by Efficiency (kW/Ton) Baseline Efficiency: 0.78 kW/Ton | [5 empty] | Water-Cooled Centrifugal Chiller Incremental Cost Estimates (Categorized by Efficiency (kW / Ton) ) Baseline Efficiency: 0.64 kW / Ton
Capacity (Tons) | 9.6 | 9.9 | 10.2 | 10.52 | 10.7 | Capacity (Tons) | 0.78 | 0.72 | 0.68 | 0.64 | 0.6 | Capacity (Tons) | 0.64 | 0.6 | 0.58 | 0.54
50 | 0 | 223.9664 | 447.9328 | 686.8303 | 821.2101 | 50 | 0 | 74.3119 | 123.8532 | n/a | n/a | 100 | 0 | 71.8828 | 107.8242 | 179.707
100 | 0 | 111.9832 | 223.9664 | 343.4151 | 410.6051 | 100 | 0 | 37.156 | 61.9266 | n/a | n/a | 150 | 0 | 47.9219 | 71.8828 | 119.8047
150 | 0 | 74.6555 | 149.3109 | 228.9434 | 273.7367 | 150 | 0 | 24.7706 | 41.2844 | n/a | n/a | 200 | 0 | 35.9414 | 53.9121 | 89.8535
200 | 0 | 45.669 | 91.3381 | 140.0517 | 167.4532 | 200 | n/a | 0 | 59.8978 | 119.7956 | 179.6934 | 300 | 0 | 59.7078 | 89.5617 | 149.2694
400 | 0 | 22.8345 | 45.669 | 70.0259 | 83.7266 | 400 | n/a | 0 | 29.9489 | 59.8978 | 89.8467 | 600 | 0 | 29.8539 | 44.7808 | 74.6347
Market 2 Air-Cooled Chiller Incremental Cost/Ton Estimates (Categorized by Efficiency (EER) ) Baseline EER = 9.60 | [5 empty] | Market 2 Water-Cooled Scroll/Screw Chiller Incremental Cost Estimates (Categorized by Efficiency (kW/Ton) Baseline Efficiency: 0.78 kW/Ton | [5 empty] | Water-Cooled Centrifugal Chiller Incremental Cost Estimates (Categorized by Efficiency (kW / Ton) ) Baseline Efficiency: 0.64 kW / Ton
Capacity (Tons) | 9.6 | 9.9 | 10.2 | 10.52 | 10.7 | Capacity (Tons) | 0.78 | 0.72 | 0.68 | 0.64 | 0.6 | Capacity (Tons) | 0.64 | 0.6 | 0.58 | 0.54
50 | 0 | 226.2518 | 452.5035 | 693.8388 | 829.5898 | 50 | 0 | 75.0702 | 125.117 | n/a | n/a | 100 | 0 | 72.6163 | 108.9244 | 181.5407
100 | 0 | 113.1259 | 226.2518 | 346.9194 | 414.7949 | 100 | 0 | 37.5351 | 62.5585 | n/a | n/a | 150 | 0 | 48.4109 | 72.6163 | 121.0272
150 | 0 | 75.4173 | 150.8345 | 231.2796 | 276.5299 | 150 | 0 | 25.0234 | 41.7057 | n/a | n/a | 200 | 0 | 36.3081 | 54.4622 | 90.7704
200 | 0 | 46.1351 | 92.2701 | 141.4808 | 169.1619 | 200 | n/a | 0 | 60.509 | 121.018 | 181.527 | 300 | 0 | 60.317 | 90.4755 | 150.7926
400 | 0 | 23.0675 | 46.1351 | 70.7404 | 84.5809 | 400 | n/a | 0 | 30.2545 | 60.509 | 90.7635 | 600 | 0 | 30.1585 | 45.2378 | 75.3963
Market 3 Air-Cooled Chiller Incremental Cost/Ton Estimates (Categorized by Efficiency (EER) ) Baseline EER = 9.60 | [5 empty] | Market 3 Water-Cooled Scroll/Screw Chiller Incremental Cost Estimates (Categorized by Efficiency (kW/Ton) Baseline Efficiency: 0.78 kW/Ton | [5 empty] | Water-Cooled Centrifugal Chiller Incremental Cost Estimates (Categorized by Efficiency (kW / Ton) ) Baseline Efficiency: 0.64 kW / Ton
Capacity (Tons) | 9.6 | 9.9 | 10.2 | 10.52 | 10.7 | Capacity (Tons) | 0.78 | 0.72 | 0.68 | 0.64 | 0.6 | Capacity (Tons) | 0.64 | 0.6 | 0.58 | 0.54
50 | 0 | 230.8225 | 461.645 | 707.8557 | 846.3492 | 50 | 0 | 76.5868 | 127.6447 | n/a | n/a | 100 | 0 | 74.0833 | 111.1249 | 185.2082
100 | 0 | 115.4113 | 230.8225 | 353.9278 | 423.1746 | 100 | 0 | 38.2934 | 63.8223 | n/a | n/a | 150 | 0 | 49.3889 | 74.0833 | 123.4721
150 | 0 | 76.9408 | 153.8817 | 235.9519 | 282.1164 | 150 | 0 | 25.5289 | 42.5482 | n/a | n/a | 200 | 0 | 37.0416 | 55.5625 | 92.6041
200 | 0 | 47.0671 | 94.1342 | 144.339 | 172.5793 | 200 | n/a | 0 | 61.7314 | 123.4628 | 185.1942 | 300 | 0 | 61.5356 | 92.3033 | 153.8389
400 | 0 | 23.5335 | 47.0671 | 72.1695 | 86.2896 | 400 | n/a | 0 | 30.8657 | 61.7314 | 92.5971 | 600 | 0 | 30.7678 | 46.1517 | 76.9194
Market 4 Air-Cooled Chiller Incremental Cost/Ton Estimates (Categorized by Efficiency (EER) ) Baseline EER = 9.60 | [5 empty] | Market 4 Water-Cooled Scroll/Screw Chiller Incremental Cost Estimates (Categorized by Efficiency (kW/Ton) Baseline Efficiency: 0.78 kW/Ton | [5 empty] | Water-Cooled Centrifugal Chiller Incremental Cost Estimates (Categorized by Efficiency (kW / Ton) ) Baseline Efficiency: 0.64 kW / Ton
Capacity (Tons) | 9.6 | 9.9 | 10.2 | 10.52 | 10.7 | Capacity (Tons) | 0.78 | 0.72 | 0.68 | 0.64 | 0.6 | Capacity (Tons) | 0.64 | 0.6 | 0.58 | 0.54
50 | 0 | 235.3933 | 470.7865 | 721.8726 | 863.1086 | 50 | 0 | 78.1034 | 130.1723 | n/a | n/a | 100 | 0 | 75.5503 | 113.3254 | 188.8757
100 | 0 | 117.6966 | 235.3933 | 360.9363 | 431.5543 | 100 | 0 | 39.0517 | 65.0861 | n/a | n/a | 150 | 0 | 50.3669 | 75.5503 | 125.9171
150 | 0 | 78.4644 | 156.9288 | 240.6242 | 287.7029 | 150 | 0 | 26.0345 | 43.3908 | n/a | n/a | 200 | 0 | 37.7751 | 56.6627 | 94.4379
200 | 0 | 47.9991 | 95.9982 | 147.1972 | 175.9967 | 200 | n/a | 0 | 62.9538 | 125.9076 | 188.8614 | 300 | 0 | 62.7541 | 94.1311 | 156.8852
400 | 0 | 23.9996 | 47.9991 | 73.5986 | 87.9984 | 400 | n/a | 0 | 31.4769 | 62.9538 | 94.4307 | 600 | 0 | 31.377 | 47.0656 | 78.4426
Market 5 Air-Cooled Chiller Incremental Cost/Ton Estimates (Categorized by Efficiency (EER) ) Baseline EER = 9.60 | [5 empty] | Market 5 Water-Cooled Scroll/Screw Chiller Incremental Cost Estimates (Categorized by Efficiency (kW/Ton) Baseline Efficiency: 0.78 kW/Ton | [5 empty] | Water-Cooled Centrifugal Chiller Incremental Cost Estimates (Categorized by Efficiency (kW / Ton) ) Baseline Efficiency: 0.64 kW / Ton
Capacity (Tons) | 9.6 | 9.9 | 10.2 | 10.52 | 10.7 | Capacity (Tons) | 0.78 | 0.72 | 0.68 | 0.64 | 0.6 | Capacity (Tons) | 0.64 | 0.6 | 0.58 | 0.54
50 | 0 | 226.2518 | 452.5035 | 693.8388 | 829.5898 | 50 | 0 | 75.0702 | 125.117 | n/a | n/a | 100 | 0 | 72.6163 | 108.9244 | 181.5407
100 | 0 | 113.1259 | 226.2518 | 346.9194 | 414.7949 | 100 | 0 | 37.5351 | 62.5585 | n/a | n/a | 150 | 0 | 48.4109 | 72.6163 | 121.0272
150 | 0 | 75.4173 | 150.8345 | 231.2796 | 276.5299 | 150 | 0 | 25.0234 | 41.7057 | n/a | n/a | 200 | 0 | 36.3081 | 54.4622 | 90.7704
200 | 0 | 46.1351 | 92.2701 | 141.4808 | 169.1619 | 200 | n/a | 0 | 60.509 | 121.018 | 181.527 | 300 | 0 | 60.317 | 90.4755 | 150.7926
400 | 0 | 23.0675 | 46.1351 | 70.7404 | 84.5809 | 400 | n/a | 0 | 30.2545 | 60.509 | 90.7635 | 600 | 0 | 30.1585 | 45.2378 | 75.3963
[12 empty] | Market Code | 6 | Mid-Atlantic
Market 6 Air-Cooled Chiller Incremental Cost/Ton Estimates (Categorized by Efficiency (EER) ) Baseline EER = 9.60 | [5 empty] | Market 6 Water-Cooled Scroll/Screw Chiller Incremental Cost Estimates (Categorized by Efficiency (kW/Ton) Baseline Efficiency: 0.78 kW/Ton | [5 empty] | Water-Cooled Centrifugal Chiller Incremental Cost Estimates (Categorized by Efficiency (kW / Ton) ) Baseline Efficiency: 0.64 kW / Ton
Capacity (Tons) | 9.6 | 9.9 | 10.2 | 10.52 | 10.7 | Capacity (Tons) | 0.78 | 0.72 | 0.68 | 0.64 | 0.6 | Capacity (Tons) | 0.64 | 0.6 | 0.58 | 0.54
50 | 0 | 228.5371 | 457.0743 | 700.8472 | 837.9695 | 50 | 0 | 75.8285 | 126.3809 | n/a | n/a | 100 | 0 | 73.3498 | 110.0247 | 183.3745
100 | 0 | 114.2686 | 228.5371 | 350.4236 | 418.9848 | 100 | 0 | 37.9143 | 63.1904 | n/a | n/a | 150 | 0 | 48.8999 | 73.3498 | 122.2496
150 | 0 | 76.179 | 152.3581 | 233.6157 | 279.3232 | 150 | 0 | 25.2762 | 42.127 | n/a | n/a | 200 | 0 | 36.6749 | 55.0123 | 91.6872
200 | 0 | 46.6011 | 93.2021 | 142.9099 | 170.8706 | 200 | n/a | 0 | 61.1202 | 122.2404 | 183.3606 | 300 | 0 | 60.9263 | 91.3894 | 152.3157
400 | 0 | 23.3005 | 46.6011 | 71.455 | 85.4353 | 400 | n/a | 0 | 30.5601 | 61.1202 | 91.6803 | 600 | 0 | 30.4631 | 45.6947 | 76.1579
Market | Market Code | Example | Material Adj Factor | Labor Adj Factor | Average Adj Factor
Northern New England | 1 | ME, VT, NH | 0.98 | 0.69 | 0.835
Central/Southern New England | 2 | MA exc Boston, RI, most CT | 0.99 | 1.13 | 1.06
New England City | 3 | Boston, Providence | 1.01 | 1.24 | 1.125
NY Metro | 4 | NYC, metro suburbs Southwest CT | 1.03 | 1.55 | 1.29
NY Upstate | 5 | Buffalo, Rochester etc. | 0.99 | 1 | 0.995
Mid-Atlantic | 6 | MD, DE DC | 1 | 0.89 | 0.945
Base Cost Factor | - | - | 1 | 1 | 1
Summary of incremental cost data analysis for Air and Water-Cooled Chillers. Regional adjustment factors are applied to the base cost factors to calculate market specific results. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category.
Note: Baseline assumptions correspond to a standard chiller with the lowest efficiency rating available in the NEEP market. The assumption is that the least efficient chillers will be the most economical to purchase. The total installation cost estimate includes all material and labor costs for a typical chiller replacement installation.
Equipment costing data obtained from manufacturers and contractors were cross-checked with invoice data provided by National Grid to confirm costing is in expected range. Navigant assumed that chillers are replaced either at failure or at the end of its useful life. Therefore, installation cost estimates include chiller removal, new chiller installation (ground for air-cooled, rooftop (of a 3-storey building) for water-cooled), and any cooling tower costs associated with water-cooled chillers. EER = Energy Efficiency Ratio = 12/(kW/Ton) kW/Ton = kilowatt per Ton Chiller Capacity

## Com Boilers - README
Commercial Boilers
Return to Measure Index
Measure Characterization:
| Measure Description | Commercial Boilers
| Baseline Description | Baseline (Federal Minimum Standard Efficiency) Boiler
| Measure Scenario(s) | ROB, NC
| Baseline Efficiency Levels | 80% Thermal Efficiency (TE)
| Measure Level Description and Specifications | Two high-efficiency cases were defined in terms of thermal efficiency based on review of federal specifications.
>= 85% TE
>= 90% TE
| Sizes | Between 300 and 2,200 kBTU/hr.
| Distinguishing Features | N/A
| Installation Scenarios | Gas-fired hot water boilers
| Sources | Gas Networks, National Grid, Vermont Gas
| Incremental Labor Cost | Yes
| Cost Basis | Incremental
| Fuel Type | Gas
| Data Vintage | 2011
Incremental Cost Study Phase One
Published: September, 2011
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the standard (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = measure material cost (material + labor) - base case material cost (material + labor)
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as a commercial gas-fired boiler with a thermal efficiency greater than or equal to 85%.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity . The baseline equipment in this instance is a commercial gas-fired boiler with a thermal efficiency of 80% which corresponds to the current minimum Federal standard.
Results Tab
The tab presents the incremental cost for the commercial boilers. Material, labor, and installed incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis
Raw Data
A total of 15 contractor interviews were completed for the analysis of the measure. A total of 54 contractor-reported cost points and 23 internet-based cost points were collected for commercial boilers (77 cost points in total).
Formatted Data
Primary cost data was collected from contractors across a five states (MA, NY, NH, VT, and RI). Due to the inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent base cost factor (BCF) data using RSMeans CCI. Table 1 provides a regional break down of the NEEP. For example, if the cost provided from a contractor in New York Metro for a commercial boiler was $10,000, than the BCF cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $10,000 / 1.26
BCF = $7936.51
The same method was used to adjust all labor cost.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data.
A linear regression was used to develop the material cost for the measure. A regression was done for the following efficiency categories:
a) Thermal Efficiency = 80
b) 80 < Thermal Efficiency =< 96
Labor Analysis
Some contractor interviews identified a small incremental difference in the time to install efficient versus base scenario equipment, while other contractors report no incremental labor for high efficiency installations. On average, efficient equipment took approximately 7 additional man- hours to install when compared with base equipment. The labor rate was calculated by an average of all contractor- reported labor rates ($/HR). An average installation times was used to determine the time required to install measure and baseline equipment.
Results
Through contractor interviews, Navigant defined the most common unit sizes. As such, results are presented for each of those size categories at a non-regional specific level.

## Com Boilers - Results
Commercial Boilers
Data Vintage | 2011
Does this measure have incremental labor cost (Yes/No)? | Yes
Return to Measure Index
Base Cost Factor Results:
Size (MBH) | Base Cost Factor ($/Unit)
| CEE Tier 1 (80 to 85%) | CEE Tier 2 (80 to 90%)
300 | 625.3016 | 3304.7005
500 | 1384.5214 | 4063.9202
700 | 2143.7411 | 4823.14
900 | 2902.9609 | 5582.3598
1100 | 3662.1807 | 6341.5795
1300 | 4421.4004 | 7100.7993
1500 | 5180.6202 | 7860.0191
1700 | 5939.84 | 8619.2388
2000 | 7078.6696 | 9758.0685
2200 | 7837.8894 | 10517.2882
Results by Market:
Size (MBH) | Market 1 Northern New England Incremental Cost ($/Unit)
| CEE Tier 1 (80 to 85%) | CEE Tier 2 (80 to 90%)
300 | 532.1317 | 2812.3001
500 | 1178.2277 | 3458.3961
700 | 1824.3237 | 4104.4921
900 | 2470.4197 | 4750.5882
1100 | 3116.5158 | 5396.6842
1300 | 3762.6118 | 6042.7802
1500 | 4408.7078 | 6688.8762
1700 | 5054.8038 | 7334.9722
2000 | 6023.9478 | 8304.1163
2200 | 6670.0439 | 8950.2123
Size (MBH) | Market 2 Central/Southern New England Incremental Cost ($/Unit)
| CEE Tier 1 (80 to 85%) | CEE Tier 2 (80 to 90%)
300 | 658.1925 | 3478.5277
500 | 1457.3472 | 4277.6824
700 | 2256.5019 | 5076.8372
900 | 3055.6567 | 5875.9919
1100 | 3854.8114 | 6675.1466
1300 | 4653.9661 | 7474.3013
1500 | 5453.1208 | 8273.4561
1700 | 6252.2756 | 9072.6108
2000 | 7451.0076 | 10271.3429
2200 | 8250.1624 | 11070.4976
Size (MBH) | Market 3 New England City Incremental Cost ($/Unit)
| CEE Tier 1 (80 to 85%) | CEE Tier 2 (80 to 90%)
300 | 697.2113 | 3684.741
500 | 1543.7413 | 4531.2711
700 | 2390.2714 | 5377.8011
900 | 3236.8014 | 6224.3311
1100 | 4083.3315 | 7070.8612
1300 | 4929.8615 | 7917.3912
1500 | 5776.3915 | 8763.9213
1700 | 6622.9216 | 9610.4513
2000 | 7892.7166 | 10880.2463
2200 | 8739.2467 | 11726.7764
Size (MBH) | Market 4 NY Metro Incremental Cost ($/Unit)
| CEE Tier 1 (80 to 85%) | CEE Tier 2 (80 to 90%)
300 | 785.2225 | 4149.8776
500 | 1738.6127 | 5103.2678
700 | 2692.0029 | 6056.6581
900 | 3645.3932 | 7010.0483
1100 | 4598.7834 | 7963.4385
1300 | 5552.1736 | 8916.8287
1500 | 6505.5638 | 9870.2189
1700 | 7458.954 | 10823.6092
2000 | 8889.0394 | 12253.6945
2200 | 9842.4296 | 13207.0847
Size (MBH) | Market 5 NY Upstate Incremental Cost ($/Unit)
| CEE Tier 1 (80 to 85%) | CEE Tier 2 (80 to 90%)
300 | 618.267 | 3267.5226
500 | 1368.9455 | 4018.2011
700 | 2119.6241 | 4768.8797
900 | 2870.3026 | 5519.5582
1100 | 3620.9811 | 6270.2368
1300 | 4371.6597 | 7020.9153
1500 | 5122.3382 | 7771.5938
1700 | 5873.0168 | 8522.2724
2000 | 6999.0346 | 9648.2902
2200 | 7749.7131 | 10398.9687
Size (MBH) | Market 6 Mid-Atlantic Incremental Cost ($/Unit)
| CEE Tier 1 (80 to 85%) | CEE Tier 2 (80 to 90%)
300 | 572.3073 | 3024.6271
500 | 1267.1832 | 3719.503
700 | 1962.0591 | 4414.3789
900 | 2656.935 | 5109.2548
1100 | 3351.8109 | 5804.1307
1300 | 4046.6868 | 6499.0066
1500 | 4741.5626 | 7193.8824
1700 | 5436.4385 | 7888.7583
2000 | 6478.7524 | 8931.0722
2200 | 7173.6283 | 9625.9481
Market | Market Code | Regions | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.851
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 1.0526
New England City | 3 | Boston, Providence | 1.115
NY Metro | 4 | NYC, Metro, Suburbs, SE CT | 1.2557
NY Upstate | 5 | Buffalo, Rochester etc. | 0.98875
Mid-Atlantic | 6 | MD, DE, DC | 0.91525
National Average | - | - | 1
Summary of incremental cost data analysis for commercial gas boilers. Regional adjustment factors are applied to national average incremental costs.
Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category
Note: Baseline Assumptions corresponds to Federal Minimum Thermal Efficiency (80%) .

## Com Convection Ovens - README
Commercial Convection Ovens | Return to Measure Index
Measure Characterization:
| Efficient Measure Description | ENERGY STAR® Commercial Gas Convection Ovens
| Baseline Description | Standard Commercial Convection Oven
| Measure Scenario(s) | NC, RET
| Baseline Efficiency Levels and Specifications | Existing equipment or standard cooking efficiency: Gas Convection Ovens = 30% cooking efficiency
| Efficient Measure Description & Specifications | ENERGY STAR® qualified efficient commercial ovens, which save energy during preheat, cooking, and idle times due to improved cooking efficiency, and preheat and idle energy rates
ENERGY STAR® Criteria: Gas
|  | Oven Capacity | Idle Rate (Btu/h) | Cooking Efficiency (%)
|  | Full-Size | ≤ 12,000 Btu/h | ≥ 46%
| Sizes | Per oven. [Note: Ovens come in single, double or sometimes quadruple stacks] The size of the oven, or its capacity, depends on whether it can accept standard full-size (18" x 26" x 1") or hal-size (18" x 13" x 1") sheet pans
| Distinguishing Features | ENERGY STAR® qualified; meeting the criteria described in the "Efficient Measure Description & Specifications"
| Installation Scenarios | Commercial kitchens
| Sources | Massachusetts TRM, Mass Save, Rhode Island TRM, Delaware TRM, Energize CT, Baltimore Gas and Electric, DC Sustainable Energy Utility, Food Service Technology Center, ENERY STAR website, Illinois TRM, and Indiana TRM
| Comments | Cooking energy efficiency is the ratio of energy added to the food and the total energy supplied to the oven during cooking.
| Incremental Labor Cost | No - Labor cost is the same for efficient and baseline equipment.
| Cost Basis | Incremental
| Fuel Type | Gas
| Data Vintage | 2014
Incremental Cost Study Phase Four
Published: May, 2015
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the baseline (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = ( efficient measure material cost + efficient measure installation cost ) -
( baseline equipment material cost + baseline equipment installation cost )
In the case of the Commercial Convection Ovens measure, the efficient measure and baseline equipment installation costs are the same (as confirmed by installer interviews), so the baseline and efficient measure labor costs cancel out, and the formula becomes:
Incremental measure cost = efficient measure material cost - baseline equipment material cost
Qualifying Measure: A qualifying measure is defined as the efficient alternative to the baseline option of installation. In this case, it is an ENERGY STAR rated Commercial Kitchen Gas Convection Oven in line with the ENERGY STAR Criteria (see the Measure Characterization portion of this tab).
Baseline: The baseline equipment is defined as the standard equipment that would have been installed without the utility rebate or incentive program. The baseline equipment in this instance is a non-qualifying, economy or standard commercial kitchen gas convection oven in line with the current minimum Federal standards.
Measure Characteristics
Size Category - Ovens can be sold in singles, doubles and even quadruples, often referred to as single stack, double stack and quadruple stack. There are typically two identical ovens of the same size and model number in a double stack, and four in a quadruple stack.
Oven Cavity - The cavity of an oven is described via two distinct metrics, its literal height and width in terms of inches, and its depth, in terms of standard or full and deep or bakery verbiage. If an oven cavity is defined as deep or bakery, it will have a larger depth and typically a larger cavity than standard of full ovens.
Summary of Results Tab
The summary of results tab presents the incremental cost for the Commercial Kitchen Gas Convection Oven. Incremental costs are presented in 7 categories allowing NEEP members to choose the market that best represents their service territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis Tab
Raw Data
A total of 179 cost points were collected through contractor interviews, equipment catalogues, and invoices provided by NEEP member Program Administrators. Each data point is given equal weighting. A total of 25 data points were removed, with 5 of those being electric convection ovens. (Only gas ovens were assessed and researched for this study.) Nine of the remaining data points were removed based on a standard deviation determination of outliers as they relate to the arithmetic mean of the population. See 'Removal of Outliers' section, below.
Eleven of the removed data points were the Manufacturer's Suggested Retail Price ("MSRP"), which is rarely the price paid in the marketplace. There was often a substantially discounted price for the same model that was used in place of the MSRP. The MSRP is a mechanism utilized by manufacturers to standardize prices among locations in the region. Every source Navigant researched suggested the industry standard was to sell below, and in most cases substantially below the MSRP. As a result, the MSRP is not a product listed price, but rather a suggestion that is rarely adhered to in the commercial oven retail market, and as such, MSRP data was not included in this study.
To determine the incremental cost, Navigant collected data points on both baseline and qualifying units. Qualifying units are defined as units that are Energy Star rated and meet or exceed the Energy Star requirements. In column I ("Efficiency Tier") of the 'Data Analysis' tab, qualifying units are given the value 1, and baseline units are labeled with a 0.
Removal of Outliers
After MSRP and electric oven data points were removed as described above, remaining data points that were more than two standard deviations above or below the arithmetic mean for the remaining baseline population or efficient population respectively were removed as outliers. For more detail on the removed data, see the 'Outlier Determination' tab.
Formatted Data
Primary cost data was collected from contractors across three states (MA, CT, and NY). Due to the inherent differences in cost from one region to another, Navigant adjusted all material and labor cost points to represent non-regional specific Base Cost Factor (BCF) using RSMeans City Cost Indexes (CCI). For example, if the cost provided from a contractor in Massachusetts for a commercial gas fryer was $3,000, than the BCF would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $3,000 / 0.98
BCF = $3,061
Alternative Data Integration
The majority of data points used in the analysis were sourced from invoices provided by Program Administrators and equipment catalogues from retailers who have previously participated in utility offered programs. Additional cost data was obtained from the following sources:
Installer Interviews: Navigant conducted four interviews with knowledgeable installers and manufacturers for the study. Each of the interviews produced one data point, including accurate estimates of equipment cost. These interviews also confirmed that the installation costs were the same for qualifying vs. non-qualifying equipment.
Internet-derived equipment costs: Costs for rebate-eligible Commercial Kitchen Gas Convection Ovens were gathered through online retailers and vendor catalogues published online. Each price for each model of equipment was given the weight of one data point. These costs were confirmed to be retail prices and as such were not marked-up.
CPUC/Itron Measure Cost Study: Itron completed a comparable incremental cost study for the California Public Utilities Commission (CPUC) that included Commercial Gas Convection Ovens. The results were published in an aggregate form for equipment costs only, which meant that Navigant did not have access to the raw data points used in the study. Navigant used the CPUC/Itron results only for comparison to the Navigant results, not as a data point to be included in the cost analysis.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data. Manufacturer Specified Retail Prices (MSRP) were also removed as they did not represent the actual equipment prices paid on the market. Cost data for electric convection ovens were excluded as Navigant's research focused solely on natural gas convection ovens.
A linear regression was used to identify any correlation between the size of an oven and its cost. This analysis determined that there was little correlation and as a result, the incremental material costs are reported as an arithmetic mean on a per unit and per kBtu output basis.
Labor Analysis
Contractor interviews identified no incremental difference in the time or cost to install efficient versus baseline equipment. In general, efficient equipment took just as much time, cost, work, and labor to install as compared with base equipment. There is no labor incremental cost associated with this measure, and was not included in the analysis.
Results and Findings
Navigant reported findings on a per unit basis, or per cavity basis. For double or quadruple models, the full price was divided by two and four, respectively. The analysis resulted in a negative incremental cost, meaning that the baseline equipment was more expensive, on average, than the efficient, ENERGY STAR rated units. These results mirror those found by the CPUC/Itron in their incremental cost study, although Navigant's result was of greater magnitude.
One plausible explanation for this finding is the market's continuing shift away from the production of non-qualifying units toward ENERGY STAR rated models. Since the upgrades required to meet the ENERGY STAR standard are minimal and the marketing benefits of the ENERGY STAR label are significant, some manufacturers are almost exclusively producing ENERGY STAR Convection Ovens, and others have now discontinued many of their non-qualifying units. This trend was a common theme in Navigant's market actor and subject matter expert interviews. However, while manufacturers have been discontinuing most non-qualifying models, they have continued the production of the most durable, high-end non-qualifying units - models made of sturdier materials and accessorized with high quality controls and features - which are still in high demand. Thus the non-qualifying units in the market today are for the most part high-end, high-priced alternatives to the common ENERGY STAR rated units, which results in the negative average incremental cost as determined through this and other studies.

## Com Convection Ovens - Results
Commercial Convection Ovens
Data Vintage | 2014
Does this measure have incremental labor cost (Yes/No)? | No
Return to Measure Index
Base Cost Factor Results:
Equipment Description | Non-Regional Specific Incremental Cost ($/Cavity)
Commercial Kitchen Convection Oven | -1791.4229
Results by Market:
Equipment Description | Market 1: Northern New England Incremental Cost ($/Cavity)
Commercial Kitchen Convection Oven | -1748.1301
Equipment Description | Market 2: Central/Southern New England Incremental Cost ($/Cavity)
Commercial Kitchen Convection Oven | -1762.0435
Equipment Description | Market 3: New England City Incremental Cost ($/Cavity)
Commercial Kitchen Convection Oven | -1805.7542
Equipment Description | Market 4: NY Metro Incremental Cost ($/Cavity)
Commercial Kitchen Convection Oven | -1841.1348
Equipment Description | Market 5: NY Upstate Incremental Cost ($/Cavity)
Commercial Kitchen Convection Oven | -1767.2387
Equipment Description | Market 6: Mid-Atlantic Incremental Cost ($/Cavity)
Commercial Kitchen Convection Oven | -1778.435
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.97583 | 0.81533 | 0.90417
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9836 | 1.1632 | 1.0628
New England City | 3 | Boston, Providence | 1.008 | 1.2795 | 1.1275
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT | 1.0278 | 1.5593 | 1.262
NY Upstate | 5 | Buffalo, Rochester etc. | 0.9865 | 1.0135 | 0.99825
Mid-Atlantic | 6 | MD, DE, DC | 0.99275 | 0.88775 | 0.94625
National Average | - | - | 1 | 1 | 1
Summary of incremental cost data analysis for Commercial Convection Ovens including both materials and labor. Regional adjustment factors are applied to national average incremental costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category .

## Com Fryers - README
Commercial Gas Fryers
Return to Measure Index
Measure Characterization:
| Efficient Measure Description | ENERGY STAR® Commercial Gas Fryers
| Baseline Description | Standard Commercial Gas Fryer
| Measure Scenario(s) | NC, RET
| Baseline Efficiency Levels and Specifications | Existing equipment or standard cooking efficiency: Gas = 35% cooking efficiency
| Efficient Measure Description & Specifications | ENERGY STAR® qualified commerical fryers, which save energy with shorter cook times and higher production rates through advanced burner and heat exchanger designs
ENERGY STAR® Criteria: Gas
|  | Fryer Type | Idle Rate (Btu/h) | Cooking Efficiency (%)
|  | Standard Open Deep | ≤ 9,000 | ≥ 50%
|  | Large Vat Open Deep | ≤ 12,000
| Sizes | Per fryer; Fryers can have multiple vats, which can differ in width, depth, and shortening capacity
| Distinguishing Features | ENERGY STAR® qualified; meeting the criteria described in the "Efficient Measure Description & Specifications"
| Installation Scenarios | Commerical kitchens
| Sources | Massachusetts TRM, Mass Save, Rhode Island TRM, Delaware TRM, Energize CT, Baltimore Gas and Electric, DC Sustainable Energy Utility, Food Service Technology Center, ENERY STAR website, Illinois TRM, and Indiana TRM
| Comments | Initial cost generally plays a more significant role in commercial fryer purchasing than the operating costs. Cooking energy efficiency is the ratio of energy added to the food and the total energy supplied to the oven during cooking.
| Incremental Labor Cost | No - Labor cost is the same for efficient and baseline equipment.
| Cost Basis | Incremental
| Fuel Type | Gas
| Data Vintage | 2014
Incremental Cost Study Phase Four
Published: May, 2015
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the baseline (less efficient) appliance/measure. The equation for calculating incremental measure costs is:
Incremental measure cost = ( efficient measure material cost + efficient measure installation cost ) -
( baseline equipment material cost + baseline equipment installation cost )
In the case of the Commercial Fryers measure, the efficient measure and baseline equipment installation costs are the same (as confirmed by installer interviews), so the baseline and efficient measure labor costs cancel out, and the formula becomes:
Incremental measure cost = efficient measure material cost - baseline equipment material cost
Qualifying Measure: A qualifying measure is defined as the efficient alternative to the baseline option of installation. In this case, it is an ENERGY STAR rated commercial kitchen gas fryer in line with the ENERGY STAR Criteria (see the Measure Characterization portion of this tab).
Baseline: The baseline equipment is defined as the standard equipment that would have been installed without the utility rebate or incentive program. The baseline equipment in this instance is a non-qualifying, economy or standard commercial kitchen gas fryer in line with the current minimum Federal standards.
Summary of Results Tab
The summary of results tab presents the incremental cost for the commercial kitchen gas fryer. Incremental costs are presented in 7 categories allowing NEEP members to choose the market that best represents their service territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis Tab
Raw Data
A total of 113 cost points for new baseline and qualifying equipment were collected through contractor interviews, equipment catalogues, and invoices provided by NEEP constituents. Each data point is given equal weighting. A total of 24 data points were removed, with 9 of those being electric or propane fryers (only gas fryers were assessed in this study). The other 15 data points were removed based on a standard deviation determination of outliers relative to the arithmetic mean of the population. Any data point greater than two standard deviations from the mean was removed.
To determine the incremental cost, Navigant collected data points on both baseline and qualifying units. Qualifying units are defined as units that meet or exceed the ENERGY STAR requirements. In column I ("Efficiency Tier") of the 'Data Analysis' tab, qualifying units are given the value 1, and baseline units, 0.
Removal of Outliers
Data points more than two standard deviations either side of the arithmetic mean were removed from the dataset before final analysis.
The calculation of standard deviation and identification of outliers is shown on the 'Outlier Determination' tab.
Formatted Data
Primary cost data was collected from contractors across three states (MA, CT, and NY). Due to the inherent differences in cost from one region to another, Navigant adjusted all material and labor cost points to represent a non-regional specific Base Cost Factor (BCF) using RSMeans City Cost Indexes (CCI). For example, if the cost provided from a contractor in Massachusetts for a commercial gas fryer was $3,000, than the BCF cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $3,000 / 0.98
BCF = $3,061
Alternative Data Integration
The majority of data points used in the analysis were sourced from invoices provided by Program Administrators and equipment catalogues from retailers who have previously participated in utility offered programs. Additional cost data was obtained from the following sources:
Installer Interviews: Navigant conducted three interviews with knowledgeable installers for the study. Each of the interviews produced one data point, including accurate estimates of equipment cost. These interviews also confirmed that the installation costs were the same for qualifying vs. non-qualifying equipment.
Internet-derived equipment costs: Costs for rebate-eligible Commercial Kitchen Gas Fryers were gathered through online retailers and vendor catalogues published online. Each price point for each model of equipment was given the weight of one data point. These costs were confirmed to be retail prices and as such were not marked-up.
CPUC/Itron Measure Cost Study: Itron completed a comparable incremental cost study for the California Public Utilities Commission (CPUC) that included commercial kitchen equipment in 2014. The results were published as an aggregate, meaning Navigant does not have access to the raw data points used in the study. Navigant used the CPUC/Itron results only for comparison to the Navigant results, not as a data point to be included in the cost analysis.
Material Analysis
The analysis identified and removed any potential outlier data points through the procedure described in the "Removal of Outliers" section, above. Manufacturer Specified Retail Prices (MSRP) were also removed as they are not an accurate representation of the cost of equipment on the market. This was confirmed through our installer interviews. Some invoice data received from Program Administrators were for electric and propane fryers and were excluded as the Navigant's research focused solely on natural gas fryers.
A linear regression was used to determine that there was little correlation between the size of a fryer and its cost. As a result, the analysis results are reported as the arithmetic mean on a per unit basis. Results are also reported on a per pound of shortening capacity basis for comparison to the CPUC/Itron findings, and on a per kBtu output basis. Shortening capacity is a measure of a fryer's vat size and is comparable to the production capacity units the CPUC/Itron study used. Production capacity is a measure of how much food a fryer can process in one hour, typically in units of pounds per hour. Navigant's analysis did not report results in terms of price per pound of production capacity because a fryer's production capacity is not a regularly published specification, while shortening capacity is.
Labor Analysis
Contractor interviews identified no incremental difference in the time or cost to install efficient versus baseline equipment. In general, efficient equipment took just as much time and labor to install as compared with baseline equipment, so there is no labor incremental cost associated with this measure.
Results and Findings
Navigant reported incremental cost results on a per unit, per pound of shortening capacity, and per kBtu output on the "Summary of Results" tab.
As a test of the validity of the study results, Navigant compared the results of this incremental cost study with those of a similar cost study performed by Itron for the CPUC in 2014. Both studies had the same approach in terms of focusing on new equipment rather than quantifying the impact of the used secondary market on both the baseline and efficient conditions. On a per unit basis, the results of the Navigant/NEEP study came within 1% of the results reported in the CPUC study.
Note: Restaurant franchises and fast food chains make up a significant portion of commercial kitchen equipment purchases, and NEEP PA data confirmed that restaurant franchises and fast food chains are frequent participants in energy efficiency programs, installing and receiving rebates for qualifying units. However, these restaurant suppliers refused participation in the study, and even after multiple guarantees of confidentiality, would not share their price points, leaving major market data out of the study.

## Com Fryers - Results
Commercial Gas Fryers
Data Vintage | 2014
Does this measure have incremental labor cost (Yes/No)? | No
Return to Measure Index
Base Cost Factor Results:
Non-Regional Specific Incremental Cost
Equipment Description | Incremental Cost ($/Unit) | Incremental Cost ($/lbs of Shortening Capacity) | Incremental Cost ($/kBtu)
Commercial Kitchen Fryer | 2599.4992 | 34.3528 | 24.909
Results by Market:
Market 1: Northern New England
Equipment Description | Incremental Cost ($/Unit) | Incremental Cost ($/lbs of Shortening Capacity) | Incremental Cost ($/kBtu)
Commercial Kitchen Fryer | 2536.678 | 33.5226 | 24.307
Market 2: Central/Southern New England
Equipment Description | Incremental Cost ($/Unit) | Incremental Cost ($/lbs of Shortening Capacity) | Incremental Cost ($/kBtu)
Commercial Kitchen Fryer | 2556.8674 | 33.7894 | 24.5005
Market 3: New England City
Equipment Description | Qualified Unit | Qualified Unit | Qualified Unit
Commercial Kitchen Fryer | 2620.2952 | 34.6276 | 25.1083
Market 4: New York Metro
Equipment Description | Incremental Cost ($/Unit) | Incremental Cost ($/lbs of Shortening Capacity) | Incremental Cost ($/kBtu)
Commercial Kitchen Fryer | 2671.6353 | 35.306 | 25.6002
Market 5: Upstate New York
Equipment Description | Incremental Cost ($/Unit) | Incremental Cost ($/lbs of Shortening Capacity) | Incremental Cost ($/kBtu)
Commercial Kitchen Fryer | 2564.4059 | 33.889 | 24.5727
Market 6: Mid-Atlantic
Equipment Description | Incremental Cost ($/Unit) | Incremental Cost ($/lbs of Shortening Capacity) | Incremental Cost ($/kBtu)
Commercial Kitchen Fryer | 2580.6528 | 34.1037 | 24.7284
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.97583 | 0.81533 | 0.90417
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9836 | 1.1632 | 1.0628
New England City | 3 | Boston, Providence | 1.008 | 1.2795 | 1.1275
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT | 1.0278 | 1.5593 | 1.262
NY Upstate | 5 | Buffalo, Rochester etc. | 0.9865 | 1.0135 | 0.99825
Mid-Atlantic | 6 | MD, DE, DC | 0.99275 | 0.88775 | 0.94625
National Average | - | - | 1 | 1 | 1
Summary of incremental cost data analysis for Commercial Fryers including both materials and labor. Regional adjustment factors are applied to national average incremental costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category .

## Com Infrared Heaters - README
Commercial Infrared Heaters
Return to Measure Index
Measure Characterization:
| Efficient Measure Description | Commercial Gas-fired Infrared Heater
| Baseline Description | Commercial Gas-fired Unit Heater or RTU, with 10% greater Btuh output
| Measure Scenario(s) | RET, ROB, NC
| Baseline Efficiency Levels | Unit heater, RTU, or other standard efficiency equipment with 10% greater Btuh output
| Measure Level Description | Gas-fired high-intensity or low-intensity infrared heating system
| Measure Efficiency Levels | Efficiency levels not defined for this measure
| Sizes | Up to 50,000 BTUh Greater than 50,000 BTUh up to 150,000 BTUh Greater than 150,000 BTUh up to 175,000 BTUh Greater than 175,000 BTUh
| Distinguishing Features of Efficient Measure | Low Intensity Infrared Heaters - usually forced draft or draft induced
High Intensity Infrared Heaters
| Installation Scenarios | Ceiling–mounted or hung overhead in large indoor spaces with low occupancy, like warehouses or aircraft hangars.
| Sources | MA TRM, NYSERDA, conEdison, National Grid, Mass Save, Energize CT
| Incremental Labor Cost | Yes
| Cost Basis | Incremental
| Fuel Type | Gas
| Data Vintage | 2014
Incremental Cost Study Phase Four
Published: May, 2015
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the baseline (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = ( efficient measure material cost + efficient measure installation cost ) -
( baseline material cost + baseline installation cost )
Measure: A qualifying measure is defined as the efficient alternative to the baseline option. In this case, it is defined as a commercial infrared heater.
Baseline: The baseline equipment is defined as the standard equipment that would have been installed without the utility EE activity. For purposes of this study, the baseline equipment for infrared heaters is a commercial ductless unit heater. However, some high intensity IR heater installations are add-ons to the HVAC system for instance for spot heating at the front end of a large box store. Another less likely baseline for high intensity IR heaters might be added ductwork from a rooftop unit (RTU), but the cost of this latter baseline has not been investigated for this study.
Measure Characteristics
High Intensity Infrared Heaters are usually unvented, have no draft inducing fans or other moving parts, and have a compact square or rectangular shape. Because they are unvented, they are most often installed at loading docks, near open doors or other places that are very well ventilated.
Low Intensity Infrared Heaters are usually tube-style with induced draft and venting of combustion products, all of which increase the cost of these units compared to high intensity units.
Alternative Data Integration
Navigant made every effort to obtain program data, but was only able to obtain eleven data points. These eleven data points were ultimately not used in the analysis due to uncertainties with the information provided. Only total installed cost was available and without invoices, it was unclear what was included in the total cost. As such, it was not possible to isolate material, labor, and other costs. Due to the lack of program data, it was necessary to obtain material and installation cost data through the following alternative data sources:
Internet-derived equipment costs: Costs for high intensity and low intensity Infrared Heaters gathered through web searches were marked up by 30% under the assumption that no end-user would install such equipment themselves. Rather, a contractor / installer would purchase the equipment and apply a standard markup before invoicing the customer. Each price for each model of equipment was given the weight of one data point.
Installer Interviews: Navigant conducted two interviews with knowledgeable installers for the study. The interviews produced 26 data points, one for each of a variety of equipment types and sizes. Interviews also resulted in accurate estimates of equipment costs, labor rates and labor hours for their respective territories. One interviewee was unfamiliar with high intensity infrared heaters. This interviewee supplied estimates for the cost of these high intensity units, but Navigant removed these data points from the final dataset because of their low confidence level, and since they were significantly higher cost than other similar units in the data set. (See highlighted data in the Raw Data section, and the scatterplot in the Material Analysis section of the 'Data Analysis' tab)
Summary of Results Tab
The summary of results tab presents the incremental cost for Infrared Heaters. Incremental costs are presented in seven market categories allowing NEEP members to choose the market that best represents their service territory. The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into six unique regions (seven including a Non-Regional Specific category).
Data Analysis Tab
Raw Data
A total of 250 cost points were collected from online retailers. This data was supplemented with 26 data points collected through interviews with knowledgeable installers. The one Program data extract obtained from Columbia Gas of Massachusetts had installed costs that were well outside the expected range. This could be because the projects included the installation of several heaters, but without knowing the actual number of heaters installed, Navigant was unable to use this data. Two duplicate models with different price points from the same web retailer were found. In this case the duplicate items were averaged in the analysis.
Formatted Data
Primary cost data was collected from online retailers and contractors based in Massachusetts. Due to the inherent differences in cost from one region to another, Navigant adjusted all material and labor cost points to represent a non-regional specific Base Cost Factor (BCF) using RSMeans City Cost Indexes (CCI). For example, if the cost provided from a contractor in Massachusetts for a high intensity Infrared Heater was $5,000, then the BCF would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $5,000 / 0.98
BCF = $5,102
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data. A linear regression was used to develop the material cost for the measure. A regression was done for the following equipment types:
a) Baseline Unit Heater
b) High Intensity Infrared Heater
c) Low Intensity Infrared Heater
A baseline factor was applied to adjust for greater capacity required for a unit heater to match that of a high intensity or low intensity Infrared Heater.
Labor Analysis
Contractor interviews identified minimal difference in the time to install efficient versus baseline equipment, however one contractor identified a 10% increase in time required to install a gas unit heater due to it being a little more complex to install. In general, high intensity and low intensity units took just as much time to install. With all of these findings indicating little or no difference in labor costs between the baseline and efficient cases, labor costs were a non-factor in the final incremental cost calculation.
Results
Navigant defined the unit size categories to line up with the size categories used by program administrators offering Infrared Heater incentives. Results are presented for each of those size categories at a non-regional specific level. These results are summarized on the "Summary of Results" tab. The incremental cost presented is for total installation cost which includes both material and labor costs. However since it was determined that there was little difference in installation labor costs between the baseline and qualifying equipment, the incremental cost becomes the marked up equipment and materials cost.
One significant finding of this study is the negative incremental cost of the high intensity Infrared Heaters. This may be explained by the fact that IR Heaters achieve savings in part by being providing the same level of comfort using a lower btuh input. They also do not require any large fans like the baseline equipment does, further reducing costs.
High Intensity IR Heaters are usually unvented, have no draft inducing fans or other moving parts, and have a compact shape, resulting in a lower cost, and a negative incremental cost compared to a larger output, fan-driven unit heater. Low intensity units on the other hand, are usually tube-style with induced draft and venting of combustion products, all features which increase the cost of these units compared to high intensity units. It should be noted that because they are unvented, High Intensity IR Heaters are often not appropriate for indoor applications which may explain the scarcity of Program data for this type of equipment. It may also explain why only one PA offered rebates for High Intensity Infrared Heaters.

## Com Infrared Heaters - Results
Commercial Infrared Heater
Data Vintage | 2014
Does this measure have incremental labor cost (Yes/No)? | Yes
Return to Measure Index
Base Cost Factor Results:
Size Category | Non Regional Specific Incremental Cost
| High Intensity | Low Intensity
Up to 50,000 BTUh | -295.3766 | 469.5776
Greater than 50,000 BTUh up to 150,000 BTUh | -278.3925 | 422.0193
Greater than 150,000 BTUh up to 175,000 BTUh | -263.8346 | 381.2551
Greater than 175,000 BTUh | -254.1294 | 354.079
Results by Market:
Size Category | Market 1 Northern New England Incremental Cost
| High Intensity | Low Intensity
Up to 50,000 BTUh | -288.2383 | 458.2294
Greater than 50,000 BTUh up to 150,000 BTUh | -271.6646 | 411.8205
Greater than 150,000 BTUh up to 175,000 BTUh | -257.4586 | 372.0415
Greater than 175,000 BTUh | -247.988 | 345.5221
Size Category | Market 2 Central/Southern New England Incremental Cost
| High Intensity | Low Intensity
Up to 50,000 BTUh | -290.5324 | 461.8765
Greater than 50,000 BTUh up to 150,000 BTUh | -273.8268 | 415.0982
Greater than 150,000 BTUh up to 175,000 BTUh | -259.5077 | 375.0026
Greater than 175,000 BTUh | -249.9617 | 348.2721
Size Category | Market 3 New England City Incremental Cost
| High Intensity | Low Intensity
Up to 50,000 BTUh | -297.7396 | 473.3342
Greater than 50,000 BTUh up to 150,000 BTUh | -280.6196 | 425.3955
Greater than 150,000 BTUh up to 175,000 BTUh | -265.9453 | 384.3052
Greater than 175,000 BTUh | -256.1625 | 356.9116
Size Category | Market 4 NY Metro Incremental Cost
| High Intensity | Low Intensity
Up to 50,000 BTUh | -303.5733 | 482.6084
Greater than 50,000 BTUh up to 150,000 BTUh | -286.1178 | 433.7304
Greater than 150,000 BTUh up to 175,000 BTUh | -271.156 | 391.835
Greater than 175,000 BTUh | -261.1815 | 363.9047
Size Category | Market 5 NY Upstate Incremental Cost
| High Intensity | Low Intensity
Up to 50,000 BTUh | -291.389 | 463.2383
Greater than 50,000 BTUh up to 150,000 BTUh | -274.6342 | 416.3221
Greater than 150,000 BTUh up to 175,000 BTUh | -260.2729 | 376.1082
Greater than 175,000 BTUh | -250.6987 | 349.2989
Size Category | Market 5 NY Upstate Incremental Cost
| High Intensity | Low Intensity
Up to 50,000 BTUh | -293.2351 | 466.1731
Greater than 50,000 BTUh up to 150,000 BTUh | -276.3741 | 418.9597
Greater than 150,000 BTUh up to 175,000 BTUh | -261.9218 | 378.491
Greater than 175,000 BTUh | -252.287 | 351.5119
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.97583 | 0.81533 | 0.90417
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9836 | 1.1632 | 1.0628
New England City | 3 | Boston, Providence | 1.008 | 1.2795 | 1.1275
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT | 1.0278 | 1.5593 | 1.262
NY Upstate | 5 | Buffalo, Rochester etc. | 0.9865 | 1.0135 | 0.99825
Mid-Atlantic | 6 | MD, DE, DC | 0.99275 | 0.88775 | 0.94625
National Average | - | - | 1 | 1 | 1
Summary of incremental cost data analysis for commercial Infrared Heaters including both materials and labor. Regional adjustment factors are applied to national average incremental costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category.

## Com Lighting Ctrls - README
Commercial Lighting Controls
Return to Measure Index
Measure Characterization:
| Measure Description | Lighting controls, timers, and sensors installed
| Baseline Description | No lighting controls, timers, or sensors installed
| Measure Scenario(s) | RET, NC
| Baseline Efficiency Levels | N/A
| Efficient Measure Description & Specifications | Lighting controls, timers, and sensors installed
| Sizes | N/A
| Distinguishing Features | N/A
| Installation Scenarios | Ceiling, wall
| Sources | Northeast Utilities
| Incremental Labor Cost | Yes - Full labor cost
| Cost Basis | Full
| Fuel Type | Electric
| Data Vintage | 2011
Incremental Cost Study Phase One
Published: September, 2011
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the standard (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = measure material cost - base case material cost
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as commercial lighting controls, either daylighting/photocells, occupancy sensors, and/or timers.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity. The baseline equipment in this instance is the lack of a lighting control.
Results Tab
The presents the incremental cost for commercial lighting controls. Material, labor, and installed incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis
Raw Data
A total of 5 contractor interviews were completed for the analysis of the measure a total of 278 on-line cost points were collected.
Five contractor interviews were conducted for the analysis of the on-line data collection verification.
Formatted Data
Primary cost data was collected as national data and verification from contractors across one state (CT). Due to the inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent non-regional specific (NRS) data using RSMeans CCI. Table 1 provides a regional break down of the NEEP. For example, if the cost provided from a contractor in New York Metro for an indirect water heater was $1000, than the NRS cost would be:
NRS = Original State Cost ($) / Average Adjustment Factor for Original State
NRS = $1000 / 1.26
NRS = $793.65
The same method was used to adjust all labor cost.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data.
A simple average was used to develop the material cost for internet data. A percent difference was calculated between the internet cost data and the contractor interview data. The average percent difference for each technology type was then applied to the internet cost .
Labor Analysis
Frequently, lighting control devices are installed at the time of a retrofit or within a lighting fixture, making it difficult to assess the true incremental time for installation. Overall, the labor costs did not play a significant role in the overall cost of the measure.
Results
Through contractor interviews, Navigant defined the most common control devices. As such, results are presented for each of those technologies on separate analysis tabs; defined all categories at a non-regional specific level.

## Com Lighting Ctrls - Results
Commercial Lighting Controls
Data Vintage | 2011
Does this measure have incremental labor cost (Yes/No)? | No
Return to Measure Index
Photocontrols |  |  |  | Timers |  | Occupancy Sensors
Base Cost Factor Results:
Type | Base Cost Factor ($/Unit) |  | Type | Non Regional Specific Incremental Cost ($/Unit) | Type | Non Regional Specific Incremental Cost ($/Unit)
Fixed Photocontrol | 105.0909 |  | Electronic | 390.2115 | Passive Infrared - Ceiling | 239.295
Turn-Lock Photocontrol | 159.9606 |  | Digital | 256.4283 | Passive Infrared - Wall | 108.1638
Wired-in Photocontrol | 99.604 |  | Switch | 497.2705 | Passive Infrared and Ultrasonic - Ceiling | 229.8755
Screw-in Photocontrol | 108.4021 |  |  |  | Passive Infrared and Ultrasonic - Wall | 161.5936
Swivel Photocontrol | 114.4039
Button Photocontrol | 103.4059
Shorting Cap Photocontrol | 109.5115
Results by Market:
Type | Market 1 Northern New England Incremental Cost ($/Unit) |  | Type | Market 1 Northern New England Incremental Cost ($/Unit) | Type | Market 1 Northern New England Incremental Cost ($/Unit)
Fixed Photocontrol | 89.4324 |  | Electronic | 332.07 | Passive Infrared - Ceiling | 233.0095
Turn-Lock Photocontrol | 136.1265 |  | Digital | 218.2205 | Passive Infrared - Wall | 106.18
Wired-in Photocontrol | 84.763 |  | Switch | 423.1772 | Passive Infrared and Ultrasonic - Ceiling | 239.4015
Screw-in Photocontrol | 92.2502 |  |  |  | Passive Infrared and Ultrasonic - Wall | 168.9936
Swivel Photocontrol | 97.3577
Button Photocontrol | 87.9984
Shorting Cap Photocontrol | 93.1943
Type | Market 2 Central/Southern New England Incremental Cost ($/Unit) |  | Type | Market 2 Central/Southern New England Incremental Cost ($/Unit) | Type | Market 2 Central/Southern New England Incremental Cost ($/Unit)
Fixed Photocontrol | 110.6187 |  | Electronic | 410.7366 | Passive Infrared - Ceiling | 288.2089
Turn-Lock Photocontrol | 168.3746 |  | Digital | 269.9164 | Passive Infrared - Wall | 131.3338
Wired-in Photocontrol | 104.8432 |  | Switch | 523.4269 | Passive Infrared and Ultrasonic - Ceiling | 296.1151
Screw-in Photocontrol | 114.1041 |  |  |  | Passive Infrared and Ultrasonic - Wall | 209.0278
Swivel Photocontrol | 120.4216
Button Photocontrol | 108.8451
Shorting Cap Photocontrol | 115.2719
Type | Market 3 New England City Incremental Cost ($/Unit) |  | Type | Market 3 New England City Incremental Cost ($/Unit) | Type | Market 3 New England City Incremental Cost ($/Unit)
Fixed Photocontrol | 117.1764 |  | Electronic | 435.0858 | Passive Infrared - Ceiling | 305.2944
Turn-Lock Photocontrol | 178.3561 |  | Digital | 285.9176 | Passive Infrared - Wall | 139.1195
Wired-in Photocontrol | 111.0585 |  | Switch | 554.4566 | Passive Infrared and Ultrasonic - Ceiling | 313.6694
Screw-in Photocontrol | 120.8684 |  |  |  | Passive Infrared and Ultrasonic - Wall | 221.4193
Swivel Photocontrol | 127.5604
Button Photocontrol | 115.2976
Shorting Cap Photocontrol | 122.1054
Type | Market 4 NY Metro Incremental Cost ($/Unit) |  | Type | Market 4 NY Metro Incremental Cost ($/Unit) | Type | Market 4 NY Metro Incremental Cost ($/Unit)
Fixed Photocontrol | 131.968 |  | Electronic | 490.0081 | Passive Infrared - Ceiling | 343.8327
Turn-Lock Photocontrol | 200.8706 |  | Digital | 322.0098 | Passive Infrared - Wall | 156.681
Wired-in Photocontrol | 125.0777 |  | Switch | 624.4474 | Passive Infrared and Ultrasonic - Ceiling | 353.2649
Screw-in Photocontrol | 136.126 |  |  |  | Passive Infrared and Ultrasonic - Wall | 249.3698
Swivel Photocontrol | 143.6627
Button Photocontrol | 129.852
Shorting Cap Photocontrol | 137.5191
Type | Market 5 NY Upstate Incremental Cost ($/Unit) |  | Type | Market 5 NY Upstate Incremental Cost ($/Unit) | Type | Market 5 NY Upstate Incremental Cost ($/Unit)
Fixed Photocontrol | 103.9087 |  | Electronic | 385.8216 | Passive Infrared - Ceiling | 270.7263
Turn-Lock Photocontrol | 158.1611 |  | Digital | 253.5435 | Passive Infrared - Wall | 123.3672
Wired-in Photocontrol | 98.4835 |  | Switch | 491.6762 | Passive Infrared and Ultrasonic - Ceiling | 278.153
Screw-in Photocontrol | 107.1826 |  |  |  | Passive Infrared and Ultrasonic - Wall | 196.3483
Swivel Photocontrol | 113.1169
Button Photocontrol | 102.2426
Shorting Cap Photocontrol | 108.2795
Type | Market 6 Mid-Atlantic Incremental Cost ($/Unit) |  | Type | Market 6 Mid-Atlantic Incremental Cost ($/Unit) | Type | Market 6 Mid-Atlantic Incremental Cost ($/Unit)
Fixed Photocontrol | 96.1845 |  | Electronic | 357.1411 | Passive Infrared - Ceiling | 250.6015
Turn-Lock Photocontrol | 146.404 |  | Digital | 234.696 | Passive Infrared - Wall | 114.1965
Wired-in Photocontrol | 91.1626 |  | Switch | 455.1268 | Passive Infrared and Ultrasonic - Ceiling | 257.4761
Screw-in Photocontrol | 99.2151 |  |  |  | Passive Infrared and Ultrasonic - Wall | 181.7525
Swivel Photocontrol | 104.7082
Button Photocontrol | 94.6423
Shorting Cap Photocontrol | 100.2304
Market | Market Code | Regions |  | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH |  | 0.851
Central/Southern New England | 2 | MA (exc Boston), RI, most CT |  | 1.0526
New England City | 3 | Boston, Providence |  | 1.115
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT |  | 1.2557
NY Upstate | 5 | Buffalo, Rochester etc. |  | 0.98875
Mid-Atlantic | 6 | MD, DE, DC |  | 0.91525
National Average | - | - |  | 1
Summary of incremental cost data analysis for Commercial Lighting Controls. Regional adjustment factors are applied to national average incremental costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category.

## Economizers - README
Economizers
Return to Measure Index
Measure Characterization:
| Measure Description | Economizer with Dual Enthalpy Controls
| Baseline Description | Air economizers only. Scenarios: No Economizer vs. Dual Enthalpy Air Economizer
| Measure Scenario(s) | RET, NC
| Baseline Efficiency Levels | N/A
| Measure Level Description | New or replacement HVAC installations with Dual Enthalpy Air Economizer
| Measure Efficiency Levels | Currently only incentives offered for dual enthalpy economizer controls
| Sizes | For 5 ton to 70 ton HVAC units
| Distinguishing Features | Economizer with Dual enthalpy controls
| Installation Scenarios | Rooftop or Inside building only
| Sources | Interviews from MA, NY, RI, and CT
| Incremental Labor Cost | Yes - Full labor cost
| Cost Basis | Incremental, Full
| Fuel Type | Electric
| Data Vintage | 2012
Incremental Cost Study Phase Two
Published: January, 2013
Incremental Cost Methodology
Full Measure Costs are used where the scenario assumes that there is no alternative measure .
Incremental Measure Costs are used when an energy-efficient appliance or measure promoted through a program is installed in lieu of the standard (less efficient) appliance/measure. The incremental cost is the difference between the baseline energy efficiency measure (material and labor) and the standard efficiency model. The equation for calculating incremental measure costs is simply:
Incremental measure cost = energy efficient measure cost (material + labor) - standard efficient baseline cost (material + labor)
In some cases there is no difference in the installation cost between the standard and efficient measure and/or an efficient measure and a more efficient measure. In those cases only materials costs are provided in the incremental cost.
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as a dual enthalpy economizer.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity . There are two baseline scenarios in this instance. Scenario A: Existing HVAC equipment without Economizer has Dual-Enthalpy Economizer installed. Scenario B: Existing HVAC equipment with single (dry-bulb) Economizer has Dual-Enthalpy Controls installed.
Incremental path: This analysis assumes that the end-user's HVAC system fails and decides to either replace HVAC system either with the economizer installed or not. The end user can further install dual enthalpy controls to take advantage of utility rebates, as opposed to just single enthalpy control that comes standard with economizers.
Results Tab
The tab presents the incremental cost for the HVAC system. Material, labor, and installed incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
Since the measure(s) are offered as an add-on feature to the HVAC system, there were several comments from manufacturers and contractors on pricing strategies and product availability which have been summarized in this section.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis
Raw Data
A total of 11 contractor interviews and 5 HVAC manufacturer interviews were completed for the analysis of the measure. A total of 53 cost points were collected for combination equipment.
Formatted Data
Primary cost data was collected from contractors across four states (MA, NY, RI, and CT). Due to the inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent the Base Cost Factors (BCF) using RSMeans CCI. Table 1 provides a regional break down of NEEP. For example, if the cost provided from a contractor in New York Metro for a combination unit was $2,000, than the BCF cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $2,000 / 1.26
BCF = $1,592.67
The same method was used to adjust all labor costs.
Similarly, once BCF costs were determined for each measure, the costs were then allocated to each market by multiplying the BCF cost by the individual market factor.
The R.S. Means recalculated CCI factors annually. For this study, Navigant used the 2012 CCI factors. Additionally, any older data, collected for the ICS Phase One Report or other sources , was updated with the 2012 factors to maintain comparability with data collected in 2012 for the ICS Phase Two.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data.
A linear regression was used to develop the material cost for the measure. A regression was done for the entire range of efficiencies and HVAC system capacities.
Labor Analysis
While installing a dry-bulb economizer takes additional labor time, all contractors and manufacturers mentioned that they do not charge these labor costs to the customer. However, contractor interviews identified that it took approximately 0.82 hours to install dual enthalpy economizer controls, and that this labor cost does get charged to the customer. Finally, the labor rate was calculated with a weighted average of all contractor labor rates ($/Hr) collected for the study.
Results
Through contractor and distributor interviews, Navigant defined the most common unit sizes installed. As such, results are presented for each of those size categories at a non-regional specific level.

## Economizers - Results
Economizers
Data Vintage | 2012
Does this measure have incremental labor cost (Yes/No)? | Yes
Return to Measure Index
Base Cost Factor Results:
SCENARIO A |  |  |  |  | SCENARIO B
Base Cost Factor Total Costs |  |  |  |  | Base Cost Factor Total Costs
HVAC System Capacity (Tons) | Single Enthalpy Economizer | Dual Enthalpy Economizer Controls | Measure Total |  | HVAC System Capacity (Tons) | Dual Enthalpy Control | Dual Enthalpy Control Installation | Measure Total
5 | 772.9034 | 178.1024 | 951.0059 |  | 5 | 106.2612 | 71.8412 | 178.1024
15 | 1266.8732 | 251.0967 | 1517.97 |  | 15 | 179.2555 | 71.8412 | 251.0967
25 | 1760.8431 | 324.091 | 2084.9341 |  | 25 | 252.2498 | 71.8412 | 324.091
40 | 2501.7978 | 433.5824 | 2935.3802 |  | 40 | 361.7412 | 71.8412 | 433.5824
70 | 3983.7073 | 652.5652 | 4636.2725 |  | 70 | 580.724 | 71.8412 | 652.5652
Results by Market:
SCENARIO A |  |  |  |  | SCENARIO B
Market 1 Northern New England Results |  |  |  |  | Market 1 Northern New England Results
HVAC System Capacity (Tons) | Single Enthalpy Economizer | Dual Enthalpy Economizer Controls | Measure Total |  | HVAC System Capacity (Tons) | Dual Enthalpy Control | Dual Enthalpy Control Installation | Measure Total
5 | 757.4454 | 153.7064 | 911.1518 |  | 5 | 104.136 | 49.5704 | 153.7064
15 | 1241.5358 | 225.2408 | 1466.7766 |  | 15 | 175.6704 | 49.5704 | 225.2408
25 | 1725.6262 | 296.7752 | 2022.4014 |  | 25 | 247.2048 | 49.5704 | 296.7752
40 | 2451.7619 | 404.0768 | 2855.8387 |  | 40 | 354.5064 | 49.5704 | 404.0768
70 | 3904.0331 | 618.68 | 4522.7131 |  | 70 | 569.1095 | 49.5704 | 618.68
SCENARIO A |  |  |  |  | SCENARIO B
Market 2 Central/Southern New England Results |  |  |  |  | Market 2 Central/Southern New England Results
HVAC System Capacity (Tons) | Single Enthalpy Economizer | Dual Enthalpy Economizer Controls | Measure Total |  | HVAC System Capacity (Tons) | Dual Enthalpy Control | Dual Enthalpy Control Installation | Measure Total
5 | 765.1744 | 186.3792 | 951.5536 |  | 5 | 105.1986 | 81.1806 | 186.3792
15 | 1254.2045 | 258.6435 | 1512.848 |  | 15 | 177.463 | 81.1806 | 258.6435
25 | 1743.2346 | 330.9078 | 2074.1425 |  | 25 | 249.7273 | 81.1806 | 330.9078
40 | 2476.7798 | 439.3043 | 2916.0842 |  | 40 | 358.1238 | 81.1806 | 439.3043
70 | 3943.8702 | 656.0973 | 4599.9676 |  | 70 | 574.9168 | 81.1806 | 656.0973
SCENARIO A |  |  |  |  | SCENARIO B
Market 3 New England City Results |  |  |  |  | Market 3 New England City Results
HVAC System Capacity (Tons) | Single Enthalpy Economizer | Dual Enthalpy Economizer Controls | Measure Total |  | HVAC System Capacity (Tons) | Dual Enthalpy Control | Dual Enthalpy Control Installation | Measure Total
5 | 780.6325 | 196.4069 | 977.0394 |  | 5 | 107.3239 | 89.0831 | 196.4069
15 | 1279.542 | 270.1312 | 1549.6731 |  | 15 | 181.0481 | 89.0831 | 270.1312
25 | 1778.4515 | 343.8554 | 2122.3069 |  | 25 | 254.7723 | 89.0831 | 343.8554
40 | 2526.8158 | 454.4417 | 2981.2575 |  | 40 | 365.3586 | 89.0831 | 454.4417
70 | 4023.5444 | 675.6144 | 4699.1587 |  | 70 | 586.5313 | 89.0831 | 675.6144
SCENARIO A |  |  |  |  | SCENARIO B
Market 4 NY Metro Results |  |  |  |  | Market 4 NY Metro Results
HVAC System Capacity (Tons) | Single Enthalpy Economizer | Dual Enthalpy Economizer Controls | Measure Total |  | HVAC System Capacity (Tons) | Dual Enthalpy Control | Dual Enthalpy Control Installation | Measure Total
5 | 796.0905 | 220.8029 | 1016.8935 |  | 5 | 109.4491 | 111.3539 | 220.8029
15 | 1304.8794 | 295.987 | 1600.8665 |  | 15 | 184.6332 | 111.3539 | 295.987
25 | 1813.6684 | 371.1711 | 2184.8395 |  | 25 | 259.8173 | 111.3539 | 371.1711
40 | 2576.8517 | 483.9473 | 3060.799 |  | 40 | 372.5934 | 111.3539 | 483.9473
70 | 4103.2185 | 709.4996 | 4812.7181 |  | 70 | 598.1457 | 111.3539 | 709.4996
SCENARIO A |  |  |  |  | SCENARIO B
Market 5 NY Upstate Results |  |  |  |  | Market 5 NY Upstate Results
HVAC System Capacity (Tons) | Single Enthalpy Economizer | Dual Enthalpy Economizer Controls | Measure Total |  | HVAC System Capacity (Tons) | Dual Enthalpy Control | Dual Enthalpy Control Installation | Measure Total
5 | 765.1744 | 177.0398 | 942.2142 |  | 5 | 105.1986 | 71.8412 | 177.0398
15 | 1254.2045 | 249.3042 | 1503.5087 |  | 15 | 177.463 | 71.8412 | 249.3042
25 | 1743.2346 | 321.5685 | 2064.8031 |  | 25 | 249.7273 | 71.8412 | 321.5685
40 | 2476.7798 | 429.965 | 2906.7448 |  | 40 | 358.1238 | 71.8412 | 429.965
70 | 3943.8702 | 646.758 | 4590.6282 |  | 70 | 574.9168 | 71.8412 | 646.758
SCENARIO A |  |  |  |  | SCENARIO B
Market 6 Mid-Atlantic Results |  |  |  |  | Market 6 Mid-Atlantic Results
HVAC System Capacity (Tons) | Single Enthalpy Economizer | Dual Enthalpy Economizer Controls | Measure Total |  | HVAC System Capacity (Tons) | Dual Enthalpy Control | Dual Enthalpy Control Installation | Measure Total
5 | 772.9034 | 170.1999 | 943.1033 |  | 5 | 106.2612 | 63.9387 | 170.1999
15 | 1266.8732 | 243.1942 | 1510.0674 |  | 15 | 179.2555 | 63.9387 | 243.1942
25 | 1760.8431 | 316.1885 | 2077.0315 |  | 25 | 252.2498 | 63.9387 | 316.1885
40 | 2501.7978 | 425.6799 | 2927.4777 |  | 40 | 361.7412 | 63.9387 | 425.6799
70 | 3983.7073 | 644.6627 | 4628.37 |  | 70 | 580.724 | 63.9387 | 644.6627
Market | Market Code | Example | Material Adj Factor | Labor Adj Factor | Average Adj Factor
Northern New England | 1 | ME, VT, NH | 0.98 | 0.69 | 0.835
Central/Southern New England | 2 | MA exc Boston, RI, most CT | 0.99 | 1.13 | 1.06
New England City | 3 | Boston, Providence | 1.01 | 1.24 | 1.125
NY Metro | 4 | NYC, metro suburbs Southwest CT | 1.03 | 1.55 | 1.29
NY Upstate | 5 | Buffalo, Rochester etc. | 0.99 | 1 | 0.995
Mid-Atlantic | 6 | MD, DE DC | 1 | 0.89 | 0.945
Base Cost Factor | - | - | 1 | 1 | 1
Summary of incremental cost data analysis for Economizers. Regional adjustment factors are applied to the base cost factors to calculate market specific results. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category.
Note: Results are presented for two baseline scenarios. Scenario A: Existing HVAC equipment without Economizer has Dual-Enthalpy Economizer installed. Scenario B: Existing HVAC equipment with single (dry-bulb) Economizer has Dual-Enthalpy Controls installed.
Comments from Contractors/HVAC Manufacturers:
1. Most HVAC units over 20 tons come with economizer installed and therefore it is very difficult to find pricing information on higher capacity economizers. Very few after-market options exist for dry-bulb economizers for units greater than 30 tons.
2. No manufacturer interviewed charges end user for any additional installation costs associated with installing economizers for new HVAC system purchase.
3. IECC 2009 required all HVAC units with capacities greater than 5.40 tons to have economizers installed as part of the unit. Since Massachusetts has adopted the economizer requirements for HVAC systems as part of their building code, there may be other states, and/or municipalities that have adopted similar building codes.
4. All manufacturers mentioned that the incremental installation time for dual enthalpy controls does not depend on the size of the HVAC unit. Therefore, only the average labor cost was used for all capacities.
5. The interviews also found that the pricing of dual-enthalpy controls was highly influenced by incentive programs. Since both economizers, and dual-enthalpy controls, are offered as an add-on to an HVAC unit, the pricing of these items depends greatly on the pricing strategy adopted by manufacturers for other components of the system. Some manufacturers charge a higher price for the dual-enthalpy controls while reducing the cost of the economizer, while others charge less for controls, and more for the economizer.
6. Some HVAC manufacturers have a higher price on the HVAC system, but charge very low prices for both economizer and controls in order to win bids.
7. One manufacturer and one contractor mentioned that since there is currently no incentive on installing dry-bulb economizers, the utility incentive for dual-enthalpy controls plays an important role in incentivizing users to install economizers on HVAC units of less than 10 tons.
8. All manufacturers and contractors mentioned that installing an economizer is a decision made at the time of installing a new HVAC system.

## Evap Fan Contols - README
Evaporator Fan Controls
Return to Measure Index
Measure Characterization:
| Efficient Measure Description | Refrigeration Evaporator Fan Controls installed in walk-in coolers or freezers to turn off or reduce the speed of evaporator fans when the compressor is not running.
| Baseline Description | Uncontrolled Evaporator Fans running continuously at full speed.
| Measure Scenario(s) | Retrofit (RET) only
| Baseline Efficiency and Specifications | 8760 Hours, Continuous, Uncontrolled operation of Evaporator Fans
| Efficient Measure Description & Specifications | Evaporator Fan Controls installed in walk-in coolers or freezers save energy by turning off ('On/Off controls'), or reducing the speed of ('Two-Speed controls') evaporator fans when the refrigeration compressor is not running, reducing the fan energy usage as well as the heat load on the refrigeration system from the fan motor. 'Savings from reduced fan run-time and reduced cooling load from fan waste heat. Based on applicable TRMs, annual runtime is typically reduced from 8,760 hours per year (continuous operation) to 4,072 hours per year for both Freezers and Coolers.
| Sizes | Per fan controlled (BGE, PEPCO, National Grid), per controller (Efficiency VT, Efficiency ME, DC SEU), or per refrigeration unit (PSEGLI) [Note: Controllers for 3-phase circuits, large amperage and horsepower not included in this characterization]
| Distinguishing Features | Two control types: (1) On/off control based on the compressor cycle (most common) sometimes coupled with a small PSC or ECM circulator fan that goes on when the evaporator fans go off. (2) Two-speed controls that run the evaporator fans at low speed when the compressor is off. This approach does not require a circulator fan.
| Installation Scenarios | Retrofit (RET) only. Typical Building Types: Grocery Store, Convenience Store, Restaurant Central control based on sensing temperature differential across the evaporator coil or compressor run cycle.
| Incentive Approaches | VT (EVT): - Minimum four fans or 250 watts per control. - Controls must ensure fan energy is reduced by 70% when no refrigerant flows through the evaporator.[1] NH (PSNH, Unitil, Liberty): No Prescriptive Incentive Offered; Custom incentives available. ME (Efficiency Maine): No Control Approach Specified, Incentive offered per controller MA & RI (National Grid): ECM [fans] - Low and Medium Temperature. [2] CT (Groton Utilities): No Control Approach Specified, Custom incentive offered at $0.14 per kWh saved. NY (ConEd): Custom incentive offered at $0.16 per kWh saved. NY (PSEGLI): - Minimum fan load of 1/20 horsepower operating continuously at full speed - Must reduce fan motor power by at least 75 percent when the compressor(s) cycle off MD (BGE): - Must control a minimum fan load of 1/20 horsepower where the fan(s) operate continuously at full speed. - Must reduce fan motor power by at least 75% during the compressor off-cycle. [3] D.C. (D.C. SEU): - must turn off a minimum of 4 evaporator fans at least 70% of the time the compressor is not running, - must reduce the airflow of evaporator fans when compressor cycles off or while no refrigerant flows through the evaporator, and - must control a minimum fan load of 1/20 horsepower when the fans operate continuously at full speed. [4] Massave: Small Business D.I. Program [5]
| Sources | [1] https://www.efficiencyvermont.com/For-My-Business/Ways-To-Save-and-Rebates/Refrigeration-Controls/single-item/index/evaporator-fan-motor-controls
[2] http://www.energysmartgrocer.org/ne/documents/NationalGrid-IncentiveWorksheet-IncentiveList.pdf
[3] https://www.bgesmartenergy.com/sites/bge/files/BGE_IC_Application_Kitchen_Refrig_Incentives.pdf
[4] https://www.dcseu.com/docs/business/techspec/DCSEU-TECHSPEC-Refrigeration.pdf
[5] http://www.masssave.com/business/incentives/Small-Midsize-Business-Direct-Install
| Incremental Labor Cost | Yes - Full labor cost
| Cost Basis | Full
| Fuel Type | Electric
| Data Vintage | 2014
Incremental Cost Study Phase Four
Published: May, 2015
Incremental Cost Methodology
Incremental measure costs are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the standard (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = ( efficient measure material cost + efficient measure installation cost ) -
( baseline material cost + baseline installation cost )
In the case of the Evaporator Fan Controls measure, the baseline is no control, so the base case material and labor cost is zero, and the formula becomes:
Incremental measure cost = efficient measure material cost + efficient measure installation cost
Qualifying Measure: A qualifying measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as a retrofitted Evaporator fan control installed in walk-in coolers or freezers that turns off or reduces the speed of evaporator fans when the compressor is not running.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity. The baseline in this instance is a walk-in cooler or freezer where there is no fan control, i.e. the evaporator fans run continuously.
Types of Evaporator Fan Controls There are two types of Evaporator Fan Controls, On/Off and Two-speed Controls. Both types can use either a pair of sensors to detect a temperature difference across the evaporator coil, or an amperage sensor to detect the compressor cycling.
(1) On/off control will turn all but one or two evaporator fans off when the compressor cycles off. These controls can sometimes be coupled with a small PSC or ECM circulator fan that goes on when the compressor cycles off, and in this case, the control can turn all the evaporator fans off.
(2) Two-speed controls will run the evaporator fans at low speed when the compressor is off. This approach does not require a circulator fan.
Note: Navigant's research revealed that the only controls using the On/Off control method were complex control modules - or more accurately, refrigeration management systems - that have numerous additional capabilities including control of the compressor cycle, the defrost cycle, the door heaters, the evaporator fans, outdoor air economizer and more. These controls use complex control algorithms using many more inputs than just a compressor cycle sensor (either delta-T or amp sensor), and they can control higher amperage than the stand alone EFCs. These controls can also log the various control parameters over time like an Energy Management System.
Since these units are not directly comparable to the conventional stand-alone Evaporator Fan Controls as characterized, they were not included in the overall cost analysis. It would be difficult if not impossible to disaggregate the cost of the EFC capabilities from the total installed cost for these complex units. However, we have presented a cost range on the "Summary of Results" tab that is our best estimate of the range of equipment and installation costs for these types of controls which are highly variable in their complexity and capabilities.
Scrubbing of data: Data points were removed from the raw data set for any of the following reasons (also see Alternative Data Integration, below):
- cost data couldn't be disaggregated from overall invoice cost
- no clear cost data available
- CPUC/Itron cost study data [This data used only for comparison]
- equipment was designed for use with three phase power [costs were generally 2 to 3 times higher for these units]
- cost data for multifunctional controls that include EFC (see note above)
Removal of outliers: Two different methodologies for determining outliers are presented in the Material and Labor Cost Analysis section of the Data Analysis tab. Those two methodologies are:
- removing data points a certain number of standard deviations either side of the arithmetic mean. In this case 1.5 standard deviations was chosen rather than the standard two standard deviations since the latter would not have identified any outliers.
- removing the data in the top and bottom deciles (10 percentiles) of the data distribution.
Each of these methods has a significant effect on the results. The standard deviation method decreases the average total cost by 10%, and the decile method increases the result by 17%. The results reported on the Summary of Results tab use both the decile method and the standard deviation method to remove outliers. After removing outliers identified using both methods, the resulting average cost increased by 4%.
Our data did not include enough usable data points for On/off type controls to yield a representative result, so only cost data for two-speed type controls are included in the analysis. (See Note, above).
Alternative Data Integration
The following alternative data sources were used to inform the final result of this study:
- Internet-derived equipment costs: Costs for rebate-eligible Evaporator Fan Controllers gathered through internet searches were marked up by 34% and average labor costs added under the assumption that no end-user would install such equipment themselves. Rather, it is assumed that a contractor / installer would purchase and install the equipment and apply a standard markup before invoicing the customer. The 34% markup was a rough average of estimates from interviews, the CPUC/Itron study, and other sources. Each price for each model of equipment was given the weight of one data point.
- CPUC/Itron Measure Cost Study: The Itron study, done on behalf of the California Public Utility Commission, produced a cost for Evaporator Fan Controls including Evaporator Fan Motor replacements as one measure and reported as a cost per evaporator fan. The cost of the motor replacements and an estimate of the labor required to replace them was deducted from the Itron measure cost to calculate a comparable measure cost to the Navigant study. This derived cost was used only for comparison to the Navigant results, not as a data point to be included in the cost calculation itself. See the 'CPUC Itron data' tab for details
- Installer Interviews: Navigant conducted three interviews with knowledgeable installers for the study. Each of the interviews represented one data point, including accurate estimates of equipment cost and labor hours. Where necessary those labor hours were combined with prevailing labor rates from RS Means to generate labor cost estimates for other data points that were not broken out into labor and materials and to derive a total installed cost for Internet-derived equipment costs (see above).
- Contract pricing: For three of the PA territories where we were able to obtain data, the pricing of EFC installations was extremely regular, indicating a negotiated contract price for an approved installer. This finding was confirmed with the respective PAs. These data sets were distilled down to one data point for each contract territory using the average material and labor costs for that data set. The cost was also discounted by 20% as an estimate of the contract administration, marketing and outreach budget included in those contract prices.
Summary of Results Tab
The summary of results tab presents the incremental cost for the Evaporator Fan Controls measure after outliers were removed as described in the Removal of Outliers section, above. In this case, the incremental cost is simply the full installed cost of an Evaporator Fan control. There are no size or capacity categories for this measure.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into six unique regions (seven, including a Non-Regional Specific category).
Data Analysis Tab
Raw Data
Navigant completed three in-depth interviews with installers and contractors to understand the typical installation practices and associated costs for the Evaporator Fan Controls measure. A total of 1,868 cost points were collected through web searches, contractor interviews and data extracts with invoices provided by NEEP PAs. Note that most of the cost data was supplied per controller without regard to the number of fans controlled. This informed the finding that the overall cost of the installation is negligibly affected by the number of fans that are controlled. Many installations include the replacement of the existing fan motors with ECM or two-speed fan motors. The typical cost of these fan motor replacements was deducted from the cost in cases where fan motor replacement was included. Cost points that were supplied per fan were converted to a per controller price.
The analysis identified and removed any potential non-representative data points through a review of the data. Examples of removed data included controllers designed for 3-phase power, and duplicate or contract priced data points. Controllers for higher amperages and horsepower were removed from the data set based on the significantly higher cost and scarcity of data. (See data points 25, 26, and 35 - 36) Removed data points were relocated below line 42 and not included in the analysis. The reason each point was removed is listed in column W.
Formatted Data
Primary cost data was collected from contractors, PAs internet searches, and other sources across five states (MD, MA, CT, NY and VT). Due to the inherent differences in cost from one region to another, Navigant adjusted all material and labor cost points to represent base cost factor (BCF) data using RSMeans City Cost Indexes (CCI). For example, if the cost provided from a contractor in Pennsylvania for a unitary AC was $5000, than the NRS cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $5000 / 0.99
BCF = $5050
The same method was used to adjust all labor costs as well.
To prevent contract prices and internet-derived data from having undue weight in the final result, data from each source group (i.e. each state/region and internet data) was averaged before deriving the final result. Outliers were removed from each source group before averaging. Results are presented as a Base Cost Factor from which regional specific costs are derived using RS Means cost index data. These average costs are presented on the Summary of Results tab.
Labor Analysis
Contractor interviews identified the typical labor hours required to install the equipment. These labor hours were used to estimate labor costs wherever labor was not broken out and for internet-derived equipment costs. These labor costs were also added to web search equipment cost data to estimate an installed cost for that equipment.
Results and Findings
To the extent that we were able to determine an average installed cost per evaporator fan from our data, it appears that the results of this study are similar to the results of the CPUC/Itron study. However, this study determined a per fan installed cost about 21% lower. This could be due to regional differences, the decline in prices for controls since the CPUC study was completed or other factors. As discussed below, the predominance of contract pricing in certain PA territories and the scarcity of data in other territories may also have influenced the results.
The study revealed that negotiated contract pricing dominates the market for at least three PA territories studied. In other NEEP territories, it appears that market penetration of this technology is minimal, based on the scarcity of Program Data collected. This may indicate that market uptake of this measure may require both financial incentives and active marketing and outreach to reach full potential.
Presumably due in part to the falling cost of microprocessors and sensor technology, an emerging trend in the Refrigeration Controls market seems to be toward microprocessor-based multifunctional control modules - or more accurately, refrigeration management systems - that have numerous additional capabilities beyond control of the evaporator fans, including control of the compressor cycle, the defrost cycle, the door heaters, outdoor air economizers and more. These multifunctional controls tend to use the On/Off control method for Evaporator Fans in order to optimize energy use particularly during defrost cycles. Since it is impractical to disaggregate the cost of the Evaporator Fan Control capabilities from the overall cost of these multifunctional units, the cost data for refrigeration management systems were not included in our analysis, but presented separately on the Summary of Results tab.

## Evap Fan Controls - Results
Evaporator Fan Controls
Data Vintage | 2014
Does this measure have incremental labor cost (Yes/No)? | Yes
Return to Measure Index
Base Cost Factor Results:
Measure | Non Regional Specific Installed Cost* |  |  |  | Northern New England
[5 empty] | Central/Southern New England | Two-speed | Interview | yes
Evaporator Fan Control | 562.6928 |  |  |  | New England City | On/off | Invoice | no
[5 empty] | NY Metro | other | Program data
Results by Market: |  |  |  |  | NY Upstate |  | CPUC/Itron Cost Study
Measure | Market 1 Northern New England Installed Cost* |  |  |  | Mid-Atlantic |  | Web Search
Other: (California)
Evaporator Fan Control | 520.0219 |  |  |  | online
Measure | Market 2 Central/Southern New England Installed Cost*
Evaporator Fan Control | 599.718
Measure | Market 3 New England City Installed Cost *
Evaporator Fan Control | 634.9988
Measure | Market 4 NY Metro Installed Cost *
Evaporator Fan Control | 705.6168
Measure | Market 5 NY Upstate Installed Cost *
Evaporator Fan Control | 562.6928
Measure | Market 6 Mid-Atlantic Installed Cost *
Evaporator Fan Control | 532.3074
Refrigeration Management Devices**
Navigant's research revealed that the only controls using the On/Off control method were complex control modules - or more accurately refrigeration management systems - that have numerous additional capabilities which may include control of the compressor cycle, the defrost cycle, the door heaters, the evaporator fans, outdoor air economizer and more. These controls use complex control algorithms using many more inputs than just a compressor cycle sensor, and they can control much more amperage than the stand alone EFCs. These controls can also log the various control parameters over time like an Energy Management System. These refrigeration management systems are highly variable cost, depending on capabilities. Because it would be impossible to disaggregate the cost attributable to the EFC functions of these controls, we have not included these controls in the analyzed data set. An estimate of the price range for these multifunctional controls is presented below:
Measure | Non-Regional Specific Installed Cost Range*
Refrigeration Management Devices** | Minimum $500 | Maximum $1,700
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.97583 | 0.81533 | 0.90417
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9836 | 1.1632 | 1.0628
New England City | 3 | Boston, Providence | 1.008 | 1.2795 | 1.1275
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT | 1.0278 | 1.5593 | 1.262
NY Upstate | 5 | Buffalo, Rochester etc. | 0.9865 | 1.0135 | 0.99825
Mid-Atlantic | 6 | MD, DE, DC | 0.99275 | 0.88775 | 0.94625
National Average | - | - | 1 | 1 | 1
* Since the baseline cost for this measure is zero, these costs are actually the full installed cost including both materials and labor.
** Also see Note on READ ME tab
Summary of incremental cost data analysis for Evaporator Fan Controls. *Since the baseline cost for this measure is zero, these costs are the full installed cost including both materials and labor. Regional adjustment factors are applied to national average incremental costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category.

## LED Refrigeration Lgt - README
LED Refrigeration Lighting
Return to Measure Index
Measure Characterization:
|  | Efficient Measure Description | LED Refrigeration Case Lighting
|  | Baseline Description | Standard Case Lighting (T12HO or standard T8)
|  | Measure Scenario(s) | RET
|  | Baseline Efficiency Levels | Existing lighting
|  | Efficient Measure Description & Specifications | LED lighting is installed in place of linear fluorescent lighting in horizontal or vertical refrigeration display cases
|  | Measure Efficiency Levels | Standard LED vs. Design Lights Consortium Qualified Products list
|  | Sizes | Per unit, per door, or per foot
|  | Distinguishing Features | Vertical of horizontal display case (per door or per linear foot)
|  | Sources | ME TRM, Min-Atlantic TRM, EVT offerings, and NY TRM
|  | Incremental Labor Cost | Yes
|  | Cost Basis | Incremental for New Construction , Full Costs for Retrofit
|  | Fuel Type | Electric
|  | Data Vintage | 2013
0.75
Incremental Cost Study Phase Three
Published: May, 2014
Incremental Cost Methodology
The project provides incremental and/or full measure costs, as appropriate to each measure's scenario(s)
Retrofit (RET) scenario is done when replacing a working system with a new technology or installing a technology that was not there before
Incremental Measure Costs are used in ROB and NC scenarios when an energy-efficient appliance or measure promoted through a program is installed in lieu of the standard (less efficient) appliance/measure. The incremental cost is the difference between the baseline energy efficiency measure (material and labor) and the standard efficiency model. The equation for calculating incremental measure costs is simply:
Incremental measure cost = energy efficient measure cost (material + labor) - standard efficient baseline cost (material + labor)
In some cases there is no difference in the installation cost between the standard and efficient measure and/or an efficient measure and a more efficient measure. In those cases only materials costs are provided in the incremental cost. Labor is defined as the product of the total dollar per hour and the total hours to install the baseline or efficient measures.
For Life Cycle purposes baseline cost assumes one ballast replacement as O&M, resulting approximately 4% incremental cost reduction. Replacement CFLS not considered in baseline costs because they are minimal.
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as an LED refrigeration case light.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity . The baseline equipment in this instance is T12HO or a T8 linear fluorescent light.
The users of this data should note that this workbook also includes full costs for LED refrigeration case lighting. Therefore, other incremental path scenarios can be created by combining this data with other full cost data for baseline refrigeration case lighting.
Workbook Elements
Results Tab
The results tab presents the incremental cost for the combination. Material, labor, and installed incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Base Cost Factor category).
Data Analysis
Raw Data
In 2013, 1 contractor interview and 1 distributor interview were completed for the analysis of the measure. A total of 154 cost points were collected for LED case lighting equipment. The cost for baseline equipment is aggregated to reflect comments and data from contractors and distributors as well as web based research for common fluorescent original equipment manufacturers and energy service companies. The aggregated baseline costs account for variations in linear fluorescent bulb types (T12HO and standard T8), bulb lengths, and bulb wattages.
Formatted Data
Primary cost data was collected from contractors and distributors across four states (MD, MA, NY, and VT). The data was formatted to present material and labor costs based on the particular configuration and application of the LED refrigeration case lighting. As the size, wattage, case application, case configuration, etc. all differ depending on the installation scenario, Navigant chose common units to present the formatted data in (cost per LED or cost per unit, cost per foot of LED tube, and cost per door) depending on the application (vertical and horizontal alignment). The formatted data (cost per LED or cost per unit, cost per foot of LED, and cost per door) represent an average of different lengths ranging from 4 to 6 feet.
[Coolers, freezers, and upright refrigeration cases will have vertically aligned lights, with one more light than door. Horizontal shelf cases and certain types of reach-in cases will have horizontally aligned lights. Horizontal cases will typically not have doors.]
The same method was used to adjust all labor costs and miscellaneous installation costs.
Some baseline internet costs were included in the analysis to augment and QC the contractor data. Internet costs do not include a contractor markup. Additionally, distributor costs do not include contractor markup. Therefore, and where available, estimated markups were gathered from contractors and distributors. This average markup was applied to the internet and distributor costs to produce estimated contractor costs.
The R.S. Means recalculated CCI factors annually. For this study, Navigant used the 2013 CCI factors. The data was statistically formatted at a 90/10 confidence interval. Navigant utilized a Z score of 1.645 representing a two-sided, 90/10 confidence interval for a normal distribution. This statistical approach was used to determine an interval estimate with a specified probability that the actual value (mean value) will lie within the range of the interval. By utilizing a 1.645 Z score, Navigant is targeting that the true value (mean value) will be within 10% of the estimated value with a 90% level of confidence.
Material Analysis
The efficient material cost includes the cost of the LED, the cost of the LED driver, and the ancillary costs. The baseline material cost includes the cost of the fluorescent tube, the cost of the ballast, and the ancillary costs. The analysis identified and removed any potential outlier data points through a review of the data.
Labor Analysis
Contractor interviews identified an incremental difference in the time to install efficient versus base scenario equipment. In general, efficient equipment took approximately 5 more minutes to install when compared with baseline equipment. An average installation time was used to determine the time required to install baseline and efficient measure equipment.
Results
Through contractor and distributor interviews, Navigant defined the most common applications installed in convenient and grocery stores. As such, results are presented for each of those size categories at a Base Cost Factor level.

## LED Refrigeration Lgt - Results
LED Refrigeration Lighting
Data Vintage | 2013
Does this measure have incremental labor cost (Yes/No)? | Yes
Return to Measure Index
Base Cost Factor Results:
Base Cost Factor | Efficient Measure Incremental Cost
| Cost per Unit ($/LED) | Cost per Foot ($/ft.) | Cost per Door ($/door)
Vertical - Center | 149.9463 | 29.5691 | 199.9283
Vertical - End | 112.6649 | 22.2749 | 150.2198
Horizontal | 110.6112 | 22.7866 | N/A
Overall | 128.2212 | 25.5646 | 176.9993
Results by Market:
Case Lighting Scenario | Market 1 Northern New England Incremental Cost ($/Unit)
| Cost per Unit ($/LED) | Cost per Foot ($/ft.) | Cost per Door ($/door)
Vertical - Center | 144.9142 | 28.5518 | 193.2189
Vertical - End | 108.5337 | 21.439 | 144.7116
Horizontal | 106.5298 | 21.9452 | N/A
Overall | 123.7141 | 24.6491 | 170.844
Case Lighting Scenario | Market 2 Central/Southern New England Incremental Cost ($/Unit)
| Cost per Unit ($/LED) | Cost per Foot ($/ft.) | Cost per Door ($/door)
Vertical - Center | 149.0631 | 29.4481 | 198.7508
Vertical - End | 112.3931 | 22.2426 | 149.8575
Horizontal | 110.3732 | 22.7382 | N/A
Overall | 127.6944 | 25.4784 | 176.1978
Case Lighting Scenario | Market 3 New England City Incremental Cost ($/Unit)
| Cost per Unit ($/LED) | Cost per Foot ($/ft.) | Cost per Door ($/door)
Vertical - Center | 153.5282 | 30.3178 | 204.7043
Vertical - End | 115.9486 | 22.9565 | 154.5981
Horizontal | 113.8786 | 23.4606 | N/A
Overall | 131.6294 | 26.2726 | 181.5919
Case Lighting Scenario | Market 4 NY Metro Incremental Cost ($/Unit)
| Cost per Unit ($/LED) | Cost per Foot ($/ft.) | Cost per Door ($/door)
Vertical - Center | 0.75 | 31.3922 | 211.6949
Vertical - End | 120.4552 | 23.8785 | 160.607
Horizontal | 118.3446 | 24.3815 | N/A
Overall | 136.4433 | 27.2596 | 188.1296
Case Lighting Scenario | Market 5 NY Upstate Incremental Cost ($/Unit)
| Cost per Unit ($/LED) | Cost per Foot ($/ft.) | Cost per Door ($/door)
Vertical - Center | 148.1589 | 29.2209 | 197.5452
Vertical - End | 111.3808 | 22.0242 | 148.5077
Horizontal | 109.3549 | 22.5279 | N/A
Overall | 126.7271 | 25.2695 | 174.9257
Case Lighting Scenario | Market 6 Mid-Atlantic Cost ($/Unit)
| Cost per Unit ($/LED) | Cost per Foot ($/ft.) | Cost per Door ($/door)
Vertical - Center | 147.9378 | 29.1567 | 197.2504
Vertical - End | 110.9267 | 21.9187 | 147.9022
Horizontal | 108.8879 | 22.4312 | N/A
Overall | 126.3702 | 25.1845 | 174.4876
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor | Total
Northern New England | 1 | ME, VT, NH | 0.97583 | 0.81533 | 0.90417
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9836 | 1.1632 | 1.0628
New England City | 3 | Boston, Providence | 1.008 | 1.2795 | 1.1275
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT, | 1.0278 | 1.5593 | 1.262
NY Upstate | 5 | Buffalo, Rochester etc. | 0.9865 | 1.0135 | 0.99825
Mid-Atlantic | 6 | MD, DE, DC | 0.99275 | 0.88775 | 0.94625
National Average | - | - | 1 | 1 | 1
Summary of incremental cost data analysis for LED Refrigeration Case Lighting. Regional adjustment factors are applied to the Base Cost Factors (BCFs) to calculate market specific results. Regional adjustment factors were developed using RSMeans City Cost Indexes based on weighted average of division category.

## Steam Traps - README
Commercial Steam Traps
Return to Measure Index
Measure Characterization:
|  | Measure Description | Steam Traps
|  | Baseline Description | Leaky or Failed Steam Trap
|  | Measure Scenario(s) | RET, ROB
|  | Baseline Efficiency Levels | Leaky or Failed Steam Trap
|  | Efficient Measure Description | Newly Installed / Replaced Steam Trap
|  | Measure Efficiency Levels | N/A
|  | Sizes | Pipe diameter ranges between 0.25" and 3"
|  | Distinguishing Features | 1) Thermostatic, Thermodynamic, Mechanical, or Fixed-Orifice
2) Maximum Operating Pressure
|  | Installation Scenarios | Commercial and Industrial Steam Heating Lines (Low and Medium Temperature Applications)
|  | Sources | Mass Save TRM, CA Steam Trap Surveys, Conservation Solutions Interview
|  | Comments | Costs for steam trap installation / replacement will be captured during this study. The scope of this characterization excludes steam trap repairs, steam trap surveys, and steam trap testing.
|  | Incremental Labor Cost | Yes - Full labor cost
|  | Cost Basis | Full Installed
|  | Fuel Type | Gas
|  | Data Vintage | 2013
0.75
Incremental Cost Study Phase Three
Published: May, 2014
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the standard (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = efficient measure cost (material and labor) - base case cost (material and labor)
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as a replacement, functional Steam Trap. The full measure costs include equipment and labor.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity . The baseline equipment in this instance is a faulty, leaky Steam Trap due for replacement.
WORKBOOK ELEMENTS
Results Tab
The results tab presents the incremental cost for the Steam Traps. Material, labor, and installed incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Base Cost Factor category).
Data Analysis
Raw Data
Navigant completed 3 in-depth interviews with installing contractors, vendors, and manufacturers to understand the typical installation practices and associated costs for Steam Trap replacements. Additionally, over 100 cost points from program tracking data supports the analysis, along with over 250 internet cost data points.
Formatted Data
Primary cost data was collected from in-depth interviews and program tracking data across multiple states including MA, NY, NH, and RI. Due to the inherent differences in cost from one region to another (e.g. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent base cost factor (BCF) data using RSMeans CCI. Table 1 provides a regional break down of NEEP. For example, if the material cost provided from a contractor in New York Metro for a Steam Trap was $1,000, then the BCF cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $1,000 / 1.03
BCF = $968.29
The same method was used to adjust all labor costs.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data. It was observed that Steam Trap Material Cost increased with increasing diameter size, and also that Material Costs are highly related to Steam Trap technology type. Analysis was performed on the following Steam Trap technologies: Float & Thermostatic (F&T), Inverted Bucket, Thermodynamic / Thermodisc, and Thermostatic. It was observed that Steam Trap Material Costs for the Thermodynamic and Thermodisc technologies were almost identical, therefore these two technologies were analyzed together.
A linear regression was used to develop the material cost at various diameters for each technology type. The regression analysis was performed on the entire range of Steam Trap diameter sizes for each technology. For instance, F&T traps have data ranging from 0.5" to 2", whereas Thermostatic traps were only found in the range of 0.5" - 1". Thus, the Results for F&T traps extend from 0.5" to 2", whereas the Results for Thermostatic traps are only from 0.5" to 1". Types of Steam Traps
Float and Thermostatic type steam traps use a float connected by a linkage to the valve plug to discharge condensate from the system.
Inverted Bucket type stream traps use an inverted bucket as a float device connected by a linkage to the valve plug. Thermodynamic type steam traps operate in a cyclic on/off process using the thermodynamic properties of flash steam as it flows through the trap.
Thermodisc type steam traps use steam velocity and pressure to move a disc to open and close the valve plug.
Thermostatic Trap type steam traps use a fluid-filled thermal element that operates by thermal expansion and contraction.
Labor Analysis
Contractor interviews identified an incremental difference in the time to install Steam Traps of a larger diameter, when compared to the time to install Steam Traps of a smaller diameter. Installation times were taken from the three in-depth interviews. Finally, the labor rate was calculated with a weighted average of all contractor labor rates ($/HR) collected from the three in-depth interviews.
Results
Results are presented for each technology type and common trap diameter size at the BCF level.

## Steam Traps - Results
Commercial Steam Traps
Data Vintage | 2013
Does this measure have labor cost (Yes/No)? | Yes
Labor Cost Analysis Type (DROP DOWN MENU): | Labor Costs
Return to Measure Index
Base Cost Factor Results:
Steam Trap Type | Diameter Size (in.) | Steam Traps |  | Base Cost Factor ($/Unit)
|  | Material Cost | Labor Cost | Total Installed Cost
Float & Thermostatic | 0.5 | 308.3525 | 197.3421 | 505.6946
| 0.75 | 437.4188 | 197.3421 | 634.7609
| 1 | 566.4852 | 208.8425 | 775.3277
| 1.5 | 824.6179 | 294.9488 | 1119.5667
| 2 | 1082.7506 | 278.4567 | 1361.2072
Inverted Bucket | 0.5 | 268.1852 | 197.3421 | 465.5273
| 0.75 | 471.4003 | 197.3421 | 668.7424
| 1 | 674.6154 | 208.8425 | 883.4579
| 1.5 | 1081.0456 | 294.9488 | 1375.9944
| 2 | 1487.4758 | 278.4567 | 1765.9325
Thermodisc / Thermodynamic | 0.5 | 384.8779 | 197.3421 | 582.22
| 0.75 | 534.9141 | 197.3421 | 732.2562
| 1 | 684.9503 | 208.8425 | 893.7928
Thermostatic | 0.5 | 179.2304 | 197.3421 | 376.5725
| 0.75 | 304.5562 | 197.3421 | 501.8983
| 1 | 429.882 | 208.8425 | 638.7245
Results by Market:
Steam Trap Type | Diameter Size (in.) | Steam Traps |  | Market 1 Northern New England Cost ($/Unit)
|  | Material Cost | Labor Cost | Total Installed Cost
Float & Thermostatic | 0.5 | 300.9007 | 160.8996 | 461.8002
| 0.75 | 426.8479 | 160.8996 | 587.7475
| 1 | 552.7951 | 170.2762 | 723.0714
| 1.5 | 804.6896 | 240.4816 | 1045.1712
| 2 | 1056.5841 | 227.035 | 1283.6191
Inverted Bucket | 0.5 | 261.7041 | 160.8996 | 422.6036
| 0.75 | 460.0081 | 160.8996 | 620.9077
| 1 | 658.3122 | 170.2762 | 828.5885
| 1.5 | 1054.9204 | 240.4816 | 1295.4019
| 2 | 1451.5285 | 227.035 | 1678.5635
Thermodisc / Thermodynamic | 0.5 | 375.5767 | 160.8996 | 536.4762
| 0.75 | 521.987 | 160.8996 | 682.8866
| 1 | 668.3973 | 170.2762 | 838.6736
Thermostatic | 0.5 | 174.899 | 160.8996 | 335.7986
| 0.75 | 297.1961 | 160.8996 | 458.0957
| 1 | 419.4932 | 170.2762 | 589.7694
Steam Trap Type | Diameter Size (in.) | Steam Traps |  | Market 2 Central/Southern New England Cost ($/Unit)
|  | Material Cost | Labor Cost | Total Installed Cost
Float & Thermostatic | 0.5 | 303.2955 | 229.5483 | 532.8438
| 0.75 | 430.2452 | 229.5483 | 659.7935
| 1 | 557.1948 | 242.9256 | 800.1204
| 1.5 | 811.0941 | 343.0844 | 1154.1786
| 2 | 1064.9934 | 323.9008 | 1388.8942
Inverted Bucket | 0.5 | 263.787 | 229.5483 | 493.3353
| 0.75 | 463.6693 | 229.5483 | 693.2177
| 1 | 663.5517 | 242.9256 | 906.4773
| 1.5 | 1063.3165 | 343.0844 | 1406.4009
| 2 | 1463.0812 | 323.9008 | 1786.982
Thermodisc / Thermodynamic | 0.5 | 378.5659 | 229.5483 | 608.1142
| 0.75 | 526.1415 | 229.5483 | 755.6898
| 1 | 673.7171 | 242.9256 | 916.6427
Thermostatic | 0.5 | 176.291 | 229.5483 | 405.8393
| 0.75 | 299.5615 | 229.5483 | 529.1098
| 1 | 422.8319 | 242.9256 | 665.7575
Diameter Size (in.) | Steam Trap Type | Steam Traps |  | Market 3 New England City Cost ($/Unit)
|  | Material Cost | Labor Cost | Total Installed Cost
Float & Thermostatic | 0.5 | 310.8193 | 252.4992 | 563.3185
| 0.75 | 440.9182 | 252.4992 | 693.4174
| 1 | 571.0171 | 267.214 | 838.231
| 1.5 | 831.2148 | 377.387 | 1208.6018
| 2 | 1091.4126 | 356.2853 | 1447.6978
Inverted Bucket | 0.5 | 270.3307 | 252.4992 | 522.8299
| 0.75 | 475.1715 | 252.4992 | 727.6707
| 1 | 680.0123 | 267.214 | 947.2263
| 1.5 | 1089.694 | 377.387 | 1467.081
| 2 | 1499.3756 | 356.2853 | 1855.6609
Thermodisc / Thermodynamic | 0.5 | 387.9569 | 252.4992 | 640.4561
| 0.75 | 539.1934 | 252.4992 | 791.6926
| 1 | 690.4299 | 267.214 | 957.6439
Thermostatic | 0.5 | 180.6642 | 252.4992 | 433.1634
| 0.75 | 306.9926 | 252.4992 | 559.4918
| 1 | 433.321 | 267.214 | 700.535
Diameter Size (in.) | Steam Trap Type | Steam Traps |  | Market 4 NY Metro Cost ($/Unit)
|  | Material Cost | Labor Cost | Total Installed Cost
Float & Thermostatic | 0.5 | 316.9093 | 307.7056 | 624.6149
| 0.75 | 449.5572 | 307.7056 | 757.2629
| 1 | 582.2052 | 325.6377 | 907.8428
| 1.5 | 847.501 | 459.8989 | 1307.3999
| 2 | 1112.7969 | 434.1835 | 1546.9804
Inverted Bucket | 0.5 | 275.6273 | 307.7056 | 583.333
| 0.75 | 484.4817 | 307.7056 | 792.1873
| 1 | 693.336 | 325.6377 | 1018.9736
| 1.5 | 1111.0446 | 459.8989 | 1570.9435
| 2 | 1528.7533 | 434.1835 | 1962.9368
Thermodisc / Thermodynamic | 0.5 | 395.5582 | 307.7056 | 703.2639
| 0.75 | 549.7579 | 307.7056 | 857.4636
| 1 | 703.9577 | 325.6377 | 1029.5953
Thermostatic | 0.5 | 184.204 | 307.7056 | 491.9097
| 0.75 | 313.0076 | 307.7056 | 620.7133
| 1 | 441.8112 | 325.6377 | 767.4489
Diameter Size (in.) | Steam Trap Type | Steam Traps |  | Market 5 NY Upstate Cost ($/Unit)
|  | Material Cost | Labor Cost | Total Installed Cost
Float & Thermostatic | 0.5 | 304.1897 | 200.0062 | 504.196
| 0.75 | 431.5137 | 200.0062 | 631.5199
| 1 | 558.8376 | 211.6619 | 770.4995
| 1.5 | 813.4855 | 298.9306 | 1112.4161
| 2 | 1068.1334 | 282.2158 | 1350.3492
Inverted Bucket | 0.5 | 264.5647 | 200.0062 | 464.5709
| 0.75 | 465.0364 | 200.0062 | 665.0426
| 1 | 665.5081 | 211.6619 | 877.17
| 1.5 | 1066.4515 | 298.9306 | 1365.3821
| 2 | 1467.3949 | 282.2158 | 1749.6107
Thermodisc / Thermodynamic | 0.5 | 379.682 | 200.0062 | 579.6882
| 0.75 | 527.6927 | 200.0062 | 727.6989
| 1 | 675.7035 | 211.6619 | 887.3653
Thermostatic | 0.5 | 176.8108 | 200.0062 | 376.817
| 0.75 | 300.4447 | 200.0062 | 500.4509
| 1 | 424.0786 | 211.6619 | 635.7404
Diameter Size (in.) | Steam Trap Type | Steam Traps |  | Market 6 Mid-Atlantic Cost ($/Unit)
|  | Material Cost | Labor Cost | Total Installed Cost
Float & Thermostatic | 0.5 | 306.117 | 175.1904 | 481.3074
| 0.75 | 434.2476 | 175.1904 | 609.438
| 1 | 562.3782 | 185.3999 | 747.7781
| 1.5 | 818.6394 | 261.8408 | 1080.4802
| 2 | 1074.9006 | 247.1999 | 1322.1005
Inverted Bucket | 0.5 | 266.2409 | 175.1904 | 441.4313
| 0.75 | 467.9827 | 175.1904 | 643.1731
| 1 | 669.7245 | 185.3999 | 855.1244
| 1.5 | 1073.208 | 261.8408 | 1335.0488
| 2 | 1476.6916 | 247.1999 | 1723.8915
Thermodisc / Thermodynamic | 0.5 | 382.0875 | 175.1904 | 557.2779
| 0.75 | 531.036 | 175.1904 | 706.2264
| 1 | 679.9844 | 185.3999 | 865.3843
Thermostatic | 0.5 | 177.931 | 175.1904 | 353.1214
| 0.75 | 302.3481 | 175.1904 | 477.5386
| 1 | 426.7653 | 185.3999 | 612.1653
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.97583 | 0.81533 | 0.90417
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9836 | 1.1632 | 1.0628
New England City | 3 | Boston, Providence | 1.008 | 1.2795 | 1.1275
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT, | 1.0278 | 1.5593 | 1.262
NY Upstate | 5 | Buffalo, Rochester etc. | 0.9865 | 1.0135 | 0.99825
Mid-Atlantic | 6 | MD, DE, DC | 0.99275 | 0.88775 | 0.94625
National Average | - | - | 1 | 1 | 1
Summary of incremental cost data analysis for Steam Traps. Regional adjustment factors are applied to Base Cost Factor incremental costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category. In addition, two methods of analysis were employed for the Labor Cost Analysis:
(1) Arithmetic Mean of Labor Costs per Diameter size (Labor Costs) and; (2) Arithmetic Mean of Man Hours per Diameter size multiplied by an average labor rate (Man Hours) The user may choose between each method by toggling the selection in Cell C8.
Note: Baseline assumptions correspond to a faulty or leaky Steam Trap due for replacement. Although this measure does not have incremental labor costs, labor costs are included in the Total Installed Costs below.

## Unitary AC - README
Unitary Air Conditioning
Return to Measure Index
Measure Characterization:
|  | Measure Description | Commercial Unitary AC (packaged)
|  | Baseline Description | Standard Efficient Unitary AC
|  | Measure Scenario(s) | ROB, NC
|  | Baseline Efficiency Levels | IECC 2009 and/or jurisdiction-specific. Baseline efficiency varies by size.
|  | Efficient Measure Description | High efficiency Unitary Air-Conditioning Equipment
|  | Measure Efficiency Levels | CEE Tier 1 & Tier 2 (see CEE Criteria Tab)
|  | Sizes | 5.4 - 11.25 tons
11.25 - 20 tons
20 - 63 tons
>= 63 tons
|  | Distinguishing Features | 1) Heating type (none, gas, electric resistance)
2) Other features: (e.g., variable speed fans and compressors associated with higher EERs)
|  | Installation Scenarios | Single Package
|  | Sources | NY TRM, Mid-Atlantic TRM, EVT TRM, Efficiency Maine TRM, MA TRM
|  | Comments | Replace Unitary AC only
|  | Incremental Labor Cost | No - Labor cost is the same for efficient and baseline equipment.
|  | Cost Basis | Incremental
|  | Fuel Type | Electric
|  | Data Vintage | 2013
0.75
Incremental Cost Study Phase Three
Published: May, 2014
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the standard (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = efficient measure material cost - base case material cost
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as a commercial unitary air conditioner with EER in line with the CEE Criteria.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity. The baseline equipment in this instance is a commercial unitary air conditioner with EER in line with the current minimum Federal standard.
Workbook Elements
Results Tab
The results tab presents the incremental cost for the commercial unitary air conditioners. Incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis
Raw Data
A total of 120 cost points were collected through contractor interviews and invoices provided by NEEP constituents. Note that most of the data fell into the 5.4 - 20 ton range. The cost points for units greater than 20 tons were limited, due to the lack of invoice data for this range.
Formatted Data
Primary cost data was collected from contractors across four states (MD, MA, RI, and PA). Due to the inherent differences in cost from one region to another, Navigant adjusted all material and labor cost points to represent a non-regional specific Base Cost Factor (BCF) using RSMeans CCI. For example, if the cost provided from a contractor in Pennsylvania for a unitary AC was $5000, than the BCF would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $5000 / 0.99
BCF = $5050
The same method was used to adjust all labor cost.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data.
A linear regression was used to develop the material cost for the measure. A regression was done for the following size categories:
a) 5.4 - 20 tons
b) > 20 tons
The regression analysis resulted in one incremental cost per size category. Although the actual material costs vary within a size category, the typical incremental costs were not found to vary significantly.
Some invoice data for units smaller than 5.4 tons was received and included in the raw data but excluded from the results, because it was outside the scope of this measure.
Labor Analysis
Contractor interviews identified no incremental difference in the time to install efficient versus base scenario equipment. In general, efficient equipment took just as much time to install as compared with base equipment. The labor rate was calculated by an average of all contractor labor rates ($/HR). An average installation times was used to determine the time required to install measure and baseline equipment.
Results
Navigant defined the unit size categories to line up with the size categories used by the federal standards and CEE ratings. As such, results are presented for each of those size categories at a non-regional specific level.

## Unitary AC - Results
Unitary Air Conditioning
Data Vintage | 2013
Does this measure have incremental labor cost (Yes/No)? | No
Return to Measure Index
Base Cost Factor Results:
Size Category (Tons) | Base Cost Factor ($/Ton)
| CEE Tier 1 | CEE Tier 2
5.4 to 11.25 | 63.4207 | 126.8415
11.25 to 20 | 63.4207 | 126.8415
20 to 63 | 18.9157 | 37.8314
Results by Market:
Size Category (Tons) | Market 1 Northern New England Incremental Cost ($/Ton)
| CEE Tier 1 | CEE Tier 2
5.4 to 11.25 | 61.8881 | 123.7761
11.25 to 20 | 61.8881 | 123.7761
20 to 63 | 18.4586 | 36.9172
Size Category (Tons) | Market 2 Central/Southern New England Incremental Cost ($/Ton)
| CEE Tier 1 | CEE Tier 2
5.4 to 11.25 | 62.3806 | 124.7613
11.25 to 20 | 62.3806 | 124.7613
20 to 63 | 18.6055 | 37.211
Size Category (Tons) | Market 3 New England City Incremental Cost ($/Ton)
| CEE Tier 1 | CEE Tier 2
5.4 to 11.25 | 63.9281 | 127.8562
11.25 to 20 | 63.9281 | 127.8562
20 to 63 | 19.067 | 38.1341
Size Category (Tons) | Market 4 NY Metro Incremental Cost ($/Ton)
| CEE Tier 1 | CEE Tier 2
5.4 to 11.25 | 65.1807 | 130.3613
11.25 to 20 | 65.1807 | 130.3613
20 to 63 | 19.4406 | 38.8813
0.75
Size Category (Tons) | Market 5 NY Upstate Incremental Cost ($/Ton)
| CEE Tier 1 | CEE Tier 2
5.4 to 11.25 | 62.5645 | 125.1291
11.25 to 20 | 62.5645 | 125.1291
20 to 63 | 18.6604 | 37.3207
Size Category (Tons) | Market 6 Mid-Atlantic Incremental Cost ($/Ton)
| CEE Tier 1 | CEE Tier 2
5.4 to 11.25 | 62.9609 | 125.9219
11.25 to 20 | 62.9609 | 125.9219
20 to 63 | 18.7786 | 37.5572
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.97583 | 0.81533 | 0.90417
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9836 | 1.1632 | 1.0628
New England City | 3 | Boston, Providence | 1.008 | 1.2795 | 1.1275
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT, | 1.0278 | 1.5593 | 1.262
NY Upstate | 5 | Buffalo, Rochester etc. | 0.9865 | 1.0135 | 0.99825
Mid-Atlantic | 6 | MD, DE, DC | 0.99275 | 0.88775 | 0.94625
National Average | - | - | 1 | 1 | 1
Summary of incremental cost data analysis for commercial Unitary AC. Regional adjustment factors are applied to national average incremental costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category .

## VFD - README
Variable Frequency Drives
Return to Measure Index
Measure Characterization:
| Measure Description | Variable Frequency Drive (VFD)
| Baseline Description | No VFD installed
| Measure Scenario(s) | RET
| Baseline Efficiency Levels | Normal efficiency level of controlled application without VFD.
| Efficient Measure Description | VFD installed.
| Measure Efficiency Levels | Reduction in kWhr/HP energy consumption for controlled unit, when operating at non-maximum speed. Savings by application (kWh/HP): Supply Fan - 800, Pump - 600-700, Small fans - 300-500
| Sizes | 3HP, 5HP, 7.5HP, 10HP, 15HP
| Distinguishing Features | VFD ampage and voltage need to match that of the controlled unit
| Installation Scenarios | 1) Large VFDs for larger motors, standalone box mounted on wall, look like big black box 2) Packaged Rooftop Units can be purchased with option of pre-installed VFD 3) Some motor pumps have integrated VFDs 4) Normal installation is as add-on, requiring installation of sensors and other additional electrical equipment
| Sources | National Grid, Internet, and Interviews
| Comments | N/A
| Incremental Labor Cost | Yes - Full labor cost
| Cost Basis | Full
| Fuel Type | Electric
| Data Vintage | 2012
Incremental Cost Study Phase Two
Published: January, 2013
Incremental Cost Methodology
The project provides incremental and/or full measure costs, as appropriate to each measure's scenario(s)
The Variable Frequency Drives measure did not qualify for an incremental cost analysis, since there is no incremental efficiency associated with VFDs. From the start of the study, the baseline for the VFD measures was designated as no VFD. As a result, the incremental measure cost is equal to the total installed cost of the unit.
Full Measure Costs are used where the scenario assumes that there is no alternative measure , e.g. retrofit application .
Incremental Measure Costs are used when an energy-efficient appliance or measure promoted through a program is installed in lieu of the standard (less efficient) appliance/measure. The incremental cost is the difference between the baseline energy efficiency measure (material and labor) and the standard efficiency model. The equation for calculating incremental measure costs is simply:
Incremental measure cost = energy efficient measure cost (material + labor) - standard efficient baseline cost (material + labor)
In some cases there is no difference in the installation cost between the standard and efficient measure and/or an efficient measure and a more efficient measure. In those cases only materials costs are provided in the incremental cost.
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, the baseline option is an equipment unit with no installed VFD and the measure option is the same equipment unit with an installed VFD.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity . The baseline equipment in this instance is the controlled equipment unit without an installed VFD.
Workbook Elements
Results Tab
The results tab presents the cost for Variable Frequency Drives. Equipment, labor, and total installed costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category, also known as Base Cost Factor).
Data Analysis
Raw Data
A total of 16 contractor interviews were completed for the analysis of the measure. A total of 18 contractor cost points and 167 internet cost points were collected for variable frequency drives. In addition, invoice data was collected from National Grid, and 48 equipment cost data points were found.
Formatted Data
Primary cost data was collected from contractors across two states (RI and MA). Due to the inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent base cost factor (BCF) data using RSMeans CCI. Table 1 provides a regional break down of the NEEP. For example, if a the cost provided from a contractor in Central/Southern New England for a Variable Frequency Drive was $1000, than the BCF cost would be:
BCF= Original State Cost ($) / Average Adjustment Factor for Original State
BCF= $1000 / 1.05
BCF= $952.38
The same method was used to adjust all labor cost.
Additionally, distributor costs do not include contractor markup. Therefore and where available, estimated markups were gathered from contractors and distributors. This average markup was applied to the distributor costs to produce estimated contractor costs.
Similarly, once BCF costs were determined for each measure, the costs were then allocated to each market by multiplying the BCF cost by the individual market factor.
The R.S. Means recalculated CCI factors annually. For this study, Navigant used the 2012 CCI factors. Additionally, any older data, collected for the ICS Phase One Report or other sources , was updated with the 2012 factors to maintain comparability with data collected in 2012 for the ICS Phase Two.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data. This process involved a regression analysis on the VFD size and equipment cost to identify data points that were far outside the expected range. Results were found by averaging the values for all VFDs in the specified size range.
Labor Analysis
Contractor interviews estimated the time to complete a basic installation of a VFD and the time to complete a typical installation of a VFD. The labor rate was calculated with a weighted average of all contractor labor rates ($/HR) collected for VFD measures.
Results
Through contractor interviews, Navigant defined the most common unit size ranges. As such, results are presented for each of those size categories at a non-regional specific level as the Base Cost Factor (BCF).
Bypass
Many contractor interviews mentioned installing a bypass along with the VFD as a safety measure. The bypass allows the controlled equipment to continue running in the event that the VFD fails. Some contractors stated that they would only install VFDs with the added bypass, and so the Navigant team decided to compute a base cost factor for the bypass as a supplementary cost.

## VFD - Results
Variable Frequency Drives
| Data Vintage | 2012
| Does this measure have incremental labor cost (Yes/No)? | No
Return to Measure Index
Base Cost Factor Results:
| Size (HP) | Base Cost Factor ($/Unit)
| Size (HP) | Equipment Cost | Labor Cost | Total Installed Cost
| 5 | 1115.1023 | 1135.1657 | 2250.268
| 15 | 2182.7963 | 1135.1657 | 3317.9621
| 25 | 3250.4904 | 1135.1657 | 4385.6561
| 50 | 5437.9641 | 1135.1657 | 6573.1298
| 75 | 7397.0667 | 1135.1657 | 8532.2325
| 100 | 8848.1052 | n/a | n/a
| 200 | 15301.0363 | n/a | n/a
Results by Market:
| Size (HP) | Market 1 Northern New England ($/Unit)
|  | Equipment Cost | Labor Cost | Total Installed Cost
1 | 5 | 1091.6851 | 780.4264 | 1872.1116
1 | 15 | 2136.9576 | 780.4264 | 2917.384
1 | 25 | 3182.2301 | 780.4264 | 3962.6565
1 | 50 | 5323.7669 | 780.4264 | 6104.1933
1 | 75 | 7241.7283 | 780.4264 | 8022.1548
1 | 100 | 8662.2949 | n/a | n/a
1 | 200 | 14979.7145 | n/a | n/a
| Size (HP) | Market 2 Central/Southern New England ($/Unit)
|  | Equipment Cost | Labor Cost | Total Installed Cost
2 | 5 | 1102.3901 | 1284.0995 | 2386.4896
2 | 15 | 2157.9124 | 1284.0995 | 3442.0119
2 | 25 | 3213.4348 | 1284.0995 | 4497.5342
2 | 50 | 5375.9713 | 1284.0995 | 6660.0708
2 | 75 | 7312.7402 | 1284.0995 | 8596.8397
2 | 100 | 8747.2368 | n/a | n/a
2 | 200 | 15126.6045 | n/a | n/a
| Size (HP) | Market 3 New England City ($/Unit)
|  | Equipment Cost | Labor Cost | Total Installed Cost
3 | 5 | 1128.4835 | 1407.0379 | 2535.5214
3 | 15 | 2208.9899 | 1407.0379 | 3616.0278
3 | 25 | 3289.4962 | 1407.0379 | 4696.5342
3 | 50 | 5503.2197 | 1407.0379 | 6910.2576
3 | 75 | 7485.8315 | 1407.0379 | 8892.8695
3 | 100 | 8954.2824 | n/a | n/a
3 | 200 | 15484.6487 | n/a | n/a
| Size (HP) | Market 4 NY Metro ($/Unit)
|  | Equipment Cost | Labor Cost | Total Installed Cost
4 | 5 | 1151.6219 | 1761.7772 | 2913.3991
4 | 15 | 2254.2829 | 1761.7772 | 4016.0601
4 | 25 | 3356.9439 | 1761.7772 | 5118.7211
4 | 50 | 5616.0574 | 1761.7772 | 7377.8346
4 | 75 | 7639.3207 | 1761.7772 | 9401.0979
4 | 100 | 9137.8806 | n/a | n/a
4 | 200 | 15802.1452 | n/a | n/a
| Size (HP) | Market 5 NY Upstate ($/Unit)
|  | Equipment Cost | Labor Cost | Total Installed Cost
5 | 5 | 1100.8847 | 1136.5847 | 2237.4694
5 | 15 | 2154.9657 | 1136.5847 | 3291.5504
5 | 25 | 3209.0466 | 1136.5847 | 4345.6313
5 | 50 | 5368.6301 | 1136.5847 | 6505.2148
5 | 75 | 7302.7541 | 1136.5847 | 8439.3388
5 | 100 | 8735.2918 | n/a | n/a
5 | 200 | 15105.9481 | n/a | n/a
| Size (HP) | Market 6 Mid-Atlantic ($/Unit)
|  | Equipment Cost | Labor Cost | Total Installed Cost
6 | 5 | 1115.1023 | 1009.7299 | 2124.8322
6 | 15 | 2182.7963 | 1009.7299 | 3192.5262
6 | 25 | 3250.4904 | 1009.7299 | 4260.2203
6 | 50 | 5437.9641 | 1009.7299 | 6447.694
6 | 75 | 7397.0667 | 1009.7299 | 8406.7967
6 | 100 | 8848.1052 | n/a | n/a
6 | 200 | 15301.0363 | n/a | n/a
| Market | Market Code | Example | Material Adj Fct | Labor Adj Fct
| Northern New England | 1 | ME, VT, NH | 0.979 | 0.6875
| Central/Southern New England | 2 | MA exc Boston, RI, most CT | 0.9886 | 1.1312
| New England City | 3 | Boston, Providence | 1.012 | 1.2395
| NY Metro | 4 | NYC, metro suburbs Southwest CT | 1.0328 | 1.552
| NY Upstate | 5 | Buffalo, Rochester etc. | 0.98725 | 1.0012
| Mid-Atlantic | 6 | MD, DE DC | 1 | 0.8895
| National Average | - | - | 100 | 1
Summary of cost data analysis for variable frequency drives. Regional adjustment factors are applied to base cost factor costs.
Regional adjustment factors were developed using RSMeans City Cost Indexes based on weighted average of division category.

## Res Air Sealing - README
Residential Air Sealing
Return to Measure Index
Measure Characterization:
| Measure Description | Residential Air Sealing
| Baseline Description | No Air Sealing
| Measure Scenario(s) | RET/NC
| Baseline Efficiency Levels | 0 CFM Reduced
| Efficient Measure Description | Leakage reduction in CFM at 50 Pascals
| Measure Efficiency Levels | 250 - 1000 CFM Reduced
| Sizes | House Size 1200-3000 SF
| Distinguishing Features | N/A
| Installation Scenarios | N/A
| Sources | Contractor interviews in NY, VT, MA, ME, and CT
| Incremental Labor Cost | Yes - Full labor cost
| Cost Basis | Full
| Fuel Type | Gas
| Data Vintage | 2011
Incremental Cost Study Phase One
Published: September, 2011
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the standard (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = measure material cost (material + labor) - base case material cost (material + labor)
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as leakage reduction in CFM at 50 pascals.
Baseline: The baseline condition is defined as the standard condition, without the utility EE activity . The baseline condition in this case is existing conditions with no air sealing.
Results Tab
The tab presents the cost for air sealing. Material, labor, and installed costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis
Raw Data
A total of 19 contractor interviews were completed (19 data points) for the incremental cost analysis of residential air sealing.
Formatted Data
Primary cost data was collected from contractors across a six states (NY, VT, MA, MA, ME and CT). Due to the inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent non-regional specific (NRS) data using RSMeans CCI. Table 1 provides a regional break down of the NEEP. For example, if a cost provided from a contractor in New York Metro for air sealing was $1000, than the NRS cost would be:
NRS = Original State Cost ($) / Average Adjustment Factor for Original State
NRS = $1000 / 1.26
NRS = $793.65
The same method was used to adjust all labor cost.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data.
An arithmetic mean was used to develop the material cost for the measure. Average costs were developed according to house size and CFM reduced.
Labor Analysis
The average time spent on air sealing was determined to be 12 hours, based on contractor interviews. The labor rate was calculated by an average of all contractor labor rates ($/HR).
Results
Through contractor interviews, Navigant defined the most common house sizes and amount of air leakage reduction. As such, results are presented for each of those categories at a non-regional specific level.

## Res Air Sealing - Results
Residential Air Sealing
Data Vintage | 2011
Does this measure have incremental labor cost (Yes/No)? | No | Measure is Full cost
Return to Measure Index
Full Cost ($)
| Base Cost Factor ($) | Market 1 Northern New England | Market 2 Central/Southern New England | Market 3 New England City | Market 4 NY Metro | Market 5 NY Upstate | Market 6 Mid-Atlantic
Total Cost/SF ($) | 0.46282 | 0.39386 | 0.48716 | 0.51604 | 0.58118 | 0.45761 | 0.42359
Total Cost/CFM ($) | 1.2428 | 1.0576 | 1.3081 | 1.3857 | 1.5606 | 1.2288 | 1.1374
House Size (SF) | Full Cost ($)
| Base Cost Factor ($) | Market 1 Northern New England | Market 2 Central/Southern New England | Market 3 New England City | Market 4 NY Metro | Market 5 NY Upstate | Market 6 Mid-Atlantic
1200 | 555.3783 | 472.6269 | 584.5912 | 619.2468 | 697.4163 | 549.1303 | 508.31
1500 | 694.2229 | 590.7837 | 730.739 | 774.0585 | 871.7704 | 686.4129 | 635.3875
2000 | 925.6305 | 787.7115 | 974.3187 | 1032.078 | 1162.3605 | 915.2171 | 847.1833
2500 | 1157.0381 | 984.6394 | 1217.8983 | 1290.0975 | 1452.9506 | 1144.0214 | 1058.9791
3000 | 1388.4457 | 1181.5673 | 1461.478 | 1548.117 | 1743.5407 | 1372.8257 | 1270.775
CFM Reduced | Full Cost ($)
| Base Cost Factor ($) | Market 1 Northern New England | Market 2 Central/Southern New England | Market 3 New England City | Market 4 NY Metro | Market 5 NY Upstate | Market 6 Mid-Atlantic
250 | 310.6926 | 264.3994 | 327.035 | 346.4222 | 390.1522 | 307.1973 | 284.3614
500 | 621.3851 | 528.7987 | 654.07 | 692.8444 | 780.3044 | 614.3945 | 568.7227
750 | 932.0777 | 793.1981 | 981.105 | 1039.2666 | 1170.4565 | 921.5918 | 853.0841
1000 | 1242.7702 | 1057.5975 | 1308.1399 | 1385.6888 | 1560.6087 | 1228.7891 | 1137.4455
Market | Market Code | Regions |  | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH |  | 0.851
Central/Southern New England | 2 | MA (exc Boston), RI, most CT |  | 1.0526
New England City | 3 | Boston, Providence |  | 1.115
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT |  | 1.2557
NY Upstate | 5 | Buffalo, Rochester etc. |  | 0.98875
Mid-Atlantic | 6 | MD, DE, DC |  | 0.91525
National Average | - | - |  | 1
Summary of incremental cost data analysis for air sealing. Regional adjustment factors are applied to national average incremental costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category . Note: Baseline assumption is no air sealing.

## Res ASHP - README
Residential Air-Source Heat Pumps
Return to Measure Index
Measure Characterization:
| Measure Description | Residential Air-Source Heat Pumps
| Baseline Description | Baseline efficiency Air Source Heat Pump
| Measure Scenario(s) | ROB/NC
| Baseline Efficiency Levels | 13 SEER / 7.7 HSPF
| Efficient Measure Description & Specifications | Efficient Air Source Heat Pump 14.5 SEER / 8.2 HSPF; 15 SEER / 8.5 HSPF
| Sizes | < 65,000 Btu/h
| Distinguishing Features | N/A
| Installation Scenarios | N/A
| Sources | National Grid, Northeast Utilities, NYSERDA, BG&E
| Incremental Labor Cost | No - Labor cost is the same for efficient and baseline equipment.
| Cost Basis | Incremental
| Fuel Type | Electric
| Data Vintage | 2011
Incremental Cost Study Phase One
Published: September, 2011
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the standard (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = measure material cost - base case material cost
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as residential air source heat pump with a SEER greater than or equal to 14.5 at tier 1 or 15 at tier 2.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity. The baseline equipment in this instance is a residential air-source heat pumps with a SEER of 13 which corresponds to the current minimum Federal standard.
Results Tab
The summary of results tab presents the incremental cost for the air-source heat pumps. Material, labor, and installed incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis
Raw Data
A total of 13 contractor interviews were completed for the analysis of the measure, and a total of 43 contractor cost points were collected.
Thirteen contractor interviews were conducted for the analysis of the baseline condition. A total of 17 contractor baseline cost points were collected.
Formatted Data
Primary cost data was collected from contractors across a five states (MA, NH, CT, RI, and MD). Due to the inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in MA than in MD), Navigant adjusted all material and labor cost points to represent non-regional specific (NRS) data using RSMeans CCI. Table 1 provides a regional break down of the NEEP. For example, if the cost provided from a contractor in New York Metro for an air-source heat pump was $1000, than the NRS cost would be:
NRS = Original State Cost ($) / Average Adjustment Factor for Original State
NRS = $1000 / 1.26
NRS = $793.65
The same method was used to adjust all labor cost.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data.
A linear regression was used to develop the material cost for the measure. A regression was done for the following size categories:
a) SEER 13
b) SEER >13
Labor Analysis
Contractor interviews identified no incremental difference in the time to install efficient versus base scenario equipment. In general, efficient equipment took just as much time to install as compared with base equipment. The labor rate was calculated by an average of all contractor labor rates ($/HR). An average installation times was used to determine the time required to install measure and baseline equipment.
Results
Through contractor interviews, Navigant defined the most common unit sizes. As such, results are presented for each of those size categories at a non-regional specific level.

## RES ASHP - Results
Residential Air-Source Heat Pumps
Data Vintage | 2011
Does this measure have incremental labor cost (Yes/No)? | No
Return to Measure Index
Base Cost Factor Results: |  |  |  | Efficiency Level Definitions
Size (Tons) | Base Cost Factor ($/Unit) |  |  |  | SEER | EER | HSPF
| CEE Tier 1 (14.5 SEER) | CEE Tier 2 (15 SEER) |  | Baseline | 13 | --- | 7.7
2 | 993.3221 | 1128.4454 |  | Energy Star | 14.5 | 12 | 8.2
3 | 1335.1978 | 1470.3211 |  | CEE Tier 2 | 15 | 12.5 | 8.5
4 | 1677.0736 | 1812.1969
5 | 2018.9493 | 2154.0726 |  | SEER = Seasonal Energy Efficiency Ratio
EER = Energy Efficiency Ratio
Results by Market: |  |  |  | HSPF = Heating Seasonal Performance Factor
Size (Tons) | Market 1 Northern New England Incremental Cost ($/Unit)
| CEE Tier 1 (14.5 SEER) | CEE Tier 2 (15 SEER)
2 | 845.3171 | 960.3071
3 | 1136.2534 | 1251.2433
4 | 1427.1896 | 1542.1795
5 | 1718.1258 | 1833.1158
Size (Tons) | Market 2 Central/Southern New England Incremental Cost ($/Unit)
| CEE Tier 1 (14.5 SEER) | CEE Tier 2 (15 SEER)
2 | 1045.5708 | 1187.8016
3 | 1405.4292 | 1547.66
4 | 1765.2876 | 1907.5184
5 | 2125.146 | 2267.3768
Size (Tons) | Market 3 New England City Incremental Cost ($/Unit)
| CEE Tier 1 (14.5 SEER) | CEE Tier 2 (15 SEER)
2 | 1107.5541 | 1258.2166
3 | 1488.7456 | 1639.4081
4 | 1869.937 | 2020.5995
5 | 2251.1284 | 2401.7909
Size (Tons) | Market 4 NY Metro Incremental Cost ($/Unit)
| CEE Tier 1 (14.5 SEER) | CEE Tier 2 (15 SEER)
2 | 1247.3642 | 1417.0453
3 | 1676.6747 | 1846.3558
4 | 2105.9851 | 2275.6662
5 | 2535.2956 | 2704.9767
Size (Tons) | Market 5 NY Upstate Incremental Cost ($/Unit)
| CEE Tier 1 (14.5 SEER) | CEE Tier 2 (15 SEER)
2 | 982.1472 | 1115.7504
3 | 1320.1769 | 1453.78
4 | 1658.2065 | 1791.8097
5 | 1996.2361 | 2129.8393
Size (Tons) | Market 6 Mid-Atlantic Incremental Cost ($/Unit)
| CEE Tier 1 (14.5 SEER) | CEE Tier 2 (15 SEER)
2 | 909.1381 | 1032.8097
3 | 1222.0398 | 1345.7114
4 | 1534.9416 | 1658.6132
5 | 1847.8433 | 1971.5149
Market | Market Code | Regions | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.851
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 1.0526
New England City | 3 | Boston, Providence | 1.115
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT, | 1.2557
NY Upstate | 5 | Buffalo, Rochester etc. | 0.98875
Mid-Atlantic | 6 | MD, DE, DC | 0.91525
National Average | - | - | 1
Summary of incremental cost data analysis for residential air-source heat pumps. Regional adjustment factors are applied to national average incremental costs.
Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category
Note: Baseline Assumptions corresponds to Federal Minimum Standard (SEER 13, HSPF 7.7)

## Res Boilers - README
Residential Boilers
Return to Measure Index
Measure Characterization:
| Measure Description | Gas-fired Residential Boilers
| Baseline Description | Gas-fired boiler with AFUE of 80%
| Measure Scenario(s) | ROB, NC
| Baseline Efficiency Levels | AFUE 80%
| Efficient Measure Description & Specifications | Gas-fired boiler with AFUE of 85% or 90%
| Sizes | 50 - 300 MBH
| Distinguishing Features | N/A
| Installation Scenarios | N/A
| Sources | Gas Networks, National Grid, and Vermont Gas
| Incremental Labor Cost | Yes
| Cost Basis | Incremental
| Fuel Type | Gas
| Data Vintage | 2011
Incremental Cost Study Phase One
Published: September, 2011
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the standard (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = measure material cost (material + labor) - base case material cost (material + labor)
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as gas-fired boiler with an AFUE of 85 or 90.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity . The baseline equipment in this instance is a gas-fired boiler with an AFUE of 80% which corresponds to the current minimum Federal standard.
Results Tab
The results tab presents the incremental cost for hot water boilers. Material, labor, and installed incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis
Raw Data
A total of 20 contractor interviews were completed for the analysis of the measure. A total of 128 contractor cost points were collected for hot water boilers and 11 cost points (139 data points in total) for steam boilers were collected.
Formatted Data
Primary cost data was collected from contractors across a three states (NY, VT, and MA). Due to the inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent non-regional specific (NRS) data using RSMeans CCI. Table 1 provides a regional break down of the NEEP. For example, if the cost provided from a contractor in New York Metro for an indirect water heater was $1000, than the NRS cost would be:
NRS = Original State Cost ($) / Average Adjustment Factor for Original State
NRS = $1000 / 1.26
NRS = $793.65
The same method was used to adjust all labor cost.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data.
A linear regression was used to develop the material cost for the measure. A regression was done for the following efficiency categories:
a) AFUE = 80
b) 80 < AFUE =< 96
Labor Analysis
Contractor interviews identified an incremental difference in the time to install efficient versus base scenario equipment. In general, efficient equipment took approximately 12 additional hours to install when compared with base equipment. The labor rate was calculated by a weighted average of all residential gas contractor labor rates ($/HR). An average installation times was used to determine the time required to install measure and baseline equipment.
Results
Through contractor interviews, Navigant defined the most common unit sizes. As such, results are presented for each of those size categories at a non-regional specific level.

## Res Boilers - Results
Residential Boilers
Data Vintage | 2011
Does this measure have incremental labor cost (Yes/No)? | Yes
Return to Measure Index
Base Cost Factor Results:
Size (MBH) | Base Cost Factor ($/Unit)
| CEE Tier 1 (80 to 85 AFUE) | CEE Tier 2 (80 to 90 AFUE)
50 | 501.218 | 2142.4432
75 | 629.6341 | 2270.8593
105 | 783.7334 | 2424.9587
125 | 886.4663 | 2527.6916
150 | 1014.8825 | 2656.1077
175 | 1143.2986 | 2784.5238
200 | 1271.7147 | 2912.9399
225 | 1400.1308 | 3041.3561
250 | 1528.5469 | 3169.7722
300 | 1785.3792 | 3426.6044
Results by Market:
Size (MBH) | Market 1 Northern New England Incremental Cost ($/Unit)
| CEE Tier 1 (80 to 85 AFUE) | CEE Tier 2 (80 to 90 AFUE)
50 | 426.5365 | 1823.2192
75 | 535.8186 | 1932.5013
105 | 666.9572 | 2063.6398
125 | 754.3828 | 2151.0655
150 | 863.665 | 2260.3477
175 | 972.9471 | 2369.6298
200 | 1082.2292 | 2478.9119
225 | 1191.5113 | 2588.194
250 | 1300.7934 | 2697.4761
300 | 1519.3577 | 2916.0404
Size (MBH) | Market 2 Central/Southern New England Incremental Cost ($/Unit)
| CEE Tier 1 (80 to 85 AFUE) | CEE Tier 2 (80 to 90 AFUE)
50 | 527.582 | 2255.1357
75 | 662.7528 | 2390.3065
105 | 824.9578 | 2552.5115
125 | 933.0945 | 2660.6482
150 | 1068.2653 | 2795.819
175 | 1203.4361 | 2930.9898
200 | 1338.6069 | 3066.1606
225 | 1473.7777 | 3201.3314
250 | 1608.9485 | 3336.5022
300 | 1879.2901 | 3606.8438
Size (MBH) | Market 3 New England City Incremental Cost ($/Unit)
| CEE Tier 1 (80 to 85 AFUE) | CEE Tier 2 (80 to 90 AFUE)
50 | 558.858 | 2388.8242
75 | 702.042 | 2532.0082
105 | 873.8628 | 2703.8289
125 | 988.41 | 2818.3761
150 | 1131.5939 | 2961.5601
175 | 1274.7779 | 3104.7441
200 | 1417.9619 | 3247.928
225 | 1561.1459 | 3391.112
250 | 1704.3298 | 3534.296
300 | 1990.6978 | 3820.6639
Size (MBH) | Market 4 NY Metro Incremental Cost ($/Unit)
| CEE Tier 1 (80 to 85 AFUE) | CEE Tier 2 (80 to 90 AFUE)
50 | 629.4045 | 2690.3731
75 | 790.663 | 2851.6316
105 | 984.1733 | 3045.1419
125 | 1113.1801 | 3174.1487
150 | 1274.4386 | 3335.4072
175 | 1435.6972 | 3496.6658
200 | 1596.9557 | 3657.9243
225 | 1758.2143 | 3819.1829
250 | 1919.4728 | 3980.4414
300 | 2241.9899 | 4302.9585
Size (MBH) | Market 5 NY Upstate Incremental Cost ($/Unit)
| CEE Tier 1 (80 to 85 AFUE) | CEE Tier 2 (80 to 90 AFUE)
50 | 495.5793 | 2118.3407
75 | 622.5507 | 2245.3122
105 | 774.9164 | 2397.6779
125 | 876.4936 | 2499.2551
150 | 1003.465 | 2626.2265
175 | 1130.4365 | 2753.1979
200 | 1257.4079 | 2880.1694
225 | 1384.3793 | 3007.1408
250 | 1511.3508 | 3134.1122
300 | 1765.2937 | 3388.0551
Size (MBH) | Market 6 Mid-Atlantic Incremental Cost ($/Unit)
| CEE Tier 1 (80 to 85 AFUE) | CEE Tier 2 (80 to 90 AFUE)
50 | 458.7397 | 1960.8712
75 | 576.2726 | 2078.404
105 | 717.312 | 2219.4434
125 | 811.3383 | 2313.4697
150 | 928.8712 | 2431.0026
175 | 1046.404 | 2548.5354
200 | 1163.9369 | 2666.0683
225 | 1281.4697 | 2783.6011
250 | 1399.0026 | 2901.134
300 | 1634.0683 | 3136.1997
Market | Market Code | Regions | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.851
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 1.0526
New England City | 3 | Boston, Providence | 1.115
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT, | 1.2557
NY Upstate | 5 | Buffalo, Rochester etc. | 0.98875
Mid-Atlantic | 6 | MD, DE, DC | 0.91525
National Average | - | - | 1
Summary of incremental cost data analysis for residential boilers. Regional adjustment factors are applied to national average incremental costs.
Regional adjustment factors were developed using RSMeans City Cost Indexes based on weighted average of division category
Note: Baseline Assumptions corresponds to Federal Minimum AFUE (80%)

## Res CAC - README
Residential Central Air Conditioning
Return to Measure Index
Measure Characterization:
| Measure Description | Residential Central Air Conditioning
| Baseline Description | Residential CAC with SEER of 13
| Measure Scenario(s) | ROB, NC
| Baseline Efficiency Levels | SEER 13
| Efficient Measure Description & Specifications | Residential CAC with SEER rating of 14, 14.5, 15, or 16+
| Sizes | 2 - 5 tons
| Distinguishing Features | N/A
| Installation Scenarios | N/A
| Sources | National Grid, Northeast Utilities, NYSERDA, and BG&E
| Incremental Labor Cost | No - Labor cost is the same for efficient and baseline equipment.
| Cost Basis | Incremental
| Fuel Type | Electric
| Data Vintage | 2011
Incremental Cost Study Phase Two
Published: January, 2013
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the standard (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = measure material cost - base case material cost
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as residential air conditioner with a SEER greater than or equal to 14.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity. The baseline equipment in this instance is a residential central air conditioner with a SEER of 13 which corresponds to the current minimum Federal standard.
Results Tab
The tab presents the incremental cost for the central air conditioners. Material, labor, and installed incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis
Raw Data
A total of 19 contractor interviews were completed for the analysis of the measure a total of 102 contractor cost points were collected.
Nineteen contractor interviews were conducted for the analysis of the baseline condition. A total of 15 contractor baseline cost points were collected.
Formatted Data
Primary cost data was collected from contractors across a five states (NY, NH, VT, MA, and CT). Due to the inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent non-regional specific (NRS) data using RSMeans CCI. Table 1 provides a regional break down of the NEEP. For example, if the cost provided from a contractor in New York Metro for an indirect water heater was $1000, than the NRS cost would be:
NRS = Original State Cost ($) / Average Adjustment Factor for Original State
NRS = $1000 / 1.26
NRS = $793.65
The same method was used to adjust all labor cost.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data.
A linear regression was used to develop the material cost for the measure. A regression was done for the following size categories:
a) SEER 13
b) SEER >13
Labor Analysis
Contractor interviews identified no incremental difference in the time to install efficient versus base scenario equipment. In general, efficient equipment took just as much time to install as compared with base equipment. The labor rate was calculated by an average of all contractor labor rates ($/HR). An average installation times was used to determine the time required to install measure and baseline equipment.
Results
Through contractor interviews, Navigant defined the most common unit sizes. As such, results are presented for each of those size categories at a non-regional specific level.

## Res CAC - Results
Residential Central Air Conditioning
Data Vintage | 2011
Does this measure have incremental labor cost (Yes/No)? | No
Return to Measure Index
Base Cost Factor Results:
Size (Tons) | Base Cost Factor ($/Unit)
| CEE Tier 1 (14.5 SEER) | CEE Tier 2 (15 SEER) | CEE Tier 3 (16+ SEER)
2 | 1141.4706 | 1382.1018 | 2585.2579
3 | 1170.9035 | 1411.5347 | 2614.6908
4 | 1200.3364 | 1440.9676 | 2644.1237
5 | 1229.7693 | 1470.4005 | 2673.5566
Results by Market:
Size (Tons) | Market 1 Northern New England Incremental Cost ($/Unit)
| CEE Tier 1 (14.5 SEER) | CEE Tier 2 (15 SEER) | CEE Tier 3 (16+ SEER)
2 | 971.3915 | 1176.1686 | 2200.0544
3 | 996.4389 | 1201.216 | 2225.1018
4 | 1021.4863 | 1226.2634 | 2250.1492
5 | 1046.5337 | 1251.3108 | 2275.1966
Size (Tons) | Market 2 Central/Southern New England Incremental Cost ($/Unit)
| CEE Tier 1 (14.5 SEER) | CEE Tier 2 (15 SEER) | CEE Tier 3 (16+ SEER)
2 | 1201.5119 | 1454.8004 | 2721.2424
3 | 1232.493 | 1485.7814 | 2752.2235
4 | 1263.4741 | 1516.7625 | 2783.2046
5 | 1294.4552 | 1547.7436 | 2814.1857
Size (Tons) | Market 3 New England City Incremental Cost ($/Unit)
| CEE Tier 1 (14.5 SEER) | CEE Tier 2 (15 SEER) | CEE Tier 3 (16+ SEER)
2 | 1272.7397 | 1541.0435 | 2882.5625
3 | 1305.5574 | 1573.8612 | 2915.3802
4 | 1338.3751 | 1606.6789 | 2948.1979
5 | 1371.1928 | 1639.4966 | 2981.0156
Size (Tons) | Market 4 NY Metro Incremental Cost ($/Unit)
| CEE Tier 1 (14.5 SEER) | CEE Tier 2 (15 SEER) | CEE Tier 3 (16+ SEER)
2 | 1433.4017 | 1735.5743 | 3246.4376
3 | 1470.3621 | 1772.5347 | 3283.3979
4 | 1507.3224 | 1809.4951 | 3320.3583
5 | 1544.2828 | 1846.4554 | 3357.3187
Size (Tons) | Market 5 NY Upstate Incremental Cost ($/Unit)
| CEE Tier 1 (14.5 SEER) | CEE Tier 2 (15 SEER) | CEE Tier 3 (16+ SEER)
2 | 1128.629 | 1366.5532 | 2556.1737
3 | 1157.7308 | 1395.6549 | 2585.2755
4 | 1186.8326 | 1424.7567 | 2614.3773
5 | 1215.9344 | 1453.8585 | 2643.4791
Size (Tons) | Market 6 Mid-Atlantic Incremental Cost ($/Unit)
| CEE Tier 1 (14.5 SEER) | CEE Tier 2 (15 SEER) | CEE Tier 3 (16+ SEER)
2 | 1044.731 | 1264.9687 | 2366.1573
3 | 1071.6694 | 1291.9071 | 2393.0957
4 | 1098.6079 | 1318.8456 | 2420.0342
5 | 1125.5463 | 1345.7841 | 2446.9727
Market | Market Code | Regions | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.851
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 1.0526
New England City | 3 | Boston, Providence | 1.115
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT, | 1.2557
NY Upstate | 5 | Buffalo, Rochester etc. | 0.98875
Mid-Atlantic | 6 | MD, DE, DC | 0.91525
National Average | - | - | 1
Summary of incremental cost data analysis for central AC. Regional adjustment factors are applied to national average incremental costs.
Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category

## Combo Heat HW - README
Combination Heat and Hot Water Boilers
Return to Measure Index
Measure Characterization:
| Efficient Measure Description | Combination Heat and Hot Water Boilers
| Baseline Description | Standard residential gas boiler
| Measure Scenario(s) | ROB
| Baseline Efficiency Levels | 80% AFUE
| Measure Level Description | Residential combination boiler and water heater
| Measure Efficiency Levels | Tier 1: 90 combined appliance efficiency (CAE), Tier 2: 93 CAE, Tier 3: 95 CAE
| Sizes | 110-199 kBtu/h
| Distinguishing Features | Low cost Navien units
| Installation Scenarios | Standard/in-kind replacement of boiler; Existing water heater may also be replaced, but the cost to replace WH is not included in incremental cost, because it is assumed that homeowner installs the measure only when the boiler fails.
| Sources | 2011 ICS, Contractor interviews in MD, MA, NY, and VT
| Incremental Labor Cost | Yes
| Cost Basis | Incremental
| Fuel Type | Gas
| Data Vintage | 2012
Incremental Cost Study Phase Two
Published: January, 2013
Incremental Cost Methodology
The project provides incremental and/or full measure costs, as appropriate to each measure's scenario(s)
Full Measure Costs are used where the scenario assumes that there is no alternative measure .
Incremental Measure Costs are used when an energy-efficient appliance or measure promoted through a program is installed in lieu of the standard (less efficient) appliance/measure. The incremental cost is the difference between the baseline energy efficiency measure (material and labor) and the standard efficiency model. The equation for calculating incremental measure costs is simply:
Incremental measure cost = energy efficient measure cost (material + labor) - standard efficient baseline cost (material + labor)
In some cases there is no difference in the installation cost between the standard and efficient measure and/or an efficient measure and a more efficient measure. In those cases only materials costs are provided in the incremental cost.
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as a combination heat and hot water boiler with a combination appliance efficiency (CAE) of 90 or above.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity . The baseline equipment in this instance is a standard hot water boiler with an annual fuel utilization efficiency (AFUE) of 80 which corresponds to the current minimum Federal standard.
Incremental path: The baseline equipment set up also includes a standard storage tank water heater, however, this equipment is not included in the baseline equipment costs. This analysis assumes that a homeowner's boiler fails and decides to either replace the existing boiler in-kind, or opt for replacing the boiler and water heater with an efficient combination unit. Therefore, the cost to replace a water heater is excluded from a homeowner's consideration and this analysis.
The users of this data should note that this workbook also includes full costs for combination heat and hot water boilers. Therefore, other incremental path scenarios can be created by combining this data with other full cost data for baseline boilers and/or water heaters.
Workbook Elements
Results Tab
The results tab presents the incremental cost for the combination. Material, labor, and installed incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Base Cost Factor category).
Data Analysis
Raw Data
In 2012, a total of 10 contractor interviews were completed for the analysis of the measure. A total of 33 cost points were collected for combination equipment. The 2012 analysis also incorporated the 2011 Combination boiler data (excluding Navien units) to strengthen the dataset. Additional baseline boiler costs were sourced from the 2011 boilers analysis worksheet titled "NEEP Residential Boilers 2011_04_29.xlsx."
Formatted Data
Primary cost data was collected from contractors across four states (MD, MA, NY, and VT). Due to the inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent the Base Cost Factors (BCF) using RSMeans CCI. Table 1 provides a regional break down of NEEP. For example, if the material cost provided from a contractor in New York Metro for a combination unit was $2,000, than the BCF cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $2,000 / 1.03
BCF = $1,936.58
The same method was used to adjust all labor costs.
Some internet costs were included in the analysis to augment and QC the contractor data. Internet costs do not include a contractor markup. Additionally, distributor costs do not include contractor markup. Therefore and where available, estimated markups were gathered from contractors and distributors. This average markup was applied to the internet and distributor costs to produce estimated contractor costs.
Similarly, once BCF costs were determined for each measure, the costs were then allocated to each market by multiplying the BCF cost by the individual market factor.
The R.S. Means recalculated CCI factors annually. For this study, Navigant used the 2012 CCI factors. Additionally, any older data, collected for the ICS Phase One Report or other sources , was updated with the 2012 factors to maintain comparability with data collected in 2012 for the ICS Phase Two.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data.
A linear regression was used to develop the material cost for the measure. A regression was done for the entire range of efficiencies and burner inputs. For the baseline material, the results of the boilers analysis for the baseline equipment were sourced.
Labor Analysis
Contractor interviews identified an incremental difference in the time to install efficient versus base scenario equipment. In general, efficient equipment took approximately 14 additional hours to install when compared with base equipment. An average installation time was used to determine the time required to install baseline and measure equipment.
Results
Through contractor and distributor interviews, Navigant defined the most common unit sizes installed in homes. As such, results are presented for each of those size categories at a Base Cost Factor level.

## Combo Heat HW - Results
Combination Heat and Hot Water Boilers
Data Vintage | 2012
Does this measure have incremental labor cost (Yes/No)? | Yes | This measure has an incremental labor cost between baseline and efficient measure but the labor increment is constant across size and efficiency
Return to Measure Index
Base Cost Factor Results:
Size (MBH) | Base Cost Factor - Incremental Cost ($/Unit)
| 90 CAE | 91 CAE | 93 CAE | 95 CAE
110 | 1779.5852 | 2059.371 | 2618.9425 | 3178.5141
120 | 1835.5656 | 2115.3514 | 2674.923 | 3234.4945
126 | 1869.1539 | 2148.9397 | 2708.5113 | 3268.0828
150 | 2003.507 | 2283.2928 | 2842.8644 | 3402.4359
199 | 2277.8113 | 2557.597 | 3117.1686 | 3676.7402
Results by Market:
Size (MBH) | Market 1 Northern New England Incremental Cost ($/Unit) (Baseline = Standard Hot Water Boiler, 80 AFUE)
| 90 CAE | 91 CAE | 93 CAE | 95 CAE
110 | 1391.6209 | 1665.5312 | 2213.3517 | 2761.1723
120 | 1446.4257 | 1720.336 | 2268.1566 | 2815.9772
126 | 1479.3087 | 1753.2189 | 2301.0395 | 2848.8601
150 | 1610.8404 | 1884.7506 | 2432.5712 | 2980.3918
199 | 1879.3842 | 2153.2945 | 2701.1151 | 3248.9356
Size (MBH) | Market 2 Central/Southern New England Average Incremental Cost ($/Unit) (Baseline = Standard Hot Water Boiler, 80 AFUE)
| 90 CAE | 91 CAE | 93 CAE | 95 CAE
110 | 1930.8058 | 2207.4021 | 2760.5945 | 3313.787
120 | 1986.1481 | 2262.7443 | 2815.9368 | 3369.1292
126 | 2019.3535 | 2295.9497 | 2849.1422 | 3402.3346
150 | 2152.175 | 2428.7712 | 2981.9636 | 3535.1561
199 | 2423.3521 | 2699.9484 | 3253.1408 | 3806.3333
Size (MBH) | Market 3 New England City Incremental Cost ($/Unit) (Baseline = Standard Hot Water Boiler, 80 AFUE)
| 90 CAE | 91 CAE | 93 CAE | 95 CAE
110 | 2074.5591 | 2357.7023 | 2923.9887 | 3490.2752
120 | 2131.2113 | 2414.3545 | 2980.641 | 3546.9274
126 | 2165.2026 | 2448.3459 | 3014.6323 | 3580.9187
150 | 2301.168 | 2584.3112 | 3150.5976 | 3716.8841
199 | 2578.7639 | 2861.9071 | 3428.1935 | 3994.48
Size (MBH) | Market 4 NY Metro Incremental Cost ($/Unit) (Baseline = Standard Hot Water Boiler, 80 AFUE)
| 90 CAE | 91 CAE | 93 CAE | 95 CAE
110 | 2462.3792 | 2751.3279 | 3329.2255 | 3907.123
120 | 2520.193 | 2809.1418 | 3387.0393 | 3964.9368
126 | 2554.8813 | 2843.83 | 3421.7276 | 3999.6251
150 | 2693.6344 | 2982.5832 | 3560.4808 | 4138.3783
199 | 2976.9222 | 3265.8709 | 3843.7685 | 4421.666
Size (MBH) | Market 5 NY Upstate Incremental Cost ($/Unit) (Baseline = Standard Hot Water Boiler, 80 AFUE)
| 90 CAE | 91 CAE | 93 CAE | 95 CAE
110 | 1773.7335 | 2049.9521 | 2602.3891 | 3154.8261
120 | 1829.0003 | 2105.2188 | 2657.6558 | 3210.0928
126 | 1862.1603 | 2138.3788 | 2690.8158 | 3243.2529
150 | 1994.8004 | 2271.0189 | 2823.4559 | 3375.893
199 | 2265.6073 | 2541.8258 | 3094.2628 | 3646.6998
Size (MBH) | Market 6 Mid-Atlantic Incremental Cost ($/Unit) (Baseline = Standard Hot Water Boiler, 80 AFUE)
| 90 CAE | 91 CAE | 93 CAE | 95 CAE
110 | 1645.5308 | 1924.757 | 2483.2095 | 3041.6619
120 | 1701.3993 | 1980.6255 | 2539.078 | 3097.5304
126 | 1734.9204 | 2014.1466 | 2572.5991 | 3131.0515
150 | 1869.0048 | 2148.231 | 2706.6835 | 3265.1359
199 | 2142.7605 | 2421.9867 | 2980.4391 | 3538.8915
Market | Market Code | Regions |  | Material Adjustment Factor | Labor Adjustment Factor
Northern New England | 1 | ME, VT, NH |  | 0.979 | 0.6875
Central/Southern New England | 2 | MA (exc Boston), RI, most CT |  | 0.9886 | 1.1312
New England City | 3 | Boston, Providence |  | 1.012 | 1.2395
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT |  | 1.0328 | 1.552
NY Upstate | 5 | Buffalo, Rochester etc. |  | 0.98725 | 1.0012
Mid-Atlantic | 6 | MD, DE, DC |  | 0.998 | 0.8895
Base Cost Factor | - | - |  | 1 | 1
Summary of incremental cost data analysis for Combination Heat and Hot Water Boilers. Regional adjustment factors are applied to the Base Cost Factors (BCFs) to calculate market specific results. Regional adjustment factors were developed using RSMeans City Cost Indexes based on weighted average of division category.
Note: Baseline assumptions correspond to a standard hot water residential boiler rated at the Federal Minimum Annual Fuel Utilization Efficiency (80 AFUE).

## Res Furnace - README
Residential Furnaces
Return to Measure Index
Measure Characterization:
| Efficient Measure Description | Residential Furnaces
| Baseline Description | Gas Furnace with AFUE of 80%
| Measure Scenario(s) | ROB, NC
| Baseline Efficiency Levels | AFUE 80%
| Efficient Measure Description & Specifications | Gas Furnace with AFUE of 90%, 92%, or 94%
| Sizes | 60 - 120 MBH
| Distinguishing Features | N/A
| Installation Scenarios | N/A
| Sources | Gas Networks, National Grid, NYSERDA, and Vermont Gas
| Incremental Labor Cost | No - Labor cost is the same for efficient and baseline equipment.
| Cost Basis | Incremental
| Fuel Type | Gas
| Data Vintage | 2011
Incremental Cost Study Phase One
Published: September, 2011
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the standard (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = measure material cost - base case material cost
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as gas furnace with an AFUE of 90, 92 or 94.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity . The baseline equipment in this instance is a gas furnace with an AFUE of 80% which corresponds to the current minimum Federal standard.
Results Tab
The results tab presents the incremental cost for the gas furnaces. Material, labor, and installed incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis
Raw Data
A total of 15 contractor interviews were completed for the analysis of the measure. A total of 32 contractor cost points and 23 internet cost points were collected for residential gas furnaces.
Formatted Data
Primary cost data was collected from contractors across a three states (NY, VT, and MA). Due to the inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent non-regional specific (NRS) data using RSMeans CCI. Table 1 provides a regional break down of the NEEP. For example, if a the cost provided from a contractor in New York Metro for gas furnace was $1000, than the NRS cost would be:
NRS = Original State Cost ($) / Average Adjustment Factor for Original State
NRS = $1000 / 1.26
NRS = $793.65
The same method was used to adjust all labor cost.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data.
A linear regression was used to develop the material cost for the measure. A regression was done for the following efficiency categories:
a) AFUE = 80
b) 80 < AFUE =< 97
Labor Analysis
Contractor interviews identified an incremental difference in the time to install efficient versus base scenario equipment. In general, efficient equipment took approximately 4 additional hours to install when compared with base equipment. The labor rate was calculated with a weighted average of all contractor labor rates ($/HR) collected for residential gas measures. An average installation times was used to determine the time required to install measure and baseline equipment.
Results
Through contractor interviews, Navigant defined the most common unit sizes. As such, results are presented for each of those size categories at a non-regional specific level.

## Res Furnace - Results
Residential Furnace with Electronically Commutated Motors (ECMs)
Data Vintage | 2011
Does this measure have incremental labor cost (Yes/No)? | No
Return to Measure Index
Base Cost Factor Results:
Size (MBH) | Base Cost Factor ($/Unit)
| CEE Tier 1 (90 AFUE) | CEE Tier 2 (92 AFUE) | CEE Tier 3 (94 AFUE)
60 | 1130.6185 | 1284.4584 | 1438.2983
70 | 1140.4383 | 1294.2782 | 1448.1181
80 | 1150.2582 | 1304.0981 | 1457.938
90 | 1160.078 | 1313.9179 | 1467.7578
100 | 1169.8978 | 1323.7377 | 1477.5776
120 | 1189.5374 | 1343.3773 | 1497.2172
Results by Market:
Size (MBH) | Market 1 Northern New England Incremental Cost ($/Unit)
| CEE Tier 1 (90 AFUE) | CEE Tier 2 (92 AFUE) | CEE Tier 3 (94 AFUE)
60 | 962.1564 | 1093.0741 | 1223.9919
70 | 970.513 | 1101.4308 | 1232.3485
80 | 978.8697 | 1109.7874 | 1240.7052
90 | 987.2264 | 1118.1441 | 1249.0619
100 | 995.583 | 1126.5008 | 1257.4185
120 | 1012.2963 | 1143.2141 | 1274.1319
Size (MBH) | Market 2 Central/Southern New England Incremental Cost ($/Unit)
| CEE Tier 1 (90 AFUE) | CEE Tier 2 (92 AFUE) | CEE Tier 3 (94 AFUE)
60 | 1190.0891 | 1352.0209 | 1513.9528
70 | 1200.4254 | 1362.3573 | 1524.2892
80 | 1210.7617 | 1372.6936 | 1534.6255
90 | 1221.0981 | 1383.03 | 1544.9618
100 | 1231.4344 | 1393.3663 | 1555.2982
120 | 1252.1071 | 1414.039 | 1575.9708
Size (MBH) | Market 3 New England City Incremental Cost ($/Unit)
| CEE Tier 1 (90 AFUE) | CEE Tier 2 (92 AFUE) | CEE Tier 3 (94 AFUE)
60 | 1260.6397 | 1432.1711 | 1603.7026
70 | 1271.5888 | 1443.1202 | 1614.6517
80 | 1282.5378 | 1454.0693 | 1625.6008
90 | 1293.4869 | 1465.0184 | 1636.5499
100 | 1304.436 | 1475.9675 | 1647.499
120 | 1326.3342 | 1497.8657 | 1669.3972
Size (MBH) | Market 4 NY Metro Incremental Cost ($/Unit)
| CEE Tier 1 (90 AFUE) | CEE Tier 2 (92 AFUE) | CEE Tier 3 (94 AFUE)
60 | 1419.7742 | 1612.9587 | 1806.1431
70 | 1432.1055 | 1625.2899 | 1818.4744
80 | 1444.4367 | 1637.6211 | 1830.8056
90 | 1456.7679 | 1649.9524 | 1843.1368
100 | 1469.0991 | 1662.2836 | 1855.4681
120 | 1493.7616 | 1686.9461 | 1880.1305
Size (MBH) | Market 5 NY Upstate Incremental Cost ($/Unit)
| CEE Tier 1 (90 AFUE) | CEE Tier 2 (92 AFUE) | CEE Tier 3 (94 AFUE)
60 | 1117.8991 | 1270.0083 | 1422.1175
70 | 1127.6084 | 1279.7176 | 1431.8268
80 | 1137.3178 | 1289.427 | 1441.5362
90 | 1147.0271 | 1299.1363 | 1451.2455
100 | 1156.7364 | 1308.8456 | 1460.9548
120 | 1176.1551 | 1328.2643 | 1480.3735
Size (MBH) | Market 6 Mid-Atlantic Incremental Cost ($/Unit)
| CEE Tier 1 (90 AFUE) | CEE Tier 2 (92 AFUE) | CEE Tier 3 (94 AFUE)
60 | 1034.7986 | 1175.6006 | 1316.4025
70 | 1043.7862 | 1184.5882 | 1325.3901
80 | 1052.7738 | 1193.5757 | 1334.3777
90 | 1061.7614 | 1202.5633 | 1343.3653
100 | 1070.749 | 1211.5509 | 1352.3529
120 | 1088.7241 | 1229.5261 | 1370.3281
Market | Market Code | Regions | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.851
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 1.0526
New England City | 3 | Boston, Providence | 1.115
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT | 1.2557
NY Upstate | 5 | Buffalo, Rochester etc. | 0.98875
Mid-Atlantic | 6 | MD, DE, DC | 0.91525
National Average | - | - | 1
Summary of incremental cost data analysis for gas furnaces. Regional adjustment factors are applied to national average incremental costs.
Regional adjustment factors were developed using RSMeans City Cost Indexes based on weighted average of division category
Note: Baseline Assumptions corresponds to Federal Minimum AFUE (80%)

## Heat Pump Wtr Heater - README
Heat Pump Water Heater
Return to Measure Index
Measure Characterization:
|  | Efficient Measure Description | Heat Pump Water Heater
|  | Baseline Description | Baseline electric resistance storage water heater
|  | Measure Scenario(s) | RET, ROB, NC This measure includes incremental labor costs
|  | Baseline Efficiency Levels | Standard Natural Gas, LP or oil storage water heater EF= 0.62
|  | Efficient Measure Description & Specifications | Heat Pump storage water heater installed in conditioned or semi-conditioned space
RET: vs. existing electric resistance storage water heater
ROB and NC: vs. standard EF electric resistance water heater EF = 0.97 - (0.00132 * Vol. in gal.)
PSNH, NSTAR, Nat. Grid require Energy Star* HPWH with EF >= 2.3, min 1st hour recovery of 60 gallons
CT L&P, BGE, PEPCO require Energy Star* Heat Pump water heater EF >= 2.0
Con Ed requires EF >= 2.0 only
* Energy Star requires EF >= 2.0 and minimum 1st Hour Rating of 50 gallons
|  | Sizes | Residential sizes: 50 and 80 gallons
|  | Distinguishing Features | Rebates available to PSNH, NSTAR, BGE, PEPCO, National Grid (MA), CT L&P, and Con Ed customers
|  | Installation Scenarios | Replacing an electric water heater in conditioned or unconditioned interior space.
|  | Sources | Mid-Atlantic TRM, EVT TRM, NY TRM, Energy Star draft criteria.
|  | Comments | Base values taken from notice of final rule. 77 FR 74559 (Dec. 17, 2012). Study will accommodate Energy Star and higher efficiency standards in CT, MA, NH
|  | Incremental Labor Cost | Yes
|  | Cost Basis | Incremental
|  | Fuel Type | Electric
|  | Data Vintage | 2013
0.75
Incremental Cost Study Phase Three
Published: May, 2014
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the standard (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = efficient measure cost (material and labor) - base case cost (material and labor)
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as a heat pump water heater with an energy factor ranging from 2.00 to 2.51.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity . The baseline equipment in this instance is a standard storage-type, electric resistance water heater. Energy factor varies with storage volume. However, 50, 60, and 80 gallon storage tanks are the most common units. The corresponding current minimum Federal standard is 0.86 to 0.90 EF for this size range.
Workbook Elements
Results Tab
The results tab presents the incremental cost for the heat pump water heaters. Material, labor, and installed incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Base Cost Factor category).
Data Analysis
Raw Data
Navigant completed 2 in-depth interviews with installing contractors to understand the typical installation practices and associated costs for heat pump water heater retrofits. Additionally, over 2,100 cost points from program tracking data supports the analysis. Finally, the analysis leveraged findings from previous ICS evaluations where applicable.
Formatted Data
Primary cost data was collected from in-depth interviews and program tracking data across multiple states including MA, MD, and RI. Due to the inherent differences in cost from one region to another (e.g. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent base cost factor (BCF) data using RSMeans CCI. Table 1 provides a regional break down of NEEP. For example, if the material cost provided from a contractor in New York Metro for a heat pump water heater was $2,000, than the BCF cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $2,000 / 1.03
BCF = $1,936.58
The same method was used to adjust all labor costs.
Costs leveraged from previous ICS evaluations were inflated to 2013/2014 costs using DOE's implicit price deflator.
http://www.bea.gov/iTable/iTable.cfm?ReqID=9&step=1
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data.
A linear regression was used to develop the material cost for the measure. A regression was done for the entire range of gallon sizes. The analysis determined that efficiency is not a significant driver of cost. For the baseline material, a simple average was conducted to determine the average price for baseline units using the in-depth interview findings.
Labor Analysis
Contractor interviews identified an incremental difference in the time to install efficient versus base scenario equipment. The analysis also identified the labor difference between standard or simple installations and complex installations that require significant reworking of electrical systems, condensate drains, or venting. Installation times were taken from the in-depth interviews. Finally, the labor rate was calculated with a weighted average of all contractor labor rates ($/HR) collected for residential gas measures from previous ICS efforts that were also adjusted for inflation. This final value matched closely to the average labor rated determined from the in-depth interviews.
Measure Characterization
The measure characterization for heat pump water heaters is presented to the right and provides additional context around how Navigant characterized this measure.
Results
Results are presented for each common tank size at the BCF level. Note, that the user of this spreadsheet should select the type of installation in cell DX7.

## Heat Pump Wtr Heater - Results
Heat Pump Water Heater
Data Vintage | 2013
Does this measure have incremental labor cost (Yes/No)? | Yes
Installation type (DROP DOWN MENU) | Standard installation
Return to Measure Index
Base Cost Factor Results:
Observation | Baseline Storage Water Heater |  | Base Cost Factor Incremental Cost ($/Unit)
| Gallon Size | Efficiency (EF) | Heat Pump Water Heater (2.00 EF to 2.51 EF)
1 | 50 | 0.904 | 1029.3905
2 | 60 | 0.8908 | 1091.816
3 | 80 | 0.8644 | 1216.6671
Results by Market:
Observation | Baseline Storage Water Heater |  | Market 1 Northern New England Incremental Cost ($/Unit)
| Gallon Size | Efficiency (EF) | Heat Pump Water Heater (2.00 EF to 2.51 EF)
1 | 50 | 0.904 | 818.3147
2 | 60 | 0.8908 | 876.2654
3 | 80 | 0.8644 | 992.167
Observation | Baseline Storage Water Heater |  | Market 2 Central/Southern New England Incremental Cost ($/Unit)
| Gallon Size | Efficiency (EF) | Heat Pump Water Heater (2.00 EF to 2.51 EF)
1 | 50 | 0.904 | 1176.0196
2 | 60 | 0.8908 | 1235.4085
3 | 80 | 0.8644 | 1354.1862
Observation | Baseline Storage Water Heater |  | Market 3 New England City Incremental Cost ($/Unit)
| Gallon Size | Efficiency (EF) | Heat Pump Water Heater (2.00 EF to 2.51 EF)
1 | 50 | 0.904 | 1318.6553
2 | 60 | 0.8908 | 1382.5621
3 | 80 | 0.8644 | 1510.3758
Observation | Baseline Storage Water Heater |  | Market 4 NY Metro Incremental Cost ($/Unit)
| 0.75 | Efficiency (EF) | Heat Pump Water Heater (2.00 EF to 2.51 EF)
1 | 50 | 0.904 | 1620.5912
2 | 60 | 0.8908 | 1688.155
3 | 80 | 0.8644 | 1823.2826
Observation | Baseline Storage Water Heater |  | Market 5 NY Upstate Incremental Cost ($/Unit)
| Gallon Size | Efficiency (EF) | Heat Pump Water Heater (2.00 EF to 2.51 EF)
1 | 50 | 0.904 | 1028.684
2 | 60 | 0.8908 | 1088.6099
3 | 80 | 0.8644 | 1208.4615
Observation | Baseline Storage Water Heater |  | Market 6 Mid-Atlantic Incremental Cost ($/Unit)
| Gallon Size | Efficiency (EF) | Heat Pump Water Heater (2.00 EF to 2.51 EF)
1 | 50 | 0.904 | 908.9516
2 | 60 | 0.8908 | 970.0347
3 | 80 | 0.8644 | 1092.2009
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor | Total
Northern New England | 1 | ME, VT, NH | 0.97583 | 0.81533 | 0.90417
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9836 | 1.1632 | 1.0628
New England City | 3 | Boston, Providence | 1.008 | 1.2795 | 1.1275
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT | 1.0278 | 1.5593 | 1.262
NY Upstate | 5 | Buffalo, Rochester etc. | 0.9865 | 1.0135 | 0.99825
Mid-Atlantic | 6 | MD, DE, DC | 0.99275 | 0.88775 | 0.94625
Base Cost Factor Average | - | - | 1 | 1 | 1
Summary of incremental cost data analysis for heat pump water heaters. Regional adjustment factors are applied to Base Cost Factor incremental costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category. Two installation scenarios were analyzed:
(1) Standard installation: Replacement of existing water heater with minimal changes required for new system;
(2) Complex installation: Installation requires significant reworking of electrical systems, site conditions, and/or venting, usually in a finished basement
The user may toggle between the two installation scenarios in cell C8.
Note: Baseline assumptions correspond to a standard electric resistant tank water heater at the Federal Minimum Energy Factor.

## Res Indirect HW - README
Residential Indirect Hot Water Heaters
Return to Measure Index
Measure Characterization:
| Efficient Measure Description | Residential Indirect Water Heaters
| Baseline Description | Gas-fired 40 gallon storage water heater with EF of 59
| Measure Scenario(s) | ROB, NC
| Baseline Efficiency Levels | 40-gal. Storage Water Heater (SWH) at 59 EF
| Measure Level Description | Indirect Water Heater
| Measure Efficiency Levels | Indirect Water Heater at 40 - 120 MBH Indirect Input Ratings
| Sizes | 40 - 120 MBH
| Distinguishing Features | N/A
| Installation Scenarios | N/A
| Sources | Internet, Gas Networks, National Grid, and Northeast Utilities
| Incremental Labor Cost | Yes
| Cost Basis | Incremental
| Fuel Type | Gas
| Data Vintage | 2011
Incremental Cost Study Phase One
Published: September, 2011
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the standard (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = measure material and labor cost - base case material and labor cost
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as an indirect water heater of a specified capacity.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity . The baseline equipment in this instance is a gas-fired storage water heater with an energy factor of 59 and a capacity of 40 gallons. 59 EF is the current minimum Federal standard for gas-fired storage water heaters rated at 40 gallons.
Results Tab
The results tab presents the incremental cost for the indirect hot water heaters. Material, labor, and installed incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis
Raw Data
A total of 15 contractor interviews were completed for the analysis of the measure. Navigant incorporated internet cost data into the primary contractor data in order to strengthen the analysis. A total of 21 contractor cost points and 18 internet cost points (49 data points in total) were collected.
Fifteen contractor interviews were conducted for the analysis of the baseline condition. Baseline data was also supplemented with internet cost data. Cost data collected through the Internet can provide many useful purposes because it is extensive, transparent, and easily accessible. A total of 15 contractor cost points and 9 internet cost points (24 data points in total) were collected.
Formatted Data
Primary cost data was collected from contractors across a five states (NY, NH, VT, MA, and CT). Due to the inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent non-regional specific (NRS) data using RSMeans CCI. Table 1 provides a regional break down of the NEEP. For example, if the cost provided from a contractor in New York Metro for an indirect water heater was $1000, than the NRS cost would be:
NRS = Original State Cost ($) / Average Adjustment Factor for Original State
NRS = $1000 / 1.26
NRS = $793.65
The same method was used to adjust all labor cost.
Internet Markup Tab
Measure Data
A percent markup was applied to the internet cost data. A weighted average (based on unit capacity) difference was calculated for the cost points collect from contractors and internet costs. A percent markup of 115% was applied to all internet cost points.
Baseline Data
A percent markup was applied to the internet cost. An average difference was calculated for the cost points collect from contractors and internet costs. A percent markup of 117% was applied to all internet cost points.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data.
A linear regression was used to develop the material cost for the measure. A regression was done for the following size categories:
a) 28 <= Gallon < 50
b) 50 <= Gallon < 80
c) 80 <= Gallon =<120
A simple average was used to calculate the cost of the baseline unit.
Labor Analysis
Contractor interviews identified an incremental difference in the time to install efficient versus base scenario equipment. In general, efficient equipment took approximately 3 additional hours to install when compared with base equipment. The labor rate was calculated with a weighted average of all contractor labor rates ($/HR) collected for residential gas measures. An average installation times was used to determine the time required to install measure and baseline equipment.
Results
Through contractor interviews, Navigant defined the most common unit sizes as 40, 60, 80, and 120 gallons. As such, results are presented for each of those size categories at a non-regional specific level.

## Res Indirect HW - Results
Residential Indirect Hot Water Heaters
Data Vintage | 2011
Does this measure have incremental labor cost (Yes/No)? | No | Labor costs are included in Full cost but are not incremental for increased unit size.
Return to Measure Index
Base Cost Factor Results:
Size (MBH) | Base Cost Factor ($/Unit)
| Material Cost | Labor Cost | Installed Cost
40 | 846.206 | 240.0513 | 1086.2573
60 | 1207.7782 | 240.0513 | 1447.8295
80 | 1528.9589 | 240.0513 | 1769.0101
120 | 2093.4761 | 240.0513 | 2333.5274
Results by Market:
Size (MBH) | Market 1 Northern New England Incremental Cost ($/Unit)
| Material Cost | Labor Cost | Installed Cost
40 | 720.1213 | 204.2836 | 924.4049
60 | 1027.8193 | 204.2836 | 1232.1029
80 | 1301.144 | 204.2836 | 1505.4276
120 | 1781.5482 | 204.2836 | 1985.8318
Size (MBH) | Market 2 Central/Southern New England Incremental Cost ($/Unit)
| Material Cost | Labor Cost | Installed Cost
40 | 890.7164 | 252.678 | 1143.3944
60 | 1271.3074 | 252.678 | 1523.9853
80 | 1609.3821 | 252.678 | 1862.0601
120 | 2203.593 | 252.678 | 2456.2709
Size (MBH) | Market 3 New England City Incremental Cost ($/Unit)
| Material Cost | Labor Cost | Installed Cost
40 | 943.5197 | 267.6572 | 1211.1769
60 | 1346.6727 | 267.6572 | 1614.3299
80 | 1704.7891 | 267.6572 | 1972.4463
120 | 2334.2259 | 267.6572 | 2601.883
Size (MBH) | Market 4 NY Metro Incremental Cost ($/Unit)
| Material Cost | Labor Cost | Installed Cost
40 | 1062.6232 | 301.4444 | 1364.0676
60 | 1516.6675 | 301.4444 | 1818.1119
80 | 1919.9901 | 301.4444 | 2221.4345
120 | 2628.8826 | 301.4444 | 2930.327
Size (MBH) | Market 5 NY Upstate Incremental Cost ($/Unit)
| Material Cost | Labor Cost | Installed Cost
40 | 836.6862 | 237.3507 | 1074.0369
60 | 1194.1907 | 237.3507 | 1431.5414
80 | 1511.7581 | 237.3507 | 1749.1088
120 | 2069.9245 | 237.3507 | 2307.2752
Size (MBH) | Market 6 Mid-Atlantic Incremental Cost ($/Unit)
| Material Cost | Labor Cost | Installed Cost
40 | 774.49 | 219.7069 | 994.197
60 | 1105.419 | 219.7069 | 1325.1259
80 | 1399.3796 | 219.7069 | 1619.0865
120 | 1916.054 | 219.7069 | 2135.7609
Market | Market Code | Regions | Average Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.851
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 1.0526
New England City | 3 | Boston, Providence | 1.115
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT, | 1.2557
NY Upstate | 5 | Buffalo, Rochester etc. | 0.98875
Mid-Atlantic | 6 | MD, DE, DC | 0.91525
National Average | - | - | 1
Summary of incremental cost data analysis for Indirect Hot Water Heaters. Regional adjustment factors are applied to national average incremental costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category
Note: Baseline Assumptions corresponds to Federal Minimum Efficiency of 58%

## Res Insulation - README
Residential Insulation
Return to Measure Index
Measure Characterization:
| Efficient Measure Description | Residential Attic Insulation
| Baseline Description | Attic with No or Negligible Insulation
| Measure Scenario(s) | RET
| Baseline Efficiency Levels | N/A
| Measure Level Description | Open Blow Attic with Cellulose Insulation
| Measure Efficiency Levels | R38, R49, and R60
| Sizes | N/A
| Distinguishing Features | N/A
| Installation Scenarios | N/A
| Sources | CL&P, NYSERDA, and BG&E
| Full Labor Cost | Yes
| Cost Basis | Full | Changed Cost basis
| Fuel Type | Gas
| Data Vintage | 2012
Incremental Cost Study Phase Two
Published: January, 2013
Incremental Cost Methodology
The project provides incremental and/or full measure costs, as appropriate to each measure's scenario(s)
Full Measure Costs are used where the scenario assumes that there is no alternative measure .
Incremental Measure Costs are used when an energy-efficient appliance or measure promoted through a program is installed in lieu of the standard (less efficient) appliance/measure. The incremental cost is the difference between the baseline energy efficiency measure (material and labor) and the standard efficiency model. The equation for calculating incremental measure costs is simply:
Incremental measure cost = energy efficient measure cost (material + labor) - standard efficient baseline cost (material + labor)
In some cases there is no difference in the installation cost between the standard and efficient measure and/or an efficient measure and a more efficient measure. In those cases only materials costs are provided in the incremental cost.
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is the level of insulation installed. In an insulation retrofit, the measure cost is the full install cost.
Baseline: The baseline condition is defined as the standard condition, without the utility EE activity. The baseline condition in this case is no action ($0 installation cost).
Workbook Elements
Results Tab
The results tab presents the cost for insulation. Material, labor, and total installed costs are presented for 7 different markets, allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Base Cost Factor category).
Data Analysis
Raw Data
A total of 14 contractor interviews were completed for the cost analysis of insulation.
Formatted Data
Primary cost data was collected from contractors across three states (MD, CT, and NY). Due to the inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent base cost factor (BCF) data using RSMeans CCI. Table 1 provides a regional break down of the NEEP. For example, if a material cost provided from a contractor in New York Metro was $1000, than the BCF cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $1000 / 1.01
BCF = $990.10
The same method was used to adjust all labor cost.
Similarly, once BCF costs were determined for each measure, the costs were then allocated to each market by multiplying the BCF cost by the individual market factor.
The R.S. Means recalculated CCI factors annually. For this study, Navigant used the 2012 CCI factors. Additionally, any older data, collected for the ICS Phase One Report or other sources , was updated with the 2012 factors to maintain comparability with data collected in 2012 for the ICS Phase Two.
Material Analysis
The analysis includes all collected data points, as none were deemed to be outliers. The reported man-hours and hourly rates had high variance, but as discussed in the Labor Analysis, they were not used in the calculations, only for reference. Some of these values would likely have been deemed outliers if they were used to calculate the results.
A linear regression was used to develop the material cost for the measure.
Labor Analysis
The labor rate was calculated as the difference (per square foot) between the total installed cost and the material cost (both values provided by contractor interviewees). This method was selected due to the high variation in responses for hourly rates and man-hours to complete a job. (However both hourly rates and man-hours were collected for comparison purposes.)
Results
The Summary of Results tab presents geographically normalized data for each pre-defined region. The results are based upon the sum of geographically normalized costs for materials and labor. These values are then adjusted for each given market. Since these are normalized, it is important to understand that no contractor specifically reported (or charged) these costs per square foot. The results are intended to be representative of what a participant would find in his or her respective region.

## Res Insulation - Results
Residential Insulation
Data Vintage | 2012
Does this measure have incremental labor cost (Yes/No)? | NO | Labor costs are included in Full cost but are not incremental for increased insulation amounts.
Return to Measure Index
Base Cost Factor Results:
Blown Cellulose Attic Insulation | Base Cost Factor - Full Cost ($/SF)
| 38 | 49 | 60
Material Costs | 1.1473 | 1.2361 | 1.3248
Labor Costs | 0.7709 | 0.7709 | 0.7709
Total Full Installed Cost | 1.9182 | 2.007 | 2.0957
Results by Market:
Market | Base Cost Factors by Individual Market ($/SF)
| 38 | 49 | 60
Market 1 Northern New England | 1.6532 | 1.7401 | 1.827
Market 2 Central/Southern New England | 2.0063 | 2.094 | 2.1818
Market 3 New England City | 2.1166 | 2.2064 | 2.2963
Market 4 NY Metro | 2.3813 | 2.473 | 2.5646
Market 5 NY Upstate | 1.9046 | 1.9922 | 2.0798
Market 6 Mid-Atlantic | 1.8308 | 1.9193 | 2.0079
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.979 | 0.6875
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9886 | 1.1312
New England City | 3 | Boston, Providence | 1.012 | 1.2395
NY Metro | 4 | NYC, Metro, Suburbs, Southwest CT | 1.0328 | 1.552
NY Upstate | 5 | Buffalo, Rochester etc. | 0.98725 | 1.0012
Mid-Atlantic | 6 | MD, DE, DC | 0.998 | 0.8895
R.S. Means Base Cost Factor | - | - | 1 | 1
Summary of cost data analysis for insulation. Regional adjustment factors are applied to geographically normalized average costs. Base Cost Factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category .

## Minisplit - README
Ductless Minisplit HVAC Systems
Return to Measure Index
Measure Characterization:
| Efficient Measure Description | Residential Ductless Minisplit HVAC Systems
| Baseline Description | No A/C or Ductless Minisplit with SEER of 13
| Measure Scenario(s) | RET/NC
| Baseline Efficiency Levels | N/A or 13 SEER
| Measure Level Description | Ductless Minsiplit at 18 SEER or greater
| Measure Efficiency Levels | 18 SEER, 21 SEER, or 26 SEER
| Sizes | 3/4 - 2 tons
| Distinguishing Features | N/A
| Installation Scenarios | Single-zone systems
| Sources | NSTAR
| Incremental Labor Cost | NC: No - Labor cost is the same for efficient and baseline equipment. RET: Yes - Full labor cost
| Cost Basis | Incremental, Full Labor costs are Identical for single head units of any size. Full Costs shown include total materials and labor for Retrofit. Incremental Costs are Materials only
| Fuel Type | Electric
| Data Vintage | 2012
Incremental Cost Study Phase Two
Published: January, 2013
Incremental Cost Methodology
Full Measure Costs are used where the scenario assumes that there is no alternative measure .
Incremental Measure Costs are used when an energy-efficient appliance or measure promoted through a program is installed in lieu of the standard (less efficient) appliance/measure. The incremental cost is the difference between the baseline energy efficiency measure (material and labor) and the standard efficiency model. The equation for calculating incremental measure costs is simply:
Incremental measure cost = energy efficient measure cost (material + labor) - standard efficient baseline cost (material + labor)
In some cases there is no difference in the installation cost between the standard and efficient measure and/or an efficient measure and a more efficient measure. In those cases only materials costs are provided in the incremental cost.
Baseline: The baseline condition is defined as the standard condition or measure that would be installed, without the utility EE activity.
Results Tab
The results tab presents the full cost for the ductless minisplit air conditioners and heat pumps. The analysis is based on contractor interviews and web-based data. Material, labor, and total installed costs are presented by SEER and size for the national average, plus six regionally adjusted markets, allowing NEEP constituents to choose the market that best represents their services territory. The regions represent the results of analyzing RSMeans City Cost Index (CCI).
The analysis represents single-zone ductless minisplit units. While the trend for material costs is not significantly affected by the number of zones, multi-zone units have exponentially increased labor rates that could not be assessed adequately given the limitations of this study (contractor availability).
The analysis of ductless minisplits is based on the full cost, rather than an incremental cost. While several baseline scenarios were identified (as detailed in the Measure Characterization tab) this is based on the assumption that minisplit units are installed most frequently as an add-on where nothing existed before, rather than a substitute or replacement for another type of heating or cooling system.
Finally, this analysis assumes that there is nominal difference in cost between ductless minisplit units that provide air conditioning only, versus air conditioning and heat (i.e., heat pumps). These differences are captured in the increased size however.
Market Characterization
Navigant received program information from two utilities that rebate ductless minisplits: NStar and NYSERDA. The NStar database included approximately 605 ductless minisplit units rebated, and the NYSERDA database included 12.
All 12 NYSERDA contractors were called, however the majority of all ductless minisplit research completed was based on the NStar database. Navigant analyzed the 605 minisplit records to assess prevalence of various manufacturers, unit size, and SEER levels rebated, and contractor market share.
It is important to note that while the rebate data cannot serve as a proxy for the total ductless minisplit market, it can give information about the ‘market’ for rebates. Thus, the rebate market characterization guided the interview process. The characterization helped to ensure that contractors with greater exposure to the ductless minisplit market would be interviewed and to guide the analysis approach.
Measure Characterization
The measure characterization describes several of the assumptions used to drive the ductless minisplit analysis. It is noteworthy that the ductless minisplit is a technology that has several distinguishing factors which lead to significant variation in the baseline and measure level possibilities. Partially due to this variation, the analysis of ductless minisplits is based on the full cost, rather than an incremental cost. While several baseline scenarios were identified, this analysis is based on the assumption that minisplit units are installed most frequently as an add-on where nothing existed before, rather than a substitute or replacement for another type of heating or cooling system.
Regional Adjustments
RSMeans City Cost Index (CCI) raw data and Navigant analysis of the data to create distinct markets for NEEP is presented in this worksheet.
Primary cost data was collected from NStar contractors in Massachusetts, excluding Boston. Due to inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to calculated Base Cost Factor (BCF) data using RSMeans CCI. Table 1 provides a breakdown of the NEEP regions. For example, if the cost provided from a contractor in Massachusetts for a ductless minisplit unit was $2,000, than the BCF cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $2,000 / 0.99
BCF = $2,023
The same method was used to adjust all labor costs as well.
Similarly, once BCF costs were determined for each measure, the costs were then allocated to each market by multiplying the BCF cost by the individual market factor.
The R.S. Means recalculated CCI factors annually. For this study, Navigant used the 2012 CCI factors. Additionally, any older data, collected for the ICS Phase One Report or other sources , was updated with the 2012 factors to maintain comparability with data collected in 2012 for the ICS Phase Two.
Data Analysis for Minisplits
Raw Data
A total of 13 contractor interviews were completed with contractors in Massachusetts, excluding Boston. The contractor information was derived from the NStar program database. Only contractors who had been rebated for a ductless minisplit system were contacted.
Contractor data was supplemented with internet data, also found in the raw data section of this worksheet.
The raw data section of this worksheet represents all of the inputs, after minimal data cleaning prior to analysis.
Formatted Data
The formatted data draws from the raw data and begins the analysis by identifying and removing any potential outlier data points. It then applies regional adjustments to normalize contractor data to to a BCF for both material and labor costs. Internet data is assumed to be a national average (i.e., equivalent to the BCF value).
Material Analysis
The material analysis takes average unit costs of materials by SEER and size. It looks at the averages when considering only one factor (SEER or size) and then considers them together. Final results are based on the latter approach.
Labor Analysis
Contractor interviews solicited a value for total installed cost to customers, as well as hourly labor rates, number of hours to complete installation, and an overall estimate for labor costs for a single zone ductless minisplit unit. The labor analysis compared the values provided between individual contractors for these four values to assess the validity of each. While labor rate multiplied by number of hours needed for installation was expected to equal the total installed cost, less material costs, this did not typically hold true. The labor analysis showed more reliable labor cost data when backing out material costs from total installed costs. This is partially because the estimated “total installed cost” was collected at the beginning of each interview and as a result has more robust data (i.e., contractors that did not have time to complete all of the questions).
In addition, Navigant learned through interviews that pricing of Mini split systems does not generally follow a formula of straight hours multiplied by rate. Contractors indicated that labor for systems is priced based on an estimate of the overall for the size of the job, which varies by the quantity of units and complexity of the installation. Finally, labor costs were then correlated to ductless minisplit unit size and no correlation was found. Therefore, an average of regionally adjusted (BCF) labor costs was used as a single value that can be applied to the material costs to arrive at total installed cost.

## Minisplit - Result
Minisplit HVAC Systems
Data Vintage | 2012 | Tables show full costs (below) and Incremental Materials Costs (Right)
Does this measure have incremental labor cost (Yes/No)? | No | Labor costs are assumed to be identical for all minisplit systems @ $1,763/unit
Return to Measure Index
| Full Labor/Material Cost |  |  |  | Incremental Materials Cost
Base Cost Factor Results:
Size (Tons) | Base Cost Factor Full Cost ($/Unit) |  |  |  | Size (Tons) | Base Cost Factor Incrementla Materials Cost($/Unit)
| 13 SEER | 18 SEER (lowest SEER with strong NSTAR representation) | 21 SEER (Most Represented) | 26 SEER (Best Available) |  | 18 SEER (lowest SEER with strong Nstar representation) | 21 SEER (Most Represented) | 26 SEER (Best Available)
3/4 | 2733.0437 | 3078.0435 | 3236.427 | 3460.0287 | 3/4 | 344.9998 | 503.3832 | 726.985
1 | 2803.4368 | 3138.1384 | 3406.8919 | 3362.9711 | 1 | 334.7017 | 603.4551 | 559.5344
1.5 | 3016.0602 | 3374.3908 | 3639.7713 | * | 1.5 | 358.3306 | 623.711 | *
2 | 3273.2333 | 3874.2208 | * | * | 2 | 600.9875 | * | *
* = Insufficient data available
Results by Market:
Size (Tons) | Market 1 Northern New England Incremental Cost ($/Unit) |  |  |  | Size (Tons) | Market 1 Northern New England Incremental Cost ($/Unit)
| 13 SEER | 18 SEER (lowest SEER with strong NSTAR representation) | 21 SEER (Most Represented) | 26 SEER (Best Available) |  | 18 SEER (lowest SEER with strong Nstar representation) | 21 SEER (Most Represented) | 26 SEER (Best Available)
3/4 | 2161.598 | 2499.3527 | 2654.4102 | 2873.3163 | 3/4 | 337.7548 | 492.8122 | 711.7183
1 | 2230.5127 | 2558.1857 | 2821.2953 | 2778.2969 | 1 | 327.673 | 590.7825 | 547.7842
1.5 | 2438.6711 | 2789.4768 | 3049.2842 | * | 1.5 | 350.8056 | 610.6131 | *
2 | 2690.4435 | 3278.8103 | * | * | 2 | 588.3668 | * | *
* = Insufficient data available
Size (Tons) | Market 2 Central/Southern New England Incremental Cost ($/Unit) |  |  |  | Size (Tons) | Market 2 Central/Southern New England Incremental Cost ($/Unit)
| 13 SEER | 18 SEER (lowest SEER with strong NSTAR representation) | 21 SEER (Most Represented) | 26 SEER (Best Available) |  | 18 SEER (lowest SEER with strong Nstar representation) | 21 SEER (Most Represented) | 26 SEER (Best Available)
3/4 | 2953.358 | 3294.4248 | 3451.0027 | 3672.0554 | 3/4 | 341.0668 | 497.6447 | 718.6973
1 | 3022.9486 | 3353.8346 | 3619.5243 | 3576.1043 | 1 | 330.8861 | 596.5757 | 553.1557
1.5 | 3233.1481 | 3587.3937 | 3849.7489 | * | 1.5 | 354.2456 | 616.6007 | *
2 | 3487.3894 | 4081.5256 | * | * | 2 | 594.1362 | * | *
* = Insufficient data available
Size (Tons) | Market 3 New England City Incremental Cost ($/Unit) |  |  |  | Size (Tons) | Market 3 New England City Incremental Cost ($/Unit)
| 13 SEER | 18 SEER (lowest SEER with strong NSTAR representation) | 21 SEER (Most Represented) | 26 SEER (Best Available) |  | 18 SEER (lowest SEER with strong Nstar representation) | 21 SEER (Most Represented) | 26 SEER (Best Available)
3/4 | 3167.0299 | 3516.1697 | 3676.4538 | 3902.7387 | 3/4 | 349.1398 | 509.4238 | 735.7088
1 | 3238.2677 | 3576.9858 | 3848.9642 | 3804.5165 | 1 | 338.7181 | 610.6966 | 566.2488
1.5 | 3453.4426 | 3816.0732 | 4084.6382 | * | 1.5 | 362.6305 | 631.1956 | *
2 | 3713.7017 | 4321.9011 | * | * | 2 | 608.1993 | * | *
* = Insufficient data available
Size (Tons) | Market 4 NY Metro Incremental Cost ($/Unit) |  |  |  | Size (Tons) | Market 4 NY Metro Incremental Cost ($/Unit)
| 13 SEER | 18 SEER (lowest SEER with strong NSTAR representation) | 21 SEER (Most Represented) | 26 SEER (Best Available) |  | 18 SEER (lowest SEER with strong Nstar representation) | 21 SEER (Most Represented) | 26 SEER (Best Available)
3/4 | 3738.2333 | 4094.5318 | 4258.1023 | 4489.027 | 3/4 | 356.2985 | 519.869 | 750.7937
1 | 3810.9317 | 4156.5949 | 4434.1499 | 4388.7908 | 1 | 345.6632 | 623.2183 | 577.8591
1.5 | 4030.5186 | 4400.5845 | 4674.6562 | * | 1.5 | 370.0659 | 644.1376 | *
2 | 4296.114 | 4916.7839 | * | * | 2 | 620.6698 | * | *
* = Insufficient data available
Incremental Material Cost
Size (Tons) | Market 5 NY Upstate Incremental Cost ($/Unit) |  |  |  | Size (Tons) | Market 5 NY Upstate Incremental Cost ($/Unit)
| 13 SEER | 18 SEER (lowest SEER with strong NSTAR representation) | 21 SEER (Most Represented) | 26 SEER (Best Available) |  | 18 SEER (lowest SEER with strong Nstar representation) | 21 SEER (Most Represented) | 26 SEER (Best Available)
3/4 | 2722.886 | 3063.487 | 3219.8511 | 3440.6019 | 3/4 | 340.601 | 496.9651 | 717.7159
1 | 2792.3815 | 3122.8158 | 3388.1426 | 3344.7819 | 1 | 330.4342 | 595.761 | 552.4003
1.5 | 3002.2941 | 3356.0559 | 3618.0528 | * | 1.5 | 353.7619 | 615.7587 | *
2 | 3256.1881 | 3849.513 | * | * | 2 | 593.3249 | * | *
* = Insufficient data available
Size (Tons) | Market 6 Mid-Atlantic Incremental Cost ($/Unit) |  |  |  | Size (Tons) | Market 6 Mid-Atlantic Incremental Cost ($/Unit)
| 13 SEER | 18 SEER (lowest SEER with strong NSTAR representation) | 21 SEER (Most Represented) | 26 SEER (Best Available) |  | 18 SEER (lowest SEER with strong Nstar representation) | 21 SEER (Most Represented) | 26 SEER (Best Available)
3/4 | 2536.241 | 2880.5508 | 3038.6175 | 3261.772 | 3/4 | 344.3098 | 502.3765 | 725.531
1 | 2606.4933 | 2940.5255 | 3208.7415 | 3164.9086 | 1 | 334.0323 | 602.2482 | 558.4153
1.5 | 2818.6915 | 3176.3054 | 3441.1551 | * | 1.5 | 357.6139 | 622.4636 | *
2 | 3075.3502 | 3675.1357 | * | * | 2 | 599.7855 | * | *
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.979 | 0.6875
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9886 | 1.1312
New England City | 3 | Boston, Providence | 1.012 | 1.2395
NY Metro | 4 | NYC, Metro, Suburbs, Southwest CT | 1.0328 | 1.552
NY Upstate | 5 | Buffalo, Rochester etc. | 0.98725 | 1.0012
Mid-Atlantic | 6 | MD, DE, DC | 0.998 | 0.8895
R.S. Means Base Cost Factor | - | - | 1 | 1
Summary of cost data analysis for insulation. Regional adjustment factors are applied to geographically normalized average costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category .

## On Demand WH - README
On Demand Water Heater Standard & Condensing
Return to Measure Index
Measure Characterization:
| Efficient Measure Description | Residential Natural Gas On Demand Water Heaters
| Baseline Description | Standard storage-type gas-fired water heater
| Measure Scenario(s) | ROB
| Baseline Efficiency Levels | 59 Energy Factor (EF) for 40 gallon tank
| Efficient Measure Description & Specifications | Tankless gas-fired water heater with EF of 82 or above
| Sizes | 180 - 199 MBH
| Distinguishing Features | N/A
| Installation Scenarios | 1) a standard installation where the on-demand unit replaces storage hot water heater in-kind with minimal reworking of gas and venting lines 2) a relocation installation where an on-demand water heater is mounted to a wall away from the original water heater location. This requires significant reworking of gas lines and venting through an exterior wall.
| Sources | BG&E, Yankee Gas, NSTAR, Gas Networks, National Grid, and Northeast Utilities
| Incremental Labor Cost | Yes
| Cost Basis | Incremental
| Fuel Type | Gas
| Data Vintage | 2012
Incremental Cost Study Phase Two
Published: January, 2013
Incremental Cost Methodology
Full Measure Costs are used where the scenario assumes that there is no alternative measure .
Incremental Measure Costs are used when an energy-efficient appliance or measure promoted through a program is installed in lieu of the standard (less efficient) appliance/measure. The incremental cost is the difference between the baseline energy efficiency measure (material and labor) and the standard efficiency model. The equation for calculating incremental measure costs is simply:
Incremental measure cost = energy efficient measure cost (material + labor) - standard efficient baseline cost (material + labor)
In some cases there is no difference in the installation cost between the standard and efficient measure and/or an efficient measure and a more efficient measure. In those cases only materials costs are provided in the incremental cost.
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as a tankless gas-fired water heater with an energy factor (EF) of 82 or above.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity . The baseline equipment in this instance is a standard storage-type gas-fired water heater. Energy factor varies with storage volume, therefore the baseline is a 40 gallon tank with a 59 EF which corresponds to the current minimum Federal standard.
Workbook Elements
Results Tab
The tab presents the incremental cost for the tankless water heaters. Material, labor, and installed incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Base Cost Factor category).
Data Analysis
Raw Data
A total of 30 contractor interviews were completed for the analysis of the measure. A total of 46 contractor cost points were collected for tankless water heaters and 15 contractor cost points (61 data points in total) for standard storage water heaters were collected.
Formatted Data
Primary cost data was collected from contractors across five states (CT, MA, NH, NY, and VT). Due to the inherent differences in cost from one region to another (i.e. the cost of labor and materials is greater in NY than in VT), Navigant adjusted all material and labor cost points to represent base cost factor (BCF) data using RSMeans CCI. Table 1 provides a regional break down of NEEP. For example, if the material cost provided from a contractor in New York Metro for a tankless water heater was $2,000, than the NRS cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $2,000 / 1.03
BCF = $1,936.58
The same method was used to adjust all labor costs.
Similarly, once BCF costs were determined for each measure, the costs were then allocated to each market by multiplying the BCF cost by the individual market factor.
The R.S. Means recalculated CCI factors annually. For this study, Navigant used the 2012 CCI factors. Additionally, any older data, collected for the ICS Phase One Report or other sources , was updated with the 2012 factors to maintain comparability with data collected in 2012 for the ICS Phase Two.
Some internet costs were included in the analysis to augment and QC the contractor data. Internet costs do not include a contractor markup, therefore, a match-pairs analysis determined the percent cost difference between similar equipment sold by contractors and internet retailers. This difference was applied to the internet cost as a contractor markup.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data.
A linear regression was used to develop the material cost for the measure. A regression was done for the entire range of tankless efficiencies and burner inputs. For the baseline material, a simple average was conducted to determine the average price for 40 gallon units at 59 EF.
Labor Analysis
Contractor interviews identified an incremental difference in the time to install efficient versus base scenario equipment. This analysis also identified an incremental difference in the time to install standard tankless units (82 EF) and condensing tankless units (approx. 94 EF and above). In general, efficient equipment took approximately 4 additional hours to install when compared with base equipment (while condensing equipment took 6 additional hours). The analysis also identified the labor difference between standard or simple installations and installations that require significant reworking of gas lines, venting lines, and venting through exterior walls because tankless water heaters are sometimes installed in locations different from the original storage water. Installation times were calculated by taking the average of the applicable times quoted by contractors. Finally, the labor rate was calculated with a weighted average of all contractor labor rates ($/HR) collected for residential gas measures.
Results
Through contractor interviews, Navigant defined the most common unit sizes that can serve entire households (note: this analysis does not include point-of-use tankless water heaters). As such, results are presented for each of those size categories at a non-regional specific level. Note, that the user of this spreadsheet should select the type of installation in cell BH7.

## On Demand WH - Results
On Demand Water Heater Standard & Condensing
Data Vintage | 2012
Does this measure have incremental labor cost (Yes/No)? | Yes
Select analysis scenario:
Installation type (DROP DOWN MENU) | Additional labor to relocate measure
Return to Measure Index
Base Cost Factor Results:
Size (MBH) | Baseline Storage Water Heater |  | Base Cost Factor Incremental Cost ($/Unit)
| Gallon Size | Efficiency (EF) | Standard Tankless Water Heater (82 EF) | Condensing Tankless Water Heater (94 EF) | Condensing Tankless Water Heater (95 EF) | Condensing Tankless Water Heater (96 EF)
180 | 30 | 61.3 | 2115.7173 | 2893.599 | 2944.226 | 2994.853
180 | 40 | 59.4 | 2024.1786 | 2802.0603 | 2852.6873 | 2903.3143
180 | 48 | 57.88 | 1950.9477 | 2728.8294 | 2779.4564 | 2830.0834
199 | 50 | 57.5 | 2052.0251 | 2829.9068 | 2880.5338 | 2931.1608
199 | 65 | 54.65 | 1914.7171 | 2692.5988 | 2743.2258 | 2793.8528
Results by Market:
Size (MBH) | Baseline Storage Water Heater |  | Market 1 Northern New England Incremental Cost ($/Unit)
| Gallon Size | Efficiency (EF) | Standard Tankless Water Heater (82 EF) | Condensing Tankless Water Heater (94 EF) | Condensing Tankless Water Heater (95 EF) | Condensing Tankless Water Heater (96 EF)
180 | 30 | 61.3 | 1858.2695 | 2453.0355 | 2502.5993 | 2552.1631
180 | 40 | 59.4 | 1768.6531 | 2363.4191 | 2412.9829 | 2462.5468
180 | 48 | 57.88 | 1696.96 | 2291.726 | 2341.2898 | 2390.8537
199 | 50 | 57.5 | 1795.9148 | 2390.6808 | 2440.2447 | 2489.8085
199 | 65 | 54.65 | 1661.4903 | 2256.2563 | 2305.8201 | 2355.3839
Size (MBH) | Baseline Storage Water Heater |  | Market 2 Central/Southern New England Incremental Cost ($/Unit)
| Gallon Size | Efficiency (EF) | Standard Tankless Water Heater (82 EF) | Condensing Tankless Water Heater (94 EF) | Condensing Tankless Water Heater (95 EF) | Condensing Tankless Water Heater (96 EF)
180 | 30 | 61.3 | 2195.8051 | 2796.4034 | 2846.4532 | 2896.5031
180 | 40 | 59.4 | 2105.31 | 2705.9082 | 2755.9581 | 2806.008
180 | 48 | 57.88 | 2032.9139 | 2633.5121 | 2683.562 | 2733.6118
199 | 50 | 57.5 | 2132.839 | 2733.4373 | 2783.4871 | 2833.537
199 | 65 | 54.65 | 1997.0963 | 2597.6946 | 2647.7444 | 2697.7943
Size (MBH) | Baseline Storage Water Heater |  | Market 3 New England City Incremental Cost ($/Unit)
| Gallon Size | Efficiency (EF) | Standard Tankless Water Heater (82 EF) | Condensing Tankless Water Heater (94 EF) | Condensing Tankless Water Heater (95 EF) | Condensing Tankless Water Heater (96 EF)
180 | 30 | 61.3 | 2307.3548 | 2922.1691 | 2973.4036 | 3024.6382
180 | 40 | 59.4 | 2214.7177 | 2829.532 | 2880.7665 | 2932.001
180 | 48 | 57.88 | 2140.608 | 2755.4223 | 2806.6568 | 2857.8913
199 | 50 | 57.5 | 2242.8983 | 2857.7126 | 2908.9472 | 2960.1817
199 | 65 | 54.65 | 2103.9426 | 2718.7569 | 2769.9915 | 2821.226
Size (MBH) | Baseline Storage Water Heater |  | Market 4 NY Metro Incremental Cost ($/Unit)
| Gallon Size | Efficiency (EF) | Standard Tankless Water Heater (82 EF) | Condensing Tankless Water Heater (94 EF) | Condensing Tankless Water Heater (95 EF) | Condensing Tankless Water Heater (96 EF)
180 | 30 | 61.3 | 2564.4564 | 3191.8769 | 3244.1619 | 3296.4469
180 | 40 | 59.4 | 2469.9199 | 3097.3403 | 3149.6253 | 3201.9104
180 | 48 | 57.88 | 2394.2906 | 3021.7111 | 3073.9961 | 3126.2811
199 | 50 | 57.5 | 2498.6783 | 3126.0988 | 3178.3838 | 3230.6688
199 | 65 | 54.65 | 2356.8735 | 2984.2939 | 3036.579 | 3088.864
Size (MBH) | Baseline Storage Water Heater |  | Market 5 NY Upstate Incremental Cost ($/Unit)
| Gallon Size | Efficiency (EF) | Standard Tankless Water Heater (82 EF) | Condensing Tankless Water Heater (94 EF) | Condensing Tankless Water Heater (95 EF) | Condensing Tankless Water Heater (96 EF)
180 | 30 | 61.3 | 2098.9726 | 2698.7507 | 2748.7322 | 2798.7137
180 | 40 | 59.4 | 2008.6011 | 2608.3792 | 2658.3607 | 2708.3422
180 | 48 | 57.88 | 1936.3038 | 2536.0819 | 2586.0634 | 2636.0449
199 | 50 | 57.5 | 2036.0925 | 2635.8706 | 2685.8521 | 2735.8336
199 | 65 | 54.65 | 1900.5352 | 2500.3133 | 2550.2948 | 2600.2763
Size (MBH) | Baseline Storage Water Heater |  | Market 6 Mid-Atlantic Incremental Cost ($/Unit)
| Gallon Size | Efficiency (EF) | Standard Tankless Water Heater (82 EF) | Condensing Tankless Water Heater (94 EF) | Condensing Tankless Water Heater (95 EF) | Condensing Tankless Water Heater (96 EF)
180 | 30 | 61.3 | 2032.198 | 2638.5069 | 2689.0327 | 2739.5584
180 | 40 | 59.4 | 1940.8424 | 2547.1513 | 2597.6771 | 2648.2028
180 | 48 | 57.88 | 1867.7579 | 2474.0668 | 2524.5926 | 2575.1183
199 | 50 | 57.5 | 1968.6332 | 2574.9421 | 2625.4679 | 2675.9936
199 | 65 | 54.65 | 1831.5998 | 2437.9087 | 2488.4345 | 2538.9602
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor
Northern New England | 1 | ME, VT, NH | 0.979 | 0.6875
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9886 | 1.1312
New England City | 3 | Boston, Providence | 1.012 | 1.2395
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT | 1.0328 | 1.552
NY Upstate | 5 | Buffalo, Rochester etc. | 0.98725 | 1.0012
Mid-Atlantic | 6 | MD, DE, DC | 0.998 | 0.8895
Base Cost Factor Average | - | - | 1 | 1
Summary of incremental cost data analysis for tankless water heaters. Regional adjustment factors are applied to Base Cost Factor incremental costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category.
Two installation scenarios are analyzed.
Standard installation: Replacement of existing water heater with minimal changes to piping and venting.
Relocated installation: Installation in area away from existing water heater location that requires significant changes to venting and gas lines and venting through exterior walls.
Note: Baseline assumptions correspond to a standard gas-fired tank water heater at the Federal Minimum Energy Factor.

## Ventilation Fans - README
Ventilation Fans
Return to Measure Index
Measure Characterization:
| Efficient Measure Description | Ventilation Fans
| Baseline Description | Standard non-Energy Star bathroom or utility ventilation fan
| Measure Scenario(s) | ROB, NC, RET
| Baseline Efficiency Levels | Non-Energy Star rated ventilation fan. Varies by size.
| Efficient Measure Description | Energy Star Rated Bathroom/Utility Room Ventilation Fan (Residential ventilating fans with heat lamps are excluded.)
| Measure Efficiency Levels | Minimum Efficacy Level (CFM/W) Airflow 10 to 89 CFM: 1.4 Airflow 90 to 500 CFM: 2.8 Maximum Allowable Sound Level (Sones) Airflow 10 to 139 CFM: 2 Airflow 140 to 500 CFM: 3 Rated Airflow (0.25 in. w.g.) Airflow 10 to 89 CFM: 60% Airflow 90 to 500 CFM: 70%
| Sizes | 50 - 89 CFM, 90 - 149CFM, and 150 - 310 CFM
| Distinguishing Features | 1) With or without fluorescent/LED lighting 2) Single/multiple speeds 3) Ultra quiet 4) Humidity and/or motion sensing, timer control 5) Continuous/intermittent
| Installation Scenarios | Ceiling or wall-mounted
| Sources | Internet
| Incremental Labor Cost | NC and ROB: No - Labor cost is the same for efficient and baseline equipment. RET: Yes - Full labor cost
| Cost Basis | Incremental, Full NC for base or efficient units requires ducting so there is no incremental labor cost Replacement without adding ducting has no incremental labor cost Retrofit: Full costs include materials and labor.
| Fuel Type | Electric
| Data Vintage | 2012
Incremental Cost Study Phase Two
Published: January, 2013
Incremental Cost Methodology
Full Measure Costs are used where the scenario assumes that there is no alternative measure.
Incremental Measure Costs are used when an energy-efficient appliance or measure promoted through a program is installed in lieu of the standard (less efficient) appliance/measure. The incremental cost is the difference between the baseline energy efficiency measure (material and labor) and the standard efficiency model. The equation for calculating incremental measure costs is simply:
Incremental measure cost = energy efficient measure cost (material + labor) - standard efficient baseline cost (material + labor)
In some cases there is no difference in the installation cost between the standard and efficient measure and/or an efficient measure and a more efficient measure. In those cases only materials costs are provided in the incremental cost.
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, a measure is defined as an Energy Star rated bathroom or utility room ventilation fan, either with or without an integrated light. Ventilation fans with integrated heat lamps are excluded from this study.
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity. The baseline equipment in this instance is a standard bathroom or utility ventilation fan that is not Energy Star qualified in the NEEP market. The assumption is that the non Energy Star units will be the most economical to purchase.
Results Tab
The results tab presents the incremental cost for ventilation fans without an integrated light and ventilation fans with an integrated light. The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Material incremental costs, full installation costs (material and labor) for replacement ventilation fan, and full installation costs for a new ventilation fan are provided for each NEEP region.
Data Analysis
Raw Data
A total of 229 ventilation fan cost points across 7 web retailers. Navigant attempted to contact local contractors in the NEEP market for material cost information, but contractor participation was lacking. While online data only provides material cost at the national level, contractors installing ventilation fans include both material and labor costs. However, for ventilation fans, there is no incremental labor costs.
When appropriate, Navigant adjusted all material and labor cost points to represent base cost factor (BCF) data using RSMeans CCI. Table 1 provides a regional break down of the NEEP. For example, if a material cost provided from a contractor in New York Metro was $1000, than the BCF cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State, or
BCF = $1000 / 1.01, or
BCF = $990.10
The same method was used to adjust all labor cost when appropriate.
Similarly, once BCF costs were determined for each measure, the costs were then allocated to each market by multiplying the BCF cost by the individual market factor.
The R.S. Means recalculated CCI factors annually. For this study, Navigant used the 2012 CCI factors. Additionally, any older data, collected for the ICS Phase One Report or other sources , was updated with the 2012 factors to maintain comparability with data collected in 2012 for the ICS Phase Two.
Formatted Data
Online data is presented as national data and all materials are adjusted for each market using the material adjustment factor after the analysis of all material costs. Based on the collected data, the following max CFM size ranges were used in the analysis of ventilation fan costs: 50 - 89 CFM, 90 - 149CFM, and 150 - 310 CFM. Units outside these ranges were removed from the formatted data and were not used in the analysis due to insufficient data.
Material Analysis
A simple average was used to develop the material cost for the collected data across four identified size ranges for Energy Star and non Energy Star units. The added cost to add an integrated light to the ventilation fan unit was developed by averaging all vent fans without light versus all those with an integrated light.
Labor Analysis
Navigant confirmed, with four contractors, there is no incremental labor costs associated with the installation of a ventilation fan. Labor hours would be the same regardless of the unit's efficiency. Discussion with the interviewed contractors in the NEEP region provides rough estimates of labor hours required for the installation of ventilation fans in an average bathroom at 2.3 hours for replacement and 5.5 hours for a new installation.

## Ventilation Fans - Results
Ventilation Fans
Data Vintage | 2012
Does this measure have incremental labor cost (Yes/No)? | No. See | NC for base or efficient units requires ducting so there is no incremental labor cost
Return to Measure Index |  | Replacement without adding ducting has no incremental labor cost
Retrofit: Full costs include materials and labor.
Base Cost Factor Results:
Material Incremental Cost |  |  |  |  | Full Installation Cost for Replacement Vent Fan |  |  |  | Full Installation Cost for New Vent Fan
Feature | Base Cost Factor ($/Unit) - CFM Range |  |  |  | Feature | Base Cost Factor ($/Unit) - CFM Range |  |  | Feature | Base Cost Factor ($/Unit) - CFM Range
| 50 - 89 | 90 - 149 | 150 - 310 |  |  | 50 - 89 | 90 - 149 | 150 - 310 |  | 50 - 89 | 90 - 149 | 150 - 310
Exhaust only | 80.6402 | 68.6561 | 56.1892 |  | Exhaust only | 324.748 | 357.3928 | 386.8018 | Exhaust only | 584.237 | 616.8817 | 646.2907
Fan with Light | 123.3375 | 111.3534 | 98.8865 |  | Fan with Light | 367.4454 | 400.0901 | 429.4991 | Fan with Light | 626.9343 | 659.5791 | 688.9881
Results by Market:
Material Incremental Cost |  |  |  |  | Full Installation Cost for Replacement Vent Fan |  |  |  | Full Installation Cost for New Vent Fan
Feature | Market 1 Northern New England Incremental Cost ($/Unit) - CFM Range |  |  |  | Feature | Market 1 Northern New England Incremental Cost ($/Unit) - CFM Range |  |  | Feature | Market 1 Northern New England Incremental Cost ($/Unit) - CFM Range
| 50 - 89 | 90 - 149 | 150 - 310 |  |  | 50 - 89 | 90 - 149 | 150 - 310 |  | 50 - 89 | 90 - 149 | 150 - 310
Exhaust only | 79.0274 | 67.283 | 55.0654 |  | Exhaust only | 266.7499 | 298.7418 | 327.5626 | Exhaust only | 445.7973 | 477.7892 | 506.61
Fan with Light | 120.8708 | 109.1263 | 96.9088 |  | Fan with Light | 309.4473 | 341.4391 | 370.2599 | Fan with Light | 488.4947 | 520.4865 | 549.3073
Feature | Market 2 Central/Southern New England Incremental Cost ($/Unit) - CFM Range |  |  |  | Feature | Market 2 Central/Southern New England Incremental Cost ($/Unit) - CFM Range |  |  | Feature | Market 2 Central/Southern New England Incremental Cost ($/Unit) - CFM Range
| 50 - 89 | 90 - 149 | 150 - 310 |  |  | 50 - 89 | 90 - 149 | 150 - 310 |  | 50 - 89 | 90 - 149 | 150 - 310
Exhaust only | 79.8338 | 67.9695 | 55.6273 |  | Exhaust only | 346.3641 | 378.6824 | 407.7973 | Exhaust only | 639.5867 | 671.9049 | 701.0199
Fan with Light | 122.1042 | 110.2399 | 97.8977 |  | Fan with Light | 389.0615 | 421.3798 | 450.4947 | Fan with Light | 682.284 | 714.6023 | 743.7172
Feature | Market 3 New England City Incremental Cost ($/Unit) - CFM Range |  |  |  | Feature | Market 3 New England City Incremental Cost ($/Unit) - CFM Range |  |  | Feature | Market 3 New England City Incremental Cost ($/Unit) - CFM Range
| 50 - 89 | 90 - 149 | 150 - 310 |  |  | 50 - 89 | 90 - 149 | 150 - 310 |  | 50 - 89 | 90 - 149 | 150 - 310
Exhaust only | 81.4466 | 69.3426 | 56.7511 |  | Exhaust only | 368.8428 | 401.814 | 431.5171 | Exhaust only | 690.6091 | 723.5803 | 753.2834
Fan with Light | 124.5709 | 112.4669 | 99.8754 |  | Fan with Light | 411.5402 | 444.5113 | 474.2144 | Fan with Light | 733.3065 | 766.2776 | 795.9807
Feature | Market 4 NY Metro Incremental Cost ($/Unit) - CFM Range |  |  |  | Feature | Market 4 NY Metro Incremental Cost ($/Unit) - CFM Range |  |  | Feature | Market 4 NY Metro Incremental Cost ($/Unit) - CFM Range
| 50 - 89 | 90 - 149 | 150 - 310 |  |  | 50 - 89 | 90 - 149 | 150 - 310 |  | 50 - 89 | 90 - 149 | 150 - 310
Exhaust only | 83.0594 | 70.7158 | 57.8749 |  | Exhaust only | 426.8409 | 460.465 | 490.7563 | Exhaust only | 829.0488 | 862.6729 | 892.9642
Fan with Light | 127.0377 | 114.694 | 101.8531 |  | Fan with Light | 469.5383 | 503.1623 | 533.4536 | Fan with Light | 871.7461 | 905.3702 | 935.6615
Feature | Market 5 NY Upstate Incremental Cost ($/Unit) - CFM Range |  |  |  | Feature | Market 5 NY Upstate Incremental Cost ($/Unit) - CFM Range |  |  | Feature | Market 5 NY Upstate Incremental Cost ($/Unit) - CFM Range
| 50 - 89 | 90 - 149 | 150 - 310 |  |  | 50 - 89 | 90 - 149 | 150 - 310 |  | 50 - 89 | 90 - 149 | 150 - 310
Exhaust only | 79.8338 | 67.9695 | 55.6273 |  | Exhaust only | 323.2765 | 355.5948 | 384.7097 | Exhaust only | 582.7655 | 615.0838 | 644.1987
Fan with Light | 122.1042 | 110.2399 | 97.8977 |  | Fan with Light | 365.9739 | 398.2921 | 427.4071 | Fan with Light | 625.4628 | 657.7811 | 686.896
Feature | Market 6 Mid-Atlantic Incremental Cost ($/Unit) - CFM Range |  |  |  | Feature | Market 6 Mid-Atlantic Incremental Cost ($/Unit) - CFM Range |  |  | Feature | Market 6 Mid-Atlantic Incremental Cost ($/Unit) - CFM Range
| 50 - 89 | 90 - 149 | 150 - 310 |  |  | 50 - 89 | 90 - 149 | 150 - 310 |  | 50 - 89 | 90 - 149 | 150 - 310
Exhaust only | 80.6402 | 68.6561 | 56.1892 |  | Exhaust only | 305.2124 | 337.8571 | 367.2661 | Exhaust only | 536.1575 | 568.8023 | 598.2113
Fan with Light | 123.3375 | 111.3534 | 98.8865 |  | Fan with Light | 347.9097 | 380.5544 | 409.9634 | Fan with Light | 578.8549 | 611.4996 | 640.9086
Market | Market Code | Regions |  | Material Adjustment Factor | Labor Adjustment Factor
Northern New England | 1 | ME, VT, NH |  | 0.98 | 0.69
Central/Southern New England | 2 | MA (exc Boston), RI, most CT |  | 0.99 | 1.13
New England City | 3 | Boston, Providence |  | 1.01 | 1.24
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT |  | 1.03 | 1.55
NY Upstate | 5 | Buffalo, Rochester etc. |  | 0.99 | 1
Mid-Atlantic | 6 | MD, DE, DC |  | 1 | 0.89
Base Cost Factor | - | - |  | 1 | 1
Summary of cost data analysis for variable frequency drives. Regional adjustment factors are applied to base cost factor costs.
Regional adjustment factors were developed using RSMeans City Cost Indexes based on weighted average of division category.
"Exhaust only" feature type is a bath/utility ventilation fan without an integrated light. "Fan/Light" is a bath/utility ventilation fan that includes an integrated light.