## Incremental Cost Summary
Residential and Commercial Variable Capacity and Variable Refrigerant Flow (VRF) Air Source Heat Pumps and A/C
Definition of Variable Capacity Air Source Heat Pumps and VRF
Inverter-driven air source heat pumps and air conditioning (A/C) systems utilize a variable frequency drive (VFD) to modulate the compressor output to match changing demand. Variable refrigerant flow (VRF) systems also utilize an inverter-driven compressor, but additionally have the capability to modulate the flow of refrigerant to each individual fan coil within the building. Some VRF systems also have the ability to provide simultaneous heating and cooling across zones through heat recovery at a central distribution point. This study covers inverter-driven multiple-zone systems for residential and small commercial applications, as well as VRF systems that have the capability of simultaneous heating and cooling.
Technology | Definition
Baseline | Non-modulating air source heat pump (ASHP) systems
Multi-split heat pump systems | Multiple zone mini-split or multi-head heat pump (HP) systems
Variable refrigerant flow heat pump systems | Multiple zone variable refrigerant flow (VRF) HP systems
VRF HP with HR | Multiple zone VRF HP systems with heat recovery HR capabilities
Table 3-6
Summary of Incremental Equipment and Labor Costs by Technology
System Type | Incremental Costs per Ton | Cold Weather Performance |  | Cost Adders
Multi-split | 2360 | 2990 |  | Cold Weather Adder |  | 17%
VRF | 2860 | 3580 |  | Heat Recovery (HR) Adder on Full Cost |  | 203.3%
VRF with heat recovery (HR) | 7230 | 8690 |  | HR Adder on Incremental Cost |  | 252.8%
Table 3-5
Summary of Installed Costs by Technology
System Type | Average Costs per Ton | Notes |  | VRF Labor costs | $/Ton
Baseline | 1370 | Average from case study and published data |  | Efficiency Maine | 1794.5055
Multi-split | 3730 | Average from manufacturer data |  | Daikin | 2518.5222
VRF | 4230 | Average from manufacturer, and secondary data |  | Average | 2160
VRF with heat recovery | 8600 | Average from manufacturer data, and case studies
Table 3-2
Summary of Installed Costs Provided by Manufacturers
Manufacturer | Multi-Split ($/ton) | VRF ($/ton) | VRF w/HR ($/ton)
1 | 3330 | 8800 | 10600
2 | 4000 | 5000 | 7000
3 | 3780 | 5480 | 10330
4 | 3800 | 6120 | 8860
Data Summary and Calculation of Results
Data Sources |  |  | Installed Costs
Year of Data | Study | Location | Baseline ($/Ton) | Multi-split ($/Ton) | VRF ($/Ton) | VRF W/ HR ($/Ton)
< 2011 | EES study for BPA | http://rtf.nwcouncil.org/subcommittees/vchp/BPA_VRF_Measure_Report_Final_R1.pdf | 950 |  | 1548.1
< 2011 | PNNL study for GSA | http://www.gsa.gov/portal/mediaId/197399/fileName/GPG_Variable_Refrigerant_Flow_12-2012.action | 0 |  | 0
< 2011 | EMS Case Studies | http://www.emsenergy.com/uploads/pdfs/West-Energy-Management-Congress-VFD-Can-Save-30-of-Your-HVAC-Cost-June-2013.pdf | 950
2011 | Efficiency Maine Case Studies | Direct program data | 3664.9865 |  | 4185.6081 | 6195.3151
2011 | Energy Efficiency Emerging Technologies (E3T) | http://e3tnw.org/ItemDetail.aspx?id=200 | 0 |  | 0
2012 | SCE13HC036 | Could not find online but have document | 1355 |  | 2100 | 2700
2014 | NEEP Incremental Cost Study | http://www.neep.org/incremental-cost-study-phase-3-report | 1285.2868
2016-02-01 | Manufacturer 1 |  |  | 3330 | 8800 | 10600
2016-02-01 | Manufacturer 2 |  |  | 4000 | 5000 | 7000
2016-02-01 | Manufacturer 3 |  |  | 3780 | 5480 | 10330
2016-02-01 | Manufacturer 4 |  |  | 3800 | 6120 | 8860
Average Installed System Full Cost |  |  | 1370 | 3730 | 4230 | 8600
Average Installed System Full Cost With Cold Weather Adder |  |  |  | 4360 | 4950 | 10060
Incremental Cost Results |  |  |  | 2360 | 2860 | 7230
Cold Weather Incremental Cost Results |  |  |  | 2990 | 3580 | 8690
Cost Trends
It's expected that costs will reduced another 5% to 15% over the next 1 to 2 years
Competition between the major manufacturers in recent history has been the biggest driver of cost reductions
Moving forward it is expected that cost reductions will be driven by the move to manufacturer equipment domestically compared to that shipped from overseas.
All manufacturers agree that costs have nearly plateaued in recent months
Additional cost reductions will come from familiarity of the installing contractor
Cost Factors
A wall unit is less expensive than a cassette by about 20%. Couple of different reasons, one being that these are the most common type of unit. In part likely because of recognition they bring. A lot of flexibility being brought to the market in the type of indoor units available
Approximately 30% adder for the heat recovery option
Indoor units usually account for approximately 40% of the total cost
The number of zones per ton is the biggest driver of cost per ton
One of the incremental cost drivers is that mini-splits are usally flared while VRF are usually torched which last a lot longer
The accessibility of the refrigerent line paths and how the outdoor air is delt with are the biggest drivers of cost
Table 3-3. Manufacturer 1 Installed Costs
System Type | Tonnage | Zones | Installed Cost ($/ton)
Multi-split | 1.7 | 2 | 3750
Multi-split | 4 | 3 | 2900
Multi-split w/ cold weather capability | 1.7 | 2 | 4560
Multi-split w/ cold weather capability | 4 | 3 | 3290
VRF | N.D. | N.D. | 8800
VRF with HR | N.D. | N.D. | 10600
Table 3-4 Manufacturer 3 Installed Costs
System Type | Tonnage | Zones | Equipment Cost ($/ton) | Labor cost ($/ton) | Installed Cost ($/ton)
Multi-split | 3 | 3 | 1751 | 2028 | 3780
VRF | 4 | 4 | 2811 | 2064 | 4875
VRF | 10 | 6 | 2612 | 3462 | 6075
VRF with HR | 16 | 14 | 3717 | 6612 | 10330
Note on H28: Jesse Remillard: With unrounded manufaucturer cost values, percent adder was less than 17.5%
Note on G51: Jesse Remillard: Not included in analysis because not consistent with majority of verifiable data.
Note on E52: Jesse Remillard: Not included in analysis because not consistent with majority of verifiable data.
Note on G56: Jesse Remillard: Not included in analysis because not consistent with majority of verifiable data.
Note on H56: Jesse Remillard: Not included in analysis because not consistent with majority of verifiable data.

## VRF W HR
VRF with Heat Recovery Data Collection
Unit Type | Type | Source | Date | Region | Manufacturer | Model Number | Tons | Size kBTU/hr | Zones | EER | SEER | HSPF | COP | Total Equip Cost | Labor hours | Labor Rate | Equipment cost per ton | Labor per ton | Total installed cost | Total Installed Cost per ton
VRF W/H Rec | Report | SCE13HC036 CA working paper | 2012-05-01 | CA | ND | ND | [13 empty] | 2700
VRF W/H Rec | Case study | EMaine project |  |  |  |  | 74 | [11 empty] | 339544 | 4588.4324
VRF W/H Rec | Case study | EMaine project |  |  |  |  | 91 | [9 empty] | 6007.6923 | 1794.5055 | 710000 | 7802.1978

## VRF
Primary Data
VRF Data Collection
Yellow cells are averaged data
Unit Type | Type | Source | Date | Region | Manufacturer | Model Number | Tons | Size kBTU/hr | Zones | EER | SEER | HSPF | COP | Total Equip Cost | Labor hours | Labor Rate | Total installed cost | Installed Cost per ft^2 | Incremental cost per sq ft | Total Incremental Cost | Equipment cost per ton | Labor per ton | Total Installed Cost per ton | Incremental Cost Per Ton | Incremental Cost Baseline | Notes | Data source
VRF | Case Study | Energy Management Solutions | 2008 | MN |  |  | 50 |  | 28 | [10 empty] | 138000 |  |  |  | 2760 | boilers and window ac
VRf | Case Study | Energy Management Solutions | 2009 | MN |  |  | 15 |  | 12 | [10 empty] | 22500 |  |  |  | 1500 | window ac, no heat
VRF | Case Study | Energy Management Solutions | 2010 | MN |  |  | 37.5 |  | 11 | [10 empty] | 106000 |  |  |  | 2826.6667 | RTU AC with electric heat
VRF | Case Study | Energy Management Solutions | 2011 | MN |  |  | 200 |  | 98 | [10 empty] | 240000 |  |  |  | 1200 | window AC, electric heat
VRF | Case Study | Energy Management Solutions | 2011 | MN |  |  | 38.6875 |  | 20 | [10 empty] | 128600 |  |  |  | 3324.0711 | Packaged AC with boiler
|  | Average of EMS case studies | [21 empty] | 2322.1475
VRF | Case study | GSA VRF report | 2011 | [14 empty] | 23.2 | 2.68 |  |  |  | 0 | 0 | Packaged VAV |  | EES consulting
VRF | Case study | GSA VRF report | 2012 | [14 empty] | 16.5 | 3.5 |  |  |  | 0 | 0 | Packaged VAV |  | BPA
VRF | Case study | GSA VRF report | 2012 | [14 empty] | 33 | 6.5 |  |  |  | 0 | 0 | Packaged VAV |  | G pelser president of Hunter Davisson
VRF | Case study | GSA VRF report | 2007 | [15 empty] | 11% | [7 empty] | Goetzler 2007
VRF | Case study | GSA VRF report | 2008 | [15 empty] | 12.5% | [7 empty] | Amarnath and Blatt 2008
VRF | Case study | GSA VRF report | 2012 | [15 empty] | 25% | [7 empty] | C Richardson at Daikin
|  | Average of GSA case studies | [20 empty] | 0 |  | Packaged VAV
VRF | AVG | GSA VRF report | 2012 | [14 empty] | 24.2 | 1.2 |  |  |  | 0 | 0 | Chilled water VAV |  | GSA average of all sources
VRF | AVG | GSA VRF report | 2012 | [14 empty] | 24.2 | 3.9 |  |  |  | 0 | 0 | Packaged VAV |  | GSA average of all sources
VRF | AVG | GSA VRF report | 2012 | [14 empty] | 24.2 | 5.7 |  |  |  | 0 | 0 | Packaged Cnst Vol RTUs |  | GSA average of all sources
|  | Average of GSA VRF costs | [20 empty] | 0
VRF | case study | EMaine project |  |  |  |  | 74 | [9 empty] | 309735 | 26.4731 |  |  |  |  | 4185.6081
VRF | online | http://e3tnw.org/ItemDetail.aspx?id=200 | [15 empty] | 18 |  |  |  |  | 0
Data not used in Summary results
VRF | Spreadsheet | SCE13HC036 CA working paper | 2012-05-01 | CA | ND |  | 6 | 72 | [12 empty] | 1940 | 160 | 2100 | 469.8 | Packaged VAV baseline | All from CA SCE13 work paper spreadsheet analysis. Why are these costs so low? These do not seem valid. | RS Means and interviews
VRF | report | CAL-TF-W-07152015: CA Technical Forum - Work Paper Abstract | 2014-09-01 | CA | ND | [18 empty] | 547 | Packaged VAV DX Multi-Zone with Gas Reheat | No data on size, non-residential | interviews
1067.8347
Note on T23: Jesse Remillard: midpoint of range 0% to 22%
Note on T24: Jesse Remillard: Midpoint of 5% to 20% range

## Multi-Split
Multi-Split Data Collection
Unit Type | Source Type | Source | Date | Region | Manufacturer | Tons | kBtu/hr | Zones | EER | SEER | HSPF | COP | Incremental Cost | Incremental Cost Per Ton | Data from
Data not used in summary
AC Split Unit-< 5 Tons (55 kBtuh)-14 SEER | spreadsheet | TRM100_nonres AC and HP Units_training | 2014-03-09 | CA |  | <5 | 55 |  |  | 14 |  |  | 1011.64 | 202.328 | CA IOU Work Paper
AC Split Unit-< 5 Tons (55 kBtuh)-15 SEER | spreadsheet | TRM100_nonres AC and HP Units_training | 2014-03-09 | CA |  | <5 | 55 |  |  | 15 |  |  | 1063.99 | 212.798 | CA IOU Work Paper
AC Split Unit- 5 Tons (55-64 kBtuh)-14 SEER | spreadsheet | TRM100_nonres AC and HP Units_training | 2014-03-09 | CA |  | 5 | 60 |  |  | 14 |  |  | 559.67 | 111.934 | CA IOU Work Paper
AC Split Unit- 5 Tons (55-64 kBtuh)-15 SEER | spreadsheet | TRM100_nonres AC and HP Units_training | 2014-03-09 | CA |  | 5 | 60 |  |  | 15 |  |  | 587.22 | 117.444 | CA IOU Work Paper
HP Split Unit-< 5 Tons (55 kBtuh)-14 SEER 8.5 HSPF | spreadsheet | TRM100_nonres AC and HP Units_training | 2014-03-09 | CA |  | <5 | 55 |  |  | 14 | 8.5 |  | 741.8 | 148.36 | CA IOU Work Paper
HP Split Unit-< 5 Tons (55 kBtuh)-15 SEER 9 HSPF | spreadsheet | TRM100_nonres AC and HP Units_training | 2014-03-09 | CA |  | <5 | 55 |  |  | 15 | 9 |  | 741.8 | 148.36 | CA IOU Work Paper
HP Split Unit-5 Tons (55-64 kBtuh)-14 SEER 8.5 HSPF | spreadsheet | TRM100_nonres AC and HP Units_training | 2014-03-09 | CA |  | 5 | 55-64 |  |  | 14 | 8.5 |  | 501.97 | 100.394 | CA IOU Work Paper
HP Split Unit-5 Tons (55-64 kBtuh)-15 SEER 9 HSPF | spreadsheet | TRM100_nonres AC and HP Units_training | 2014-03-09 | CA |  | 5 | 55-64 |  |  | 15 | 9 |  | 516.16 | 103.232 | CA IOU Work Paper

## Baseline Costs
Baseline Data
Yellow cells were calculated by averaging data
Unit Type (Packaged) | Source Type | Date | Region | Heating System | Tons | kBtu/hr | Zones | EER | SEER | HSPF | COP | Total Equip Cost | Labor hours | Labor Rate | Equipment cost | Equipment cost per ton | Labor per ton | Installed Cost per Ton | Total installed cost | Average | Notes | Source
Title 24 baseline single-zone Packaged DX Air Conditioner with gas heating | Report | 2012-03-25 | CA | gas fired | 5 |  | Single | [8 empty] | 1000 | 265 | 1265 |  |  | Averaged from RS means and interviews. RS Means: 23 74 33.10 1140, 5 ton cooling, 112 MBH heating | SCE13HC036 CA working paper
Title 24 baseline single-zone Packaged DX Heat Pump | Report | 2012-03-25 | CA | hp | 5 |  | Single | [8 empty] | 1000 | 240 | 1240 |  |  | Averaged from RS means and interviews. RS Means:23 74 33.10 1310, Electic cool, electric heat 5 ton | SCE13HC036 CA working paper
Title 24 baseline multi-zone Packaged DX Variable Air Volume (VAV) Air Conditioner with gas boiler and reheat | Report | 2012-03-25 | CA | Gas boiler and reheat | 105 |  | Multi | [8 empty] | 1400 | 160 | 1560 |  |  | Averaged from RS means and interviews. RS Means:23 74 33.10 7130, multizone, cool/heat, VAV, 105 ton cooling | SCE13HC036 CA working paper
1355
Baseline | Report | 2011 | [15 empty] | 700 |  |  |  | EES 2011 study for BPA
Baseline | Report | 2011 | [15 empty] | 1200 |  |  |  | EES 2011 study for BPA
950
Packaged air source heat pump small | Navigant - sample data report and spreadsheet | 2014 |  |  | 3 | [9 empty] | 2763.4463 | 921.1488 | 305.6667 | 1226.8215 | 3680.4644 |  |  | 2014 NEEP Incremental Cost Study
Packaged air source heat pump small | Navigant - sample data report and spreadsheet | 2014 |  |  | 4 | [9 empty] | 4260.1079 | 1065.027 | 229.25 | 1294.2815 | 5177.126 |  |  | 2014 NEEP Incremental Cost Study
Packaged air source heat pump small | Navigant - sample data report and spreadsheet | 2014 |  |  | 5 | [9 empty] | 5756.7695 | 1151.3539 | 183.4 | 1334.7575 | 6673.7875 |  |  | 2014 NEEP Incremental Cost Study
1285.2868
RTUs | case study |  |  |  | 74 | [12 empty] | 3664.9865 | 271209 |  |  | EMaine project
code compliant baseline |  | 2016 | NW | [14 empty] | 0 |  |  |  | http://e3tnw.org/ItemDetail.aspx?id=200
22.4
20.3
18.5
VAV |  | 2013 | [15 empty] | 0 |  |  |  | GSA VRF report http://www.gsa.gov/portal/mediaId/169771/fileName/GPG_VRF_Report_-_FINAL_DRAFT_4-16-13.action
Data not used in summary
AC Pkg Unit-< 5 Tons (55kBtuh)-14 SEER | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | <5 | 55 |  |  | 14 | [8 empty] | 1063.2 |  | 842.7725 | Packaged AC 5 tons or less | TRM100_nonres AC and HP Units_training
AC Pkg Unit-< 5 Tons (55kBtuh)-15 SEER | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | <5 | 55 |  |  | 15 | [8 empty] | 1161 |  |  |  | TRM100_nonres AC and HP Units_training
AC Pkg Unit-5 Tons (55-64 kBtuh)-14 SEER | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 5 | 55-64 |  |  | 14 | [8 empty] | 559.67 |  |  |  | TRM100_nonres AC and HP Units_training
AC Pkg Unit-5 Tons (55-64 kBtuh)-15 SEER | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 5 | 55-64 |  |  | 15 | [8 empty] | 587.22 |  |  |  | TRM100_nonres AC and HP Units_training
AC Unit-6to8.5 Tons (65-109 kBtuh)-11.5 EER | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 6-8.5 | 65-109 |  | 11.5 | [9 empty] | 559.67 |  | 621.9944 | Packaged AC greater than 5 tons | TRM100_nonres AC and HP Units_training
AC Unit-6to8.5 Tons (65-109 kBtuh)-12 EER | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 6-8.5 | 65-109 |  | 12 | [9 empty] | 587.22 |  |  |  | TRM100_nonres AC and HP Units_training
AC Unit-10 Tons (110-134 kBtuh)-11.5 EER | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 10 | 110-134 |  | 11.5 | [9 empty] | 559.67 |  |  |  | TRM100_nonres AC and HP Units_training
AC Unit-10 Tons (110-134 kBtuh)-12 EER | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 10 | 110-134 |  | 12 | [9 empty] | 587.22 |  |  |  | TRM100_nonres AC and HP Units_training
AC Unit-12to17 Tons (135-239 kBtuh)-11.5 EER | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 12.0-17.0 | 135-239 |  | 11.5 | [9 empty] | 555.27 |  |  |  | TRM100_nonres AC and HP Units_training
AC Unit-12to17 Tons (135-239 kBtuh)-12 EER | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 12.0-17.0 | 135-239 |  | 12 | [9 empty] | 572.02 |  |  |  | TRM100_nonres AC and HP Units_training
AC Unit-20to60 Tons (240-759 kBtuh)-10.5 EER | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 20-60 | 240-759 |  | 10.5 | [9 empty] | 711.74 |  |  |  | TRM100_nonres AC and HP Units_training
AC Unit-20to60 Tons (240-759 kBtuh)-10.8 EER | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 20-60 | 240-759 |  | 10.8 | [9 empty] | 765.86 |  |  |  | TRM100_nonres AC and HP Units_training
AC Unit->60 Tons (760 kBtuh)-10.2 EER | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | >60 | 760 |  | 10.2 | [9 empty] | 699.28 |  |  |  | TRM100_nonres AC and HP Units_training
HP Pkg Unit-< 5 Tons (55 kBtuh)-14 SEER 8.0 HSPF | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | <5 | 55 |  |  | 14 | 8 | [7 empty] | 741.8 |  | 625.4325 | Packaged HP 5 tons or less | TRM100_nonres AC and HP Units_training
HP Pkg Unit-< 5 Tons (55 kBtuh)-15 SEER 8.5 HSPF | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | <5 | 55 |  |  | 15 | 8.5 | [7 empty] | 741.8 |  |  |  | TRM100_nonres AC and HP Units_training
HP Pkg Unit-5 Tons (55-64 kBtuh)-14 SEER 8.0 HSPF | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 5 | 55-64 |  |  | 14 | 8 | [7 empty] | 501.97 |  |  |  | TRM100_nonres AC and HP Units_training
HP Pkg Unit-5 Tons (55-64 kBtuh)-15 SEER 8.5 HSPF | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 5 | 55-64 |  |  | 15 | 8.5 | [7 empty] | 516.16 |  |  |  | TRM100_nonres AC and HP Units_training
HP Unit-6to8.5 Tons (65-109 kBtuh)-11.5 EER 3.4 COP | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 6-8.5 | 65-109 |  | 11.5 |  |  | 3.4 | [6 empty] | 617.36 |  | 627.19 | Packaged HP greater than 5 tons | TRM100_nonres AC and HP Units_training
HP Unit-6to8.5 Tons (65-109 kBtuh)-12 EER 3.4 COP | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 6-8.5 | 65-109 |  | 12 |  |  | 3.4 | [6 empty] | 658.29 |  |  |  | TRM100_nonres AC and HP Units_training
HP Unit-10 Tons (110-134 kBtuh)-11.5 EER 3.4 COP | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 10 | 110-134 |  | 11.5 |  |  | 3.4 | [6 empty] | 617.36 |  |  |  | TRM100_nonres AC and HP Units_training
HP Unit-10 Tons (110-134 kBtuh)-12 EER 3.4 COP | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 10 | 110-134 |  | 12 |  |  | 3.2 | [6 empty] | 658.29 |  |  |  | TRM100_nonres AC and HP Units_training
HP Unit-12to17 Tons (135-239 kBtuh)-11.5 EER 3.2 COP | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 12.0-17.0 | 135-239 |  | 11.5 |  |  | 3.2 | [6 empty] | 555.27 |  |  |  | TRM100_nonres AC and HP Units_training
HP Unit-12to17 Tons (135-239 kBtuh)-12 EER 3.2 COP | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 12.0-17.0 | 135-239 |  | 12 |  |  | 3.2 | [6 empty] | 572.02 |  |  |  | TRM100_nonres AC and HP Units_training
HP Unit-20 Tons (240 kBtuh)-10.8 EER 3.2 COP | CA IOU Work Paper | CA IOU Work Paper | 2014-03-09 | CA |  | 20 | 240 |  | 3.5 | [9 empty] | 711.74 |  |  |  | TRM100_nonres AC and HP Units_training
660.8792

## Equipment Standards
DOE small commercial as of may 16 2012
Source: | https://www1.eere.energy.gov/buildings/appliance_standards/product.aspx/productid/77
IECC 2012 page C41

## ROT & Market Trends
Rule of Thumb and Market Trends
Rule of thumb for square footage conversions to tonnage: | 400 | sq ft per ton
Sources
Greg Hasselback of Mitsubishi
Bonneville Power Association VRF report
http://www.greenbuildingadvisor.com/blogs/dept/musings/calculating-cooling-loads
http://www.sawnee.com/content/hvac
http://www.achrnews.com/articles/86221-rules-of-thumb-for-troubleshooting
Comments
A lot of folks discussing that this ROT will apply only to older buildings or buildings in warmer climates. The industry trend is to move towards a 600 sq ft per ton ROT, and potentially even higher for colder climates and or newer, better insulated and efficient buildings.
Market Trends
The cost of electricity versus the cost of natural gas has hurt the market in recent months
Soon smaller sized "micro-VRF systems" will be coming to market for residential and small commercial applications in the under 5 tons range
The market is currently mostly retrofit applications
Still a lot of potential in colder climates with the growing availability of cold weather designed systems
NYC is the number 1 VRF market in the country followed by CA. A big part of this is the availability of space
Advancements in the combination of ducted and ductless indoor units may help reduce costs in the future