## Summary
Advanced Rooftop Units (RTUs)
Incremental Cost Data for Advanced Packaged RTUs
CEE Efficiency Tier
Capacity | Reference |  | Tier 1 | Tier 2 | Tier 2+ | Advanced Tier
≤65,000 btu/h | 2011 NEEP Phase I Study |  | $123/ton | $174/ton | N.D. | N.D.
| 2016 DEER Cost Data |  | 90.4406 | 180.8813 | 271.3219 | 361.7625
| Manufacturer data |  | $75-$100 | N.D. | N.D. | N.D.
>65,000 btu/h and ≤135,000 btu/h | 2011 NEEP Phase I Study |  | $184/ton | $235/ton | N.D. | N.D.
| 2016 DEER Cost Data |  | 138.733 | 277.467 | 416.201 | 554.934
Incremental Cost Data for Advanced packaged Heat Pumps
CEE Efficiency Tier
Capacity | Tier 1 | Tier 2 | Tier 2+ | Advanced Tier
≤65,000 btu/h | 142 | 284 | 426 | N/A
>65,000 btu/h and ≤135,000 btu/h | N.D. | N.D. | N.D. | N.D.

## 2016DEERData
DEER2016 Cost Workbook for Packaged and Split HVAC Systems
Information finalized by ERS on 3/23/2016
Source: | http://www.deeresources.com/index.php/deer-versions/deer-2016/deer2016-technology-costs#DXHVAC
| SEER (units with capacities < 65,000 btu/h) | Cooling Only $/ton | Heat Pumps $/ton
| 15 | 90.4406 | 141.964
| 16 | 180.8813 | 283.928
| 17 | 271.3219 | 425.892
| 18 | 361.7625 | N/A
| EER (units with capacities < 135,000 btu/h & > 65,000 btu/h) | DX
| 11.5 | 138.733
| 12 | 277.467
| 12.5 | 416.201
| 13 | 554.934
Ex Ante Source Tables Export
Measure Table (exante.Measure)
This file created on 8/11/2015 11:50:01 AM while connected to localhost as sptviewer.
Program/Database Description: READI v.2.2.1 (Current DEER and Non-DEER Ex Ante data. Includes data for review) | [51 empty] | Determination of Incremental Measure Cost
[49 empty] | size |  |  | Meas Tech |  |  | Std Tech
Index | MeasureID | Description | Version | VersionSource | LastMod | EnergyImpactID | MeasImpactType | EnImpCalcType | ImpScaleBasis | StdScaleVal | PreScaleVal | ImpWeighting | WeightGroupID | ApplyIE | IETableName | TechBased | Sector | PA | UseCategory | UseSubCategory | TechGroup | TechType | MeasCostID | StdCostID | EUL_ID | PreDesc | StdDesc | MeasDesc | PreTechID | StdTechID | MeasTechID | Status | Comment | PreMultiTech | StdMultiTech | SourceDesc | SupportedAppType | RUL_ID | LegacyID | MeasQualifierGroup | StartDate | ExpiryDate | ReviewStatus | MeasID_SCE | MeasID_PGE | MeasID_SDG | MeasID_SCG | MeasType | min | max | use | const | per unit | $ | const | per unit | $ | Incremental $/unit | MeasureID
801 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, no Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 1664.58 | 1150.27 | 13167.28 | 277.25 | 1150.27 | 11779.95 | 138.733 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer
802 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, no Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 3051.92 | 1150.27 | 14554.62 | 277.25 | 1150.27 | 11779.95 | 277.467 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer
803 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, no Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, no Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 5826.59 | 1150.27 | 17329.29 | 277.25 | 1150.27 | 11779.95 | 554.934 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer
804 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.5-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 1664.58 | 1150.27 | 13167.28 | 277.25 | 1150.27 | 11779.95 | 138.733 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-11p5eer-wPreEcono
805 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER12.0-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 3051.92 | 1150.27 | 14554.62 | 277.25 | 1150.27 | 11779.95 | 277.467 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-12p0eer-wPreEcono
806 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 65-110 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 65 - 110 kBTU/h, EER = 13 (1 spd IEER = 13.9, 2 spd IEER = 15.1), EIR = 0.226, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-65to110kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-65to110kBTUh-EER13.0-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 5826.59 | 1150.27 | 17329.29 | 277.25 | 1150.27 | 11779.95 | 554.934 | NE-HVAC-airAC-SpltPkg-65to109kBtuh-13p0eer-wPreEcono
807 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-110to135kBTUh-EER11.5-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11.5 (1 spd IEER = 12.2, 2 spd IEER = 14.3), EIR = 0.26, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER11.5-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 1664.58 | 1150.27 | 13167.28 | 277.25 | 1150.27 | 11779.95 | 138.733 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-11p5eer
808 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-110to135kBTUh-EER12.0-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12 (1 spd IEER = 12.8, 2 spd IEER = 14.6), EIR = 0.247, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER12.0-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 3051.92 | 1150.27 | 14554.62 | 277.25 | 1150.27 | 11779.95 | 277.467 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p0eer
809 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12.5 (1 spd IEER = 13.3, 2 spd IEER = 14.9), EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-110to135kBTUh-EER12.5-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | HVAC-airAC | EER-Rated Pkg AC, 110-135 kBTU/h; Pre-2005: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2006 - 2009: EER = 10.1 (1 spd IEER = 10.6, 2 spd IEER = 13.6), one-speed fan, w/Econo; 2010 - 2013: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), one-speed fan, w/Econo; 2014 - 2015: EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 11 (1 spd IEER = 11.6, 2 spd IEER = 14.1), EIR = 0.273, Fan W/CFM = 0.4, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 110 - 135 kBTU/h, EER = 12.5 (1 spd IEER = 13.3, 2 spd IEER = 14.9), EIR = 0.236, Fan W/CFM = 0.4, two-speed fan, with Econo |  | dxAC-Com-Pkg-110to135kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-110to135kBTUh-EER12.5-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 4439.26 | 1150.27 | 15941.96 | 277.25 | 1150.27 | 11779.95 | 416.201 | NE-HVAC-airAC-SpltPkg-110to134kBtuh-12p5eer
810 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 14.2), EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER11.5-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2006 - 2009: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2010 - 2013: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 14.2), EIR = 0.255, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER11.5-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 1664.58 | 1150.27 | 13167.28 | -277.69 | 1150.27 | 11225.01 | 194.227 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-11p5eer
811 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12 (1 spd IEER = 13.1, 2 spd IEER = 14.8), EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.0-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2006 - 2009: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2010 - 2013: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12 (1 spd IEER = 13.1, 2 spd IEER = 14.8), EIR = 0.243, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER12.0-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 3051.92 | 1150.27 | 14554.62 | -277.69 | 1150.27 | 11225.01 | 332.961 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p0eer
812 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (1 spd IEER = 13.8, 2 spd IEER = 15.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 135-240 kBTU/h; Pre-2005: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2006 - 2009: EER = 9.5 (1 spd IEER = 9.6, 2 spd IEER = 11.6), one-speed fan, w/Econo; 2010 - 2013: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), one-speed fan, w/Econo; 2014 - 2015: EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 10.8 (1 spd IEER = 11.4, 2 spd IEER = 13.3), EIR = 0.274, Fan W/CFM = 0.41, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (1 spd IEER = 13.8, 2 spd IEER = 15.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo |  | dxAC-Com-Pkg-135to240kBTUh-EER10.8-2Spd | dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 4439.26 | 1150.27 | 15941.96 | -277.69 | 1150.27 | 11225.01 | 471.695 | NE-HVAC-airAC-SpltPkg-135to239kBtuh-12p5eer
813 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (1 spd IEER = 11.6, 2 spd IEER = 12.8), EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER10.8-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2010 - 2013: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 10.8 (1 spd IEER = 11.6, 2 spd IEER = 12.8), EIR = 0.255, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER10.8-2Spd | Available | Std and Meas Technologies vary by system configuration | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | -277.69 | 1150.27 | 11225.01 | -3052.36 | 1150.27 | 8450.34 | 277.467 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-10p8eer
814 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 13.6), EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER11.5-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2010 - 2013: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 11.5 (1 spd IEER = 12.4, 2 spd IEER = 13.6), EIR = 0.236, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER11.5-2Spd | Available | Std and Meas Technologies vary by system configuration | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 1664.58 | 1150.27 | 13167.28 | -3052.36 | 1150.27 | 8450.34 | 471.694 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-11p5eer
815 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (1 spd IEER = 13.6, 2 spd IEER = 14.8), EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-240to760kBTUh-EER12.5-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | HVAC-airAC | EER-Rated Pkg AC, 240-760 kBTU/h; Pre-2005: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2006 - 2009: EER = 9.3 (1 spd IEER = 9.8, 2 spd IEER = 11.1), one-speed fan, w/Econo; 2010 - 2013: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), one-speed fan, w/Econo; 2014 - 2015: EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 9.8 (1 spd IEER = 10.4, 2 spd IEER = 11.7), EIR = 0.286, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 240 - 760 kBTU/h, EER = 12.5 (1 spd IEER = 13.6, 2 spd IEER = 14.8), EIR = 0.213, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-240to760kBTUh-EER9.8-2Spd | dxAC-Com-Pkg-240to760kBTUh-EER12.5-2Spd | Available | Std and Meas Technologies vary by system configuration | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 4439.26 | 1150.27 | 15941.96 | -3052.36 | 1150.27 | 8450.34 | 749.162 | NE-HVAC-airAC-SpltPkg-240to759kBtuh-12p5eer
816 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (1 spd IEER = 10.9, 2 spd IEER = 12.1), EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER10.2-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2006 - 2009: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2010 - 2013: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 10.2 (1 spd IEER = 10.9, 2 spd IEER = 12.1), EIR = 0.273, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER10.2-2Spd | Available | Std and Meas Technologies vary by system configuration | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | -1942.49 | 1150.27 | 9560.21 | -3884.76 | 1150.27 | 7617.94 | 194.227 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-10p2eer
817 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (1 spd IEER = 11.8, 2 spd IEER = 13.1), EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER11.0-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2006 - 2009: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2010 - 2013: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 11 (1 spd IEER = 11.8, 2 spd IEER = 13.1), EIR = 0.249, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER11.0-2Spd | Available | Std and Meas Technologies vary by system configuration | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 277.25 | 1150.27 | 11779.95 | -3884.76 | 1150.27 | 7617.94 | 416.201 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-11p0eer
818 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (1 spd IEER = 13, 2 spd IEER = 14.2), EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2015-07-13 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgEER | dxAC-Com-Pkg-gte760kBTUh-EER12.0-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | HVAC-airAC | EER-Rated Pkg AC, 760+ kBTU/h; Pre-2005: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2006 - 2009: EER = 9 (1 spd IEER = 9.4, 2 spd IEER = 10.7), one-speed fan, w/Econo; 2010 - 2013: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), one-speed fan, w/Econo; 2014 - 2015: EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), two-speed fan, w/Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 9.5 (1 spd IEER = 10, 2 spd IEER = 11.3), EIR = 0.297, Fan W/CFM = 0.61, two-speed fan, with Econo | EER-rated packaged Air Conditioner, Size Range: 760 - kBTU/h, EER = 12 (1 spd IEER = 13, 2 spd IEER = 14.2), EIR = 0.224, Fan W/CFM = 0.61, two-speed fan, with Econo |  | dxAC-Com-Pkg-gte760kBTUh-EER9.5-2Spd | dxAC-Com-Pkg-gte760kBTUh-EER12.0-2Spd | Available | Std and Meas Technologies vary by system configuration | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 6.9 | 106 | 10 | 3051.92 | 1150.27 | 14554.62 | -3884.76 | 1150.27 | 7617.94 | 693.668 | NE-HVAC-airAC-SpltPkg-gte760kBtuh-12p0eer
819 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 15 (EER = 12.9), EIR = 0.234, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-15.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 15 (EER = 12.9), EIR = 0.234, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 2542.0341 | 388.05 | 4094.2341 | 2180.2716 | 388.05 | 3732.4716 | 90.4406 | NE-HVAC-airAC-Pkg-lt55kBtuh-15p0seer
820 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-16.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 2903.7966 | 388.05 | 4455.9966 | 2180.2716 | 388.05 | 3732.4716 | 180.8813 | NE-HVAC-airAC-Pkg-lt55kBtuh-16p0seer
821 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-17.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 3265.5591 | 388.05 | 4817.7591 | 2180.2716 | 388.05 | 3732.4716 | 271.3219 | NE-HVAC-airAC-Pkg-lt55kBtuh-17p0seer
822 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-lt55kBTUh-SEER-18.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.04), one-speed fan, no Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 14 (EER = 12), EIR = 0.246, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 18 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Pkg-lt55kBTUh-SEER-14.0 | dxAC-Com-Pkg-lt55kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 3627.3216 | 388.05 | 5179.5216 | 2180.2716 | 388.05 | 3732.4716 | 361.7625 | NE-HVAC-airAC-Pkg-lt55kBtuh-18p0seer
823 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 2542.0341 | 388.05 | 4094.2341 | 2180.2716 | 388.05 | 3732.4716 | 90.4406 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer
824 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 2903.7966 | 388.05 | 4455.9966 | 2180.2716 | 388.05 | 3732.4716 | 180.8813 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer
825 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 3265.5591 | 388.05 | 4817.7591 | 2180.2716 | 388.05 | 3732.4716 | 271.3219 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer
826 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 3627.3216 | 388.05 | 5179.5216 | 2180.2716 | 388.05 | 3732.4716 | 361.7625 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer
827 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 2542.0341 | 388.05 | 4094.2341 | 2180.2716 | 388.05 | 3732.4716 | 90.4406 | NE-HVAC-airAC-Pkg-55to65kBtuh-15p0seer-wPreEcono
828 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 2903.7966 | 388.05 | 4455.9966 | 2180.2716 | 388.05 | 3732.4716 | 180.8813 | NE-HVAC-airAC-Pkg-55to65kBtuh-16p0seer-wPreEcono
829 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 3265.5591 | 388.05 | 4817.7591 | 2180.2716 | 388.05 | 3732.4716 | 271.3219 | NE-HVAC-airAC-Pkg-55to65kBtuh-17p0seer-wPreEcono
830 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | pkgSEER | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airAC | Com SEER-Rated Pkg AC, 18-65 kBTU/h; pre-2001: SEER = 9.7 (EER = 9.21), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.06), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Pkg-55to65kBTUh-SEER-14.0 | dxAC-Com-Pkg-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 4 | 3627.3216 | 388.05 | 5179.5216 | 2180.2716 | 388.05 | 3732.4716 | 361.7625 | NE-HVAC-airAC-Pkg-55to65kBtuh-18p0seer-wPreEcono
831 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-15.0 | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 827.7228 | 331.2144 | 1821.366 | 551.3388 | 331.2144 | 1544.982 | 92.128 | NE-HVAC-airAC-Split-lt45kBtuh-15p0seer
832 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-16.0 | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1104.1068 | 331.2144 | 2097.75 | 551.3388 | 331.2144 | 1544.982 | 184.256 | NE-HVAC-airAC-Split-lt45kBtuh-16p0seer
833 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-17.0 | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1380.4908 | 331.2144 | 2374.134 | 551.3388 | 331.2144 | 1544.982 | 276.384 | NE-HVAC-airAC-Split-lt45kBtuh-17p0seer
834 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-lt45kBTUh-SEER-18.0 | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 12.17), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-lt45kBTUh-SEER-14.0 | dxAC-Com-Split-lt45kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1656.8748 | 331.2144 | 2650.518 | 551.3388 | 331.2144 | 1544.982 | 368.512 | NE-HVAC-airAC-Split-lt45kBtuh-18p0seer
835 | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-15.0 | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 827.7228 | 331.2144 | 1821.366 | 551.3388 | 331.2144 | 1544.982 | 92.128 | NE-HVAC-airAC-Split-45to55kBtuh-15p0seer
836 | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-16.0 | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1104.1068 | 331.2144 | 2097.75 | 551.3388 | 331.2144 | 1544.982 | 184.256 | NE-HVAC-airAC-Split-45to55kBtuh-16p0seer
837 | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-17.0 | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1380.4908 | 331.2144 | 2374.134 | 551.3388 | 331.2144 | 1544.982 | 276.384 | NE-HVAC-airAC-Split-45to55kBtuh-17p0seer
838 | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-45to55kBTUh-SEER-18.0 | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.82), one-speed fan, no Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated split Air Conditioners, Size Range: 45 - 55 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxAC-Com-Split-45to55kBTUh-SEER-14.0 | dxAC-Com-Split-45to55kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1656.8748 | 331.2144 | 2650.518 | 551.3388 | 331.2144 | 1544.982 | 368.512 | NE-HVAC-airAC-Split-45to55kBtuh-18p0seer
839 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 827.7228 | 331.2144 | 1821.366 | 551.3388 | 331.2144 | 1544.982 | 92.128 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer
840 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1104.1068 | 331.2144 | 2097.75 | 551.3388 | 331.2144 | 1544.982 | 184.256 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer
841 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1380.4908 | 331.2144 | 2374.134 | 551.3388 | 331.2144 | 1544.982 | 276.384 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer
842 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages do not include Economizer) | DEER2015 | D15 v1.0 | 2014-10-08 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, no Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, no Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1656.8748 | 331.2144 | 2650.518 | 551.3388 | 331.2144 | 1544.982 | 368.512 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer
843 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 15 (EER = 12.6), EIR = 0.236, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 827.7228 | 331.2144 | 1821.366 | 551.3388 | 331.2144 | 1544.982 | 92.128 | NE-HVAC-airAC-Split-55to65kBtuh-15p0seer-wPreEcono
844 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1104.1068 | 331.2144 | 2097.75 | 551.3388 | 331.2144 | 1544.982 | 184.256 | NE-HVAC-airAC-Split-55to65kBtuh-16p0seer-wPreEcono
845 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1380.4908 | 331.2144 | 2374.134 | 551.3388 | 331.2144 | 1544.982 | 276.384 | NE-HVAC-airAC-Split-55to65kBtuh-17p0seer-wPreEcono
846 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo (Pre-existing vintages include Economizer) | DEER2015 | D15 v1.0 | 2014-10-15 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airAC | Commercial SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan, w/Econo; post-2001: SEER = 13 (EER = 11.08), one-speed fan, w/Econo; 2014: SEER = 14 (EER = 11.75), two-speed fan, w/Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 14 (EER = 11.7), EIR = 0.249, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated split Air Conditioners, Size Range: 55 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxAC-Com-Split-55to65kBTUh-SEER-14.0 | dxAC-Com-Split-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1656.8748 | 331.2144 | 2650.518 | 551.3388 | 331.2144 | 1544.982 | 368.512 | NE-HVAC-airAC-Split-55to65kBtuh-18p0seer-wPreEcono
847 | RE-HV-ResAC-lt45kBtuh-15S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-15S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-15.0 | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 827.7228 | 331.2144 | 1821.366 | 551.3388 | 331.2144 | 1544.982 | 92.128 | RE-HV-ResAC-lt45kBtuh-15S
848 | RE-HV-ResAC-lt45kBtuh-16S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-16S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-16.0 | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1104.1068 | 331.2144 | 2097.75 | 551.3388 | 331.2144 | 1544.982 | 184.256 | RE-HV-ResAC-lt45kBtuh-16S
849 | RE-HV-ResAC-lt45kBtuh-17S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-17S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-17.0 | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1380.4908 | 331.2144 | 2374.134 | 551.3388 | 331.2144 | 1544.982 | 276.384 | RE-HV-ResAC-lt45kBtuh-17S
850 | RE-HV-ResAC-lt45kBtuh-18S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-18S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-18.0 | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1656.8748 | 331.2144 | 2650.518 | 551.3388 | 331.2144 | 1544.982 | 368.512 | RE-HV-ResAC-lt45kBtuh-18S
851 | RE-HV-ResAC-lt45kBtuh-19S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 19 (EER = 14.8), EIR = 0.201, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-19S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 19 (EER = 14.8), EIR = 0.201, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-19.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard
852 | RE-HV-ResAC-lt45kBtuh-20S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 20 (EER = 15.6), EIR = 0.19, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-20S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 20 (EER = 15.6), EIR = 0.19, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-20.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard
853 | RE-HV-ResAC-lt45kBtuh-21S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 21 (EER = 16.4), EIR = 0.18, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-lt45kBtuh-21S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 12.17), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 45 kBTU/h, SEER = 14 (EER = 12.2), EIR = 0.239, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 21 (EER = 16.4), EIR = 0.18, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-lt45kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-21.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard
855 | RE-HV-ResAC-45to65kBtuh-15S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-15S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-15.0 | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 15 (EER = 12.8), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 827.7228 | 331.2144 | 1821.366 | 551.3388 | 331.2144 | 1544.982 | 92.128 | RE-HV-ResAC-45to65kBtuh-15S
856 | RE-HV-ResAC-45to65kBtuh-16S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-16S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-16.0 | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 16 (EER = 12.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1104.1068 | 331.2144 | 2097.75 | 551.3388 | 331.2144 | 1544.982 | 184.256 | RE-HV-ResAC-45to65kBtuh-16S
857 | RE-HV-ResAC-45to65kBtuh-17S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-17S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-17.0 | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 17 (EER = 13.3), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1380.4908 | 331.2144 | 2374.134 | 551.3388 | 331.2144 | 1544.982 | 276.384 | RE-HV-ResAC-45to65kBtuh-17S
858 | RE-HV-ResAC-45to65kBtuh-18S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-18S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER | dxAC-Res-Split-SEER-18.0 | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 18 (EER = 14), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.4 | 5 | 3 | 1656.8748 | 331.2144 | 2650.518 | 551.3388 | 331.2144 | 1544.982 | 368.512 | RE-HV-ResAC-45to65kBtuh-18S
859 | RE-HV-ResAC-45to65kBtuh-19S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 19 (EER = 14.8), EIR = 0.201, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-19S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 19 (EER = 14.8), EIR = 0.201, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-19.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard
860 | RE-HV-ResAC-45to65kBtuh-20S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 20 (EER = 15.6), EIR = 0.19, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-20S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 20 (EER = 15.6), EIR = 0.19, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-20.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard
861 | RE-HV-ResAC-45to65kBtuh-21S | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 21 (EER = 16.4), EIR = 0.18, Fan W/CFM = 0.23, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResAC-45to65kBtuh-21S | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | SpaceCool | dxAC_equip | spltSEER |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | HV-ResAC | Residential SEER-rated split Air Conditioners, 18-65 kBTU/h; pre-2001: SEER = 10 (EER = 8.52), one-speed fan; post-2001: SEER = 13 (EER = 11.08), one-speed fan; 2014: SEER = 14 (EER = 11.82), one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 45 - 65 kBTU/h, SEER = 14 (EER = 11.8), EIR = 0.247, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Air Conditioners, Size Range: 18 - 65 kBTU/h, SEER = 21 (EER = 16.4), EIR = 0.18, Fan W/CFM = 0.23, two-speed fan |  | dxAC-Res-Split-45to65kBTUh-SEER-14.0 | dxAC-Res-Split-SEER-21.0 | Available |  | FALSE | FALSE |  | ErRobNc | HV-ResAC |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard
863 | RE-HV-ResHP-15p0S-8p7H | Residential SEER-rated split Heat Pumps, SEER = 15 (EER = 12.8), HSPF = 8.7 (COP = 3.68), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResHP-15p0S-8p7H | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Res-Split-SEER-15.0 | dxHP-Res-Split-SEER-14.0 | HVAC-airHP | Res SEER-Rated Splt HP, 7.1-3.01 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan; 2014: SEER = 14 (HSPF = 8.2), one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 14 (EER = 11.9), HSPF = 8.2 (COP = 3.48), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 15 (EER = 12.8), HSPF = 8.7 (COP = 3.68), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan |  | dxHP-Res-Split-SEER-14.0 | dxHP-Res-Split-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1097.5404 | 594.5616 | 2881.2252 | 549.2484 | 594.5616 | 2332.9332 | 182.764 | RE-HV-ResHP-15p0S-8p7H
864 | RE-HV-ResHP-16p0S-9p0H | Residential SEER-rated split Heat Pumps, SEER = 16 (EER = 12.5), HSPF = 9 (COP = 3.57), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResHP-16p0S-9p0H | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Res-Split-SEER-16.0 | dxHP-Res-Split-SEER-14.0 | HVAC-airHP | Res SEER-Rated Splt HP, 7.1-3.01 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan; 2014: SEER = 14 (HSPF = 8.2), one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 14 (EER = 11.9), HSPF = 8.2 (COP = 3.48), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 16 (EER = 12.5), HSPF = 9 (COP = 3.57), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan |  | dxHP-Res-Split-SEER-14.0 | dxHP-Res-Split-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1645.8324 | 594.5616 | 3429.5172 | 549.2484 | 594.5616 | 2332.9332 | 365.528 | RE-HV-ResHP-16p0S-9p0H
865 | RE-HV-ResHP-17p0S-9p4H | Residential SEER-rated split Heat Pumps, SEER = 17 (EER = 13.3), HSPF = 9.4 (COP = 3.74), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResHP-17p0S-9p4H | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Res-Split-SEER-17.0 | dxHP-Res-Split-SEER-14.0 | HVAC-airHP | Res SEER-Rated Splt HP, 7.1-3.01 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan; 2014: SEER = 14 (HSPF = 8.2), one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 14 (EER = 11.9), HSPF = 8.2 (COP = 3.48), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 17 (EER = 13.3), HSPF = 9.4 (COP = 3.74), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan |  | dxHP-Res-Split-SEER-14.0 | dxHP-Res-Split-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2194.1244 | 594.5616 | 3977.8092 | 549.2484 | 594.5616 | 2332.9332 | 548.292 | RE-HV-ResHP-17p0S-9p4H
866 | RE-HV-ResHP-18p0S-9p7H | Residential SEER-rated split Heat Pumps, SEER = 18 (EER = 14), HSPF = 9.7 (COP = 3.86), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan | DEER2015 | D15 v1.0 | 2014-10-08 | RE-HV-ResHP-18p0S-9p7H | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Res | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Res-Split-SEER-18.0 | dxHP-Res-Split-SEER-14.0 | HVAC-airHP | Res SEER-Rated Splt HP, 7.1-3.01 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan; 2014: SEER = 14 (HSPF = 8.2), one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 14 (EER = 11.9), HSPF = 8.2 (COP = 3.48), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan | Residential SEER-rated split Heat Pumps, SEER = 18 (EER = 14), HSPF = 9.7 (COP = 3.86), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan |  | dxHP-Res-Split-SEER-14.0 | dxHP-Res-Split-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2742.4164 | 594.5616 | 4526.1012 | 549.2484 | 594.5616 | 2332.9332 | 731.056 | RE-HV-ResHP-18p0S-9p7H
867 | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.226, Fan W/CFM = 0.29, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-lt55kBTUh-SEER-15.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), one-speed fan, no Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.226, Fan W/CFM = 0.29, one-speed fan, without Econo |  | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3103.5228 | 358.4592 | 4178.9004 | 2677.6308 | 358.4592 | 3753.0084 | 141.964 | NE-HVAC-airHP-Pkg-lt55kBtuh-15p0seer-8p2hspf
868 | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-lt55kBTUh-SEER-16.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), one-speed fan, no Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3529.4148 | 358.4592 | 4604.7924 | 2677.6308 | 358.4592 | 3753.0084 | 283.928 | NE-HVAC-airHP-Pkg-lt55kBtuh-16p0seer-8p5hspf
869 | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-lt55kBTUh-SEER-17.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), one-speed fan, no Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Pkg-lt55kBTUh-SEER-14.0 | dxHP-Com-Pkg-lt55kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3955.3068 | 358.4592 | 5030.6844 | 2677.6308 | 358.4592 | 3753.0084 | 425.892 | NE-HVAC-airHP-Pkg-lt55kBtuh-17p0seer-9p0hspf
870 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3103.5228 | 358.4592 | 4178.9004 | 2677.6308 | 358.4592 | 3753.0084 | 141.964 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf
871 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3529.4148 | 358.4592 | 4604.7924 | 2677.6308 | 358.4592 | 3753.0084 | 283.928 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf
872 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3955.3068 | 358.4592 | 5030.6844 | 2677.6308 | 358.4592 | 3753.0084 | 425.892 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf
873 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-wPreEcono | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.2), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3103.5228 | 358.4592 | 4178.9004 | 2677.6308 | 358.4592 | 3753.0084 | 141.964 | NE-HVAC-airHP-Pkg-55to65kBtuh-15p0seer-8p2hspf-wPreEcono
874 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-wPreEcono | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 8.5), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3529.4148 | 358.4592 | 4604.7924 | 2677.6308 | 358.4592 | 3753.0084 | 283.928 | NE-HVAC-airHP-Pkg-55to65kBtuh-16p0seer-8p5hspf-wPreEcono
875 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-wPreEcono | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | pkgSEER | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Pkg HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8), two-speed fan, w/Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.0), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Packaged Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.0), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Pkg-55to65kBTUh-SEER-14.0 | dxHP-Com-Pkg-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 2 | 5 | 3 | 3955.3068 | 358.4592 | 5030.6844 | 2677.6308 | 358.4592 | 3753.0084 | 425.892 | NE-HVAC-airHP-Pkg-55to65kBtuh-17p0seer-9p0hspf-wPreEcono
876 | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-15.0 | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.232, Fan W/CFM = 0.25, one-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1097.5404 | 594.5616 | 2881.2252 | 549.2484 | 594.5616 | 2332.9332 | 182.764 | NE-HVAC-airHP-Split-lt55kBtuh-15p0seer-8p7hspf
877 | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-16.0 | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1645.8324 | 594.5616 | 3429.5172 | 549.2484 | 594.5616 | 2332.9332 | 365.528 | NE-HVAC-airHP-Split-lt55kBtuh-16p0seer-9p0hspf
878 | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-17.0 | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2194.1244 | 594.5616 | 3977.8092 | 549.2484 | 594.5616 | 2332.9332 | 548.292 | NE-HVAC-airHP-Split-lt55kBtuh-17p0seer-9p4hspf
879 | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-lt55kBTUh-SEER-18.0 | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), one-speed fan, no Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 55 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.245, Fan W/CFM = 0.29, one-speed fan, without Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 18 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, without Econo |  | dxHP-Com-Split-lt55kBTUh-SEER-14.0 | dxHP-Com-Split-lt55kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2742.4164 | 594.5616 | 4526.1012 | 549.2484 | 594.5616 | 2332.9332 | 731.056 | NE-HVAC-airHP-Split-lt55kBtuh-18p0seer-9p7hspf
880 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1097.5404 | 594.5616 | 2881.2252 | 549.2484 | 594.5616 | 2332.9332 | 182.764 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf
881 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1645.8324 | 594.5616 | 3429.5172 | 549.2484 | 594.5616 | 2332.9332 | 365.528 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf
882 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2194.1244 | 594.5616 | 3977.8092 | 549.2484 | 594.5616 | 2332.9332 | 548.292 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf
883 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, no Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, no Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2742.4164 | 594.5616 | 4526.1012 | 549.2484 | 594.5616 | 2332.9332 | 731.056 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf
884 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 15 (HSPF = 8.7), EIR = 0.256, Fan W/CFM = 0.25, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-15.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1097.5404 | 594.5616 | 2881.2252 | 549.2484 | 594.5616 | 2332.9332 | 182.764 | NE-HVAC-airHP-Split-55to65kBtuh-15p0seer-8p7hspf-wPreEcono
885 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 16 (HSPF = 9.0), EIR = 0.238, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-16.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 1645.8324 | 594.5616 | 3429.5172 | 549.2484 | 594.5616 | 2332.9332 | 365.528 | NE-HVAC-airHP-Split-55to65kBtuh-16p0seer-9p0hspf-wPreEcono
886 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 17 (HSPF = 9.4), EIR = 0.223, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-17.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2194.1244 | 594.5616 | 3977.8092 | 549.2484 | 594.5616 | 2332.9332 | 548.292 | NE-HVAC-airHP-Split-55to65kBtuh-17p0seer-9p4hspf-wPreEcono
887 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-wPreEcono | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo | DEER2015 | D15 v1.0 | 2014-10-28 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-wPreEcono | DEER | Standard | None |  |  | None |  | FALSE |  | FALSE | Com | Any | HVAC | HeatCool | dxHP_equip | spltSEER | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | HVAC-airHP | Com SEER-Rated Split HP, 18-65 kBTU/h; pre-2001: SEER = 10 (HSPF = 7.1), one-speed fan, w/Econo; post-2001: SEER = 13 (HSPF = 8.2), one-speed fan, w/Econo; 2014: SEER = 14 (HSPF = 8.2), two-speed fan, w/Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 14 (HSPF = 8.2), EIR = 0.27, Fan W/CFM = 0.29, two-speed fan, with Econo | Commercial SEER-rated Split Heat Pumps, Size Range: 55 - 65 kBTU/h, SEER = 18 (HSPF = 9.7), EIR = 0.209, Fan W/CFM = 0.27, two-speed fan, with Econo |  | dxHP-Com-Split-55to65kBTUh-SEER-14.0 | dxHP-Com-Split-55to65kBTUh-SEER-18.0 | Available |  | FALSE | FALSE |  | ErRobNc | HVAC-airHP |  | None | 2015-01-01 |  | DEER |  |  |  |  | Standard | 1.5 | 5 | 3 | 2742.4164 | 594.5616 | 4526.1012 | 549.2484 | 594.5616 | 2332.9332 | 731.056 | NE-HVAC-airHP-Split-55to65kBtuh-18p0seer-9p7hspf-wPreEcono
901 | NG-HVAC-Blr-HW-lt300kBtuh-84p0AFUE-Drft | Hot water boiler (< 300 kBtuh, 84.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-84p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF | W-Boiler_AF-lt300k-0.84-fDraft |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 84.0 AFUE, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 90 | 240 | 200 | 1061 | 17.61 | 4583 |  |  |  |  | NG-HVAC-Blr-HW-lt300kBtuh-84p0AFUE-Drft | 7 | #N/A | W-Boiler_AF-lt300k-0.84-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
902 | NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Drft | Hot water boiler (< 300 kBtuh, 84.5 AFUE, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF | W-Boiler_AF-lt300k-0.845-fDraft |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 84.5 AFUE, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 90 | 240 | 200 | 1784 | 17.61 | 5306 |  |  |  |  | NG-HVAC-Blr-HW-lt300kBtuh-84p5AFUE-Drft | 6 | #N/A | W-Boiler_AF-lt300k-0.845-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
903 | NG-HVAC-Blr-HW-lt300kBtuh-85p0AFUE-Drft | Hot water boiler (< 300 kBtuh, 85.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-85p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF | W-Boiler_AF-lt300k-0.85-fDraft |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 85.0 AFUE, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 90 | 240 | 200 | 2506 | 17.61 | 6028 |  |  |  |  | NG-HVAC-Blr-HW-lt300kBtuh-85p0AFUE-Drft | 8 | #N/A | W-Boiler_AF-lt300k-0.85-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
904 | NG-HVAC-Blr-HW-lt300kBtuh-87p0AFUE-Drft | Hot water boiler (< 300 kBtuh, 87.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-87p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 87.0 AFUE, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | W-Boiler_AF-lt300k-0.87-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
905 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndStd | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndStd | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | W-Boiler_AF-lt300k-0.9-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
906 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndLow | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndLow | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, OA reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | W-Boiler_AF-lt300k-0.9-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
907 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndReset | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, load reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-90p0AFUE-CndReset | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 90.0 AFUE, condensing, load reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | W-Boiler_AF-lt300k-0.9-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
908 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndStd | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndStd | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | W-Boiler_AF-lt300k-0.94-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
909 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndLow | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndLow | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, OA reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | W-Boiler_AF-lt300k-0.94-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
910 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndReset | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, load reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-lt300kBtuh-94p0AFUE-CndReset | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_AF |  |  | HVAC-Blr | Hot water boiler,< 300 kBtuh; Pre-2005: 80.0 Et, No reset 2006 - 2009: 80.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 80.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 82.0 Et, OA Reset from 140 to 165 F | Hot water boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | Hot water boiler (< 300 kBtuh, 94.0 AFUE, condensing, load reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | W-Boiler_AF-lt300k-0.94-fDraft | W-Boiler_AF-lt300k-0.82-fDraft
911 | NG-HVAC-Blr-HW-300to2500kBtuh-83p0Et-Drft | Hot water boiler (300 - 2500 kBtuh, 83.0 Et, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-83p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.83-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 83.0 Et, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -422 | 17.6 | 34778 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-83p0Et-Drft | 9 | #N/A | W-Boiler_Et-300to2500k-0.83-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
912 | NG-HVAC-Blr-HW-300to2500kBtuh-85p0Et-Drft | Hot water boiler (300 - 2500 kBtuh, 85.0 Et, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-85p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.85-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 85.0 Et, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 12721 | 17.6 | 47921 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-85p0Et-Drft | 10 | #N/A | W-Boiler_Et-300to2500k-0.85-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
913 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndStd | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndStd | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.9-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -598 | 12.83 | 25062 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndStd | 12 | #N/A | W-Boiler_Et-300to2500k-0.9-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
914 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndLow | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndLow | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.9-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -598 | 12.83 | 25062 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndLow | 12 | #N/A | W-Boiler_Et-300to2500k-0.9-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
915 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndReset | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndReset | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.9-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -598 | 12.83 | 25062 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-90p0Et-CndReset | 12 | #N/A | W-Boiler_Et-300to2500k-0.9-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
916 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndStd | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndStd | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.94-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 6869 | 12.83 | 32529 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndStd | 11 | #N/A | W-Boiler_Et-300to2500k-0.94-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
917 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndLow | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndLow | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.94-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 6869 | 12.83 | 32529 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndLow | 11 | #N/A | W-Boiler_Et-300to2500k-0.94-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
918 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndReset | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndReset | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-300to2500k-0.94-fDraft |  | HVAC-Blr | Hot water boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (300 - 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | Hot water boiler (300 - 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 6869 | 12.83 | 32529 |  |  |  |  | NG-HVAC-Blr-HW-300to2500kBtuh-94p0Et-CndReset | 11 | #N/A | W-Boiler_Et-300to2500k-0.94-fDraft | W-Boiler_Et-300to2500k-0.8-fDraft
919 | NG-HVAC-Blr-HW-gt2500kBtuh-83p0Et-Drft | Hot water boiler (> 2500 kBtuh, 83.0 Et, 85.0Ec, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-83p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.83-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 83.0 Et, 85.0Ec, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -422 | 17.6 | 34778 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-83p0Et-Drft | 13 | #N/A | W-Boiler_Et-gt2500k-0.83-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
920 | NG-HVAC-Blr-HW-gt2500kBtuh-85p0Et-Drft | Hot water boiler (> 2500 kBtuh, 85.0 Et, 87.0Ec, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-85p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.85-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 85.0 Et, 87.0Ec, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 12721 | 17.6 | 47921 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-85p0Et-Drft | 14 | #N/A | W-Boiler_Et-gt2500k-0.85-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
921 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndStd | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndStd | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.9-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -598 | 12.83 | 25062 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndStd | #N/A | #N/A | W-Boiler_Et-gt2500k-0.9-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
922 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndLow | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndLow | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.9-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, OA reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -598 | 12.83 | 25062 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndLow | #N/A | #N/A | W-Boiler_Et-gt2500k-0.9-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
923 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndReset | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndReset | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.9-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 90.0 Et, condensing, load reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | -598 | 12.83 | 25062 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-90p0Et-CndReset | #N/A | #N/A | W-Boiler_Et-gt2500k-0.9-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
924 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndStd | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndStd | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.94-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 6869 | 12.83 | 32529 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndStd | 15 | #N/A | W-Boiler_Et-gt2500k-0.94-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
925 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndLow | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndLow | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.94-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, OA reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 6869 | 12.83 | 32529 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndLow | 15 | #N/A | W-Boiler_Et-gt2500k-0.94-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
926 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndReset | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndReset | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | WaterHtg_eq | Boiler_Et | W-Boiler_Et-gt2500k-0.94-fDraft |  | HVAC-Blr | Hot water boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Hot water boiler (> 2500 kBtuh, 80.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Hot water boiler (> 2500 kBtuh, 94.0 Et, condensing, load reset from 115 to 140 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 300 | 4000 | 2000 | 6869 | 12.83 | 32529 |  |  |  |  | NG-HVAC-Blr-HW-gt2500kBtuh-94p0Et-CndReset | 15 | #N/A | W-Boiler_Et-gt2500k-0.94-fDraft | W-Boiler_Et-gt2500k-0.8-fDraft
927 | NG-HVAC-Blr-Stm-lt300kBtuh-82p0AFUE-Drft | Steam boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-Stm-lt300kBtuh-82p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_AF |  |  | HVAC-Blr | Steam boiler,< 300 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Steam boiler (< 300 kBtuh, 80.0 AFUE, OA Reset from 140 to 165 F) | Steam boiler (< 300 kBtuh, 82.0 AFUE, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | S-Boiler_AF-lt300k-0.82-fDraft | S-Boiler_AF-lt300k-0.8-fDraft
928 | NG-HVAC-Blr-Stm-lt300kBtuh-83p0AFUE-Drft | Steam boiler (< 300 kBtuh, 83.0 AFUE, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-Stm-lt300kBtuh-83p0AFUE-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_AF |  |  | HVAC-Blr | Steam boiler,< 300 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 80.0 Et, OA Reset from 140 to 165 F | Steam boiler (< 300 kBtuh, 80.0 AFUE, OA Reset from 140 to 165 F) | Steam boiler (< 300 kBtuh, 83.0 AFUE, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | [11 empty] | #N/A | #N/A | S-Boiler_AF-lt300k-0.83-fDraft | S-Boiler_AF-lt300k-0.8-fDraft
929 | NG-HVAC-Blr-Stm-300to2500kBtuh-81p0Et-Drft | Steam boiler (300 - 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-Stm-300to2500kBtuh-81p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et | S-Boiler_Et-300to2500k-0.81-fDraft |  | HVAC-Blr | Steam boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (300 - 2500 kBtuh, 79.0 Et, OA Reset from 140 to 165 F) | Steam boiler (300 - 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 250 | 3190 | 1500 | 2539 | 15.97 | 26494 |  |  |  |  | NG-HVAC-Blr-Stm-300to2500kBtuh-81p0Et-Drft | 1 | #N/A | S-Boiler_Et-300to2500k-0.81-fDraft | S-Boiler_Et-300to2500k-0.79-fDraft
930 | NG-HVAC-Blr-Stm-300to2500kBtuh-82p0Et-Drft | Steam boiler (300 - 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-Stm-300to2500kBtuh-82p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et | S-Boiler_Et-300to2500k-0.82-fDraft |  | HVAC-Blr | Steam boiler,300 - 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (300 - 2500 kBtuh, 79.0 Et, OA Reset from 140 to 165 F) | Steam boiler (300 - 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 250 | 3190 | 1500 | 7544 | 15.97 | 31499 |  |  |  |  | NG-HVAC-Blr-Stm-300to2500kBtuh-82p0Et-Drft | 2 | #N/A | S-Boiler_Et-300to2500k-0.82-fDraft | S-Boiler_Et-300to2500k-0.79-fDraft
931 | NG-HVAC-Blr-Stm-gt2500kBtuh-80p0Et-Drft | Steam boiler (> 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-Stm-gt2500kBtuh-80p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et | S-Boiler_Et-gt2500k-0.8-fDraft |  | HVAC-Blr | Steam boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 79.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Steam boiler (> 2500 kBtuh, 80.0 Et, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 250 | 3190 | 1500 | -2466 | 15.97 | 21489 |  |  |  |  | NG-HVAC-Blr-Stm-gt2500kBtuh-80p0Et-Drft | 5 | #N/A | S-Boiler_Et-gt2500k-0.8-fDraft | S-Boiler_Et-gt2500k-0.79-fDraft
932 | NG-HVAC-Blr-Stm-gt2500kBtuh-81p0Et-Drft | Steam boiler (> 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-Stm-gt2500kBtuh-81p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et | S-Boiler_Et-gt2500k-0.81-fDraft |  | HVAC-Blr | Steam boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 79.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Steam boiler (> 2500 kBtuh, 81.0 Et, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 250 | 3190 | 1500 | 2539 | 15.97 | 26494 |  |  |  |  | NG-HVAC-Blr-Stm-gt2500kBtuh-81p0Et-Drft | 3 | #N/A | S-Boiler_Et-gt2500k-0.81-fDraft | S-Boiler_Et-gt2500k-0.79-fDraft
933 | NG-HVAC-Blr-Stm-gt2500kBtuh-82p0Et-Drft | Steam boiler (> 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) | DEER2016 | D16v2 | 2015-05-15 | NG-HVAC-Blr-Stm-gt2500kBtuh-82p0Et-Drft | DEER | Standard | None | 0 | 0 | None |  | FALSE |  | FALSE | Com | Any | HVAC | SpaceHeat | SteamHtg_eq | Boiler_Et | S-Boiler_Et-gt2500k-0.82-fDraft |  | HVAC-Blr | Steam boiler,> 2500 kBtuh; Pre-2005: 75.0 Et, No reset 2006 - 2009: 75.0 Et, OA Reset from 140 to 165 F 2010 - 2013: 75.0 Et, OA Reset from 140 to 165 F 2014 - 2015: 79.0 Et, OA Reset from 140 to 165 F | Steam boiler (> 2500 kBtuh, 79.0 Et, 82.0Ec, OA Reset from 140 to 165 F) | Steam boiler (> 2500 kBtuh, 82.0 Et, OA Reset from 140 to 165 F) |  |  |  | Proposed |  | FALSE | FALSE |  | ErRobNc | HVAC-Blr |  | None | 2016-01-01 |  | DEER2016 Update (non-Ltg) |  |  |  |  | Standard | 250 | 3190 | 1500 | 7544 | 15.97 | 31499 |  |  |  |  | NG-HVAC-Blr-Stm-gt2500kBtuh-82p0Et-Drft | 4 | #N/A | S-Boiler_Et-gt2500k-0.82-fDraft | S-Boiler_Et-gt2500k-0.79-fDraft
DEER Packaged and Split HVAC Technology Cost Development
8/31/2015
This workbook documents the development of Residential and Commercial Split and Packaged HVAC technology costs and Commercial Boiler technology costs based on the Itron
"Ex Ante Cost Study" (2010-2012_WO017_Ex_Ante_Measure_Cost_Study_-_Final_Report.pdf).
Tab | Description
CostModel Coef | The two tables on this worksheet compile the cost model data from table 3-11 and 3-17 from the Itron report for residential and commercial HVAC technologies,
including the following cost categories:
| ● | spltDXHP | commercial and residential SEER-rated, split system HP
| ● | spltDXAC | commercial and residential SEER-rated, split system AC
| ● | pkgDX<5tons | commercial SEER rated packaged AC, 60,000 kBTU/hr rated capacity or less
| ● | pkgDX>5tons | commercial EER-rated, packaged AC, 65,000 - 240,000 BTU/hr rated capacity
| ● | pkgHP<65k | commercial SEER-rated, packaged HP less than 65,000 BTU/hr rated capacity
| ● | Boiler<300k | commercial hot water boiler less than 300 kBTU/hr rated capacity
| ● | Boiler>300k | commercial hot water boiler greater than 300 kBTU/hr rated capacity
| ● | Boiler-Cond | commercial hot water boiler - condensing
| ● | StmBlr | commercial steam boiler
This table is used to apply the cost model to the applicable HVAC technologies utilized in DEER measures.
pkg Technology | These worksheets take the standard technology export from READI (exante1314 database) and apply the cost model to all applicable technologies.
& | The following steps are taken to determine the technology cost values:
boiler Technology | ● | the cost category (as listed above for various technology types) for each technology is determined.
| ● | out-of-scope technologies are identified; technologies are out of scope based on specific parameter values (efficiency range and capacity range)
as well as overall technology type
| ● | for the boiler technologies, new cost IDs are assigned based on unique costs (reset control scenario not part of boiler costs)
| ● | A constant material cost (i.e. the cost does not vary by number of units) and a per-unit material cost is calculated according to the cost model
MeasureCost | This worksheet formats the cost data into the standard ex ante MeasureCost table format for import into the ex ante database.
Measure | This worksheet takes the standard Measure table export from READI for the relevant DEER measures and assigns the MeasCostID and StdCostID where applicable.
Proposed addition to the ex ante "MeasureCost" table
Many HVAC technologies are defined for a range of capacities; for example, the technology: dxAC-Com-Pkg-135to240kBTUh-EER12.5-2Spd, which has the description:
EER-rated packaged Air Conditioner, Size Range: 135 - 240 kBTU/h, EER = 12.5 (1 spd IEER = 13.8, 2 spd IEER = 15.5), EIR = 0.231, Fan W/CFM = 0.41, two-speed fan, with Econo
This technology has a normalizing unit of "Cap-Tons", or rated tons of cooling capacity, and has a capacity range of 11.5 - 20 tons. Energy savings and costs are defined "per ton" of
installed capacity. Claims that reference this technology specify the total number of tons being claimed; the total energy impacts and measures costs are calculated accordingly.
From the Cost Report, the material cost for the technology is determined using: Total Material cost = $4439.26 + $1150.27 * Cap-Ton (see [pkg Technology] tab for details).
A single material cost cannot be determined for the technology as it is defined. However, multiple cost records can be defined for specific capacity values for this technology.
for example: | 12 ton: | CostID = dxAC-Com-EER12.5-2Spd-12ton |  |  |  |  | material cost / ton = ( $4439.26 + $1150.27 * 12)/12 |  |  |  |  | 1520.2083 | per ton
| 14 ton: | CostID = dxAC-Com-EER12.5-2Spd-14ton |  |  |  |  | material cost / ton = ( $4439.26 + $1150.27 * 14)/14 |  |  |  |  | 1467.36 | per ton
| 20 ton: | CostID = dxAC-Com-EER12.5-2Spd-20ton |  |  |  |  | material cost / ton = ( $4439.26 + $1150.27 * 20)/20 |  |  |  |  | 1372.233 | per ton
Program administrator (PA) implementations for this technology type would likewise need to be defined for each individual capacity rating offered by the program.
In some circumstances, such as if the PA incents only a specific piece of equipment or specific capacity, this may be a reasonable and efficient approach to defining
Implementations and Measure Costs. In other circumstances, however, this requirement may lead to having to define dozens of Implementations for a single technology type,
all of which are derived from the same data.
A relatively simple addition to the cost table, however, allows the cost model data to be utilized across the full range of the technology definition, without the need
to define cost records or Implementation records for individual technology capacities.
The new cost record fields are:
MatlCostConst | a material cost "constant" value; the units are $ per installation, in comparison to the existing MatlCost field, which has units of $/Unit
LaborCostConst | a labor cost "constant" value; the units are $ per installation, in comparison to the existing LaborCost field, which has units of $/Unit
MinUnit | this field defines the minimum number of units that can be claimed for a single installation utilizing this cost record
MaxUnit | this field defines the maximum number of units that can be claimed for a single installation utilizing this cost record
All new fields are optional and default to not being used, but If either the MatlCostConst or LaborCostConst fields are specified, the MinUnit and MaxUnit fields must also be specified.
The basic material cost associated with a claim (i.e. not including locations cost adjustment) is determined as (Number of Installations) * MatlCostConst + (Total Number of Units) * MatlCost,
as opposed to just the (Total Number of Units) * MatlCost.
Claims that reference cost records that use these constant cost values need to claim individual installations of the technology or would need to specify the number
of installations being claimed.
All existing ex ante cost records submitted by PAs are compatible with the proposed augmented cost record format, since all of the previously existing fields retain their definitions
and the new fields default to not being used.
2015-08-13
● | While the code requirement for the thermal efficiency of boilers over 300 kBTU/hr is 0.80, the data collection for the cost report did not
find any units with ratings less than 0.82. As such, costs are not available for the standard replacement boilers over 300 kBTU/hr.
● | The cost model leads to a lower cost for condensing boilers than for lower-efficiency non-condensing boilers.

## NEEPPhaseIIncCost-2011
From NEEP Phase I Incremental Cost Research, completed by Navigant in 2011:
Information finalized by ERS on 3/23/2016
http://www.neep.org/file/1001/download?token=dWXnO1Ys
| Size Range |  | Baseline Unit | CEE Tier I Unit | CEE Tier II Unit
| ≤65,000 BTU/hr | Efficiency | EER = 10.3 | EER = 11.5 | EER = 12
|  | Incremental Cost | 0 | $123/ton | $174/ton
| > 65,000 BTU/hr and ≤ 135,000 Btu/hr | Efficiency | EER = 9.7 | EER = 11.5 | EER = 12
|  | Incremental Cost | 0 | $184/ton | $235/ton

## GraniteState
From Scott Lemire at Granite State Heating and Plumbing on 3/8/2015
Information finalized by ERS on 3/8/2016 |  |  |  |  | Total Cost
Manufacturer | Name | SEER | Description | Model Number | 3 | 4 | 5 | Notes | webpage
Trane/American Standard | Precedent eflex | 19.4-20.1 | ultra-high efficiency | T/YZCXXXE/F |  |  |  | variable speed compressor motor & advanced controls | http://www.trane.com/content/dam/Trane/Commercial/global/products-systems/equipment/unitary/rooftop-systems/precedent-3-to-5-tons-eflex/RTPRC053C-EN_07062015.pdf
Trane/American Standard | Precedent 17 plus | 17.5 | higher efficiency | T/YHCXXXE |  |  |  | variable speed EC fan motor & advanced controls | http://www.trane.com/content/dam/Trane/Commercial/global/products-systems/equipment/unitary/rooftop-systems/precedent-3-to-5-tons-17-plus/RT-PRC048J-EN_07112014.pdf
Trane/American Standard | Precedent | 15 | high efficiency | T/YHCXXX | 3299 | 3799 | 4431 |  | http://www.trane.com/content/dam/Trane/Commercial/global/products-systems/equipment/unitary/rooftop-systems/precedent-3-to-10-tons/RT-PRC023AK-EN_10012015.pdf
Trane/American Standard | Precedent | 14 | standard efficiency | T/YSCXXX | 2999 | 3499 | 3999 |  | http://www.trane.com/content/dam/Trane/Commercial/global/products-systems/equipment/unitary/rooftop-systems/precedent-3-to-10-tons/RT-PRC023AK-EN_10012015.pdf
http://www.trane.com/content/dam/Trane/Commercial/global/products-systems/equipment/unitary/rooftop-systems/precedent-3-to-10-tons/RT-PRC023AK-EN_10012015.pdf
Cost per Ton Refrigeration
|  |  |  | Tons | 3 | 4 | 5
|  |  |  | Efficient RTU ($/ton) | 1099.6667 | 949.75 | 886.2
|  |  |  | Baseline RTU ($/ton) | 999.6667 | 874.75 | 799.8
|  |  |  | Incremental cost ($/ton) | 100 | 75 | 86.4

## CEEAHRICommercialCooling
Consortium for Energy Efficiency (CEE) Commercial Cooling Data
| Source: | https://www.ahridirectory.org/ahridirectory/pages/ac/cee/defaultSearch.aspx
https://www.ahridirectory.org/ahridirectory/pages/ac/cee/defaultSearch.aspx
Lists all SP-A units with SEER ≥17 serving commercial applications:
Lists all units SPY-A with SEER ≥17 serving commercial applications:
Final pull on March 23, 2016
[43 empty] | Max of Capacity95FHigh | Column Labels
[43 empty] | Row Labels | AAON | AMERICAN STANDARD | CARRIER CORPORATION | COLEMAN | DAIKIN | ENERGENCE | EVCON | FRASER - JOHNSTON | LUXAIRE | PREDATOR | SERIES 5 | TRANE | Grand Total
[15 empty] | Max of Capacity95FHigh | Column Labels | [26 empty] | 17.00 | 47000 |  |  |  |  | 60000 | [6 empty] | 60000
[15 empty] | Row Labels | AAON | AMERICAN STANDARD | COLEMAN | DAIKIN | ENERGENCE | EVCON | FRASER - JOHNSTON | LUXAIRE | PREDATOR | SERIES 5 | TRANE | Grand Total | [15 empty] | 17.10 | 49000 |  | 35600 |  |  | 60000 | [6 empty] | 60000
AHRIReferenceNumber | ModelStatus | OEMTradeName | OutdoorUnitOEMName | ModelNumber | IndoorUnitOEMName | CoilModelNumber | FurnaceModelNumber | Capacity95FHigh | EER95F | SEER | ARIType | TierValue | CEEManufacturerType | EnergyStar | 18.00 |  |  | 52000 |  | 35200 | 52000 | 52000 | 52000 | 52000 | 52000 |  | 52000 | AHRIReferenceNumber | ModelStatus | OEMTradeName | OutdoorUnitOEMName | ModelNumber | IndoorUnitOEMName | CoilModelNumber | FurnaceModelNumber | Capacity95FHigh | EER95F | SEER | ARIType | TierValue | CEEManufacturerType | EnergyStar | 17.20 |  | 58500 | 58500 | [8 empty] | 58500 | 58500
4890735 | Active | AAON | AAON, INC. | RQ-002-2-*-GA**-000 |  |  |  | 26200 | 14.75 | 19.15 | SP-A | CEE Tier 2 | OEM | - | 18.10 |  |  | 38000 |  |  | 38000 | 38000 | 38000 | 38000 | 38000 |  | 38000 | 4890734 | Active | AAON | AAON, INC. | RQ-002-2-*-GA**-*** |  |  |  | 26200 | 14.75 | 19.15 | SPY-A | CEE Tier 2 | OEM | - | 17.40 | 50000 | [11 empty] | 50000
4832461 | Active | AAON | AAON, INC. | RQ-002-2-*-HA**-000 |  |  |  | 25400 | 13.40 | 17.10 | SP-A | CEE Tier 2 | OEM | - | 18.20 | 37400 | [10 empty] | 37400 | 4832460 | Active | AAON | AAON, INC. | RQ-002-2-*-HA**-*** |  |  |  | 25400 | 13.40 | 17.10 | SPY-A | CEE Tier 2 | OEM | - | 17.45 | 59000 | [11 empty] | 59000
4890737 | Active | AAON | AAON, INC. | RQ-002-3-*-GA**-000 |  |  |  | 26200 | 14.75 | 19.15 | SP-A | CEE Tier 2 | OEM | - | 18.40 |  | 57000 | [8 empty] | 57000 | 57000 | 4890736 | Active | AAON | AAON, INC. | RQ-002-3-*-GA**-*** |  |  |  | 26200 | 14.75 | 19.15 | SPY-A | CEE Tier 2 | OEM | - | 17.50 |  | 49000 | 47500 | 64000 |  |  | 64000 | 64000 | 64000 | 64000 | 64000 | 49000 | 64000
4832463 | Active | AAON | AAON, INC. | RQ-002-3-*-HA**-000 |  |  |  | 25400 | 13.40 | 17.10 | SP-A | CEE Tier 2 | OEM | - | 18.50 |  | 44500 | [8 empty] | 44500 | 44500 | 4832462 | Active | AAON | AAON, INC. | RQ-002-3-*-HA**-*** |  |  |  | 25400 | 13.40 | 17.10 | SPY-A | CEE Tier 2 | OEM | - | 17.60 | [5 empty] | 49000 | [6 empty] | 49000
4890739 | Active | AAON | AAON, INC. | RQ-002-8-*-GA**-000 |  |  |  | 26200 | 14.75 | 19.15 | SP-A | CEE Tier 2 | OEM | - | 18.55 |  |  |  | 58000 | [7 empty] | 58000 | 4890738 | Active | AAON | AAON, INC. | RQ-002-8-*-GA**-*** |  |  |  | 26200 | 14.75 | 19.15 | SPY-A | CEE Tier 2 | OEM | - | 18.00 |  |  |  | 52000 |  | 35200 | 52000 | 52000 | 52000 | 52000 | 52000 |  | 52000
4832465 | Active | AAON | AAON, INC. | RQ-002-8-*-HA**-000 |  |  |  | 25400 | 13.40 | 17.10 | SP-A | CEE Tier 2 | OEM | - | 19.15 | 26200 | [10 empty] | 26200 | 4832464 | Active | AAON | AAON, INC. | RQ-002-8-*-HA**-*** |  |  |  | 25400 | 13.40 | 17.10 | SPY-A | CEE Tier 2 | OEM | - | 18.05 |  |  |  |  | 58000 | [7 empty] | 58000
4890745 | Active | AAON | AAON, INC. | RQ-003-2-*-GA**-000 |  |  |  | 37400 | 13.85 | 18.20 | SP-A | CEE Tier 2 | OEM | - | 19.40 |  | 44500 | [8 empty] | 44500 | 44500 | 4890744 | Active | AAON | AAON, INC. | RQ-003-2-*-GA**-*** |  |  |  | 37400 | 13.85 | 18.20 | SPY-A | CEE Tier 2 | OEM | - | 18.10 |  |  |  | 38000 |  |  | 38000 | 38000 | 38000 | 38000 | 38000 |  | 38000
4832471 | Active | AAON | AAON, INC. | RQ-003-2-*-HA**-000 |  |  |  | 37000 | 13.50 | 17.10 | SP-A | CEE Tier 2 | OEM | - | 19.50 |  | 35800 | [8 empty] | 35800 | 35800 | 4832470 | Active | AAON | AAON, INC. | RQ-003-2-*-HA**-*** |  |  |  | 37000 | 13.50 | 17.10 | SPY-A | CEE Tier 2 | OEM | - | 18.20 | 37400 | [11 empty] | 37400
4890747 | Active | AAON | AAON, INC. | RQ-003-3-*-GA**-000 |  |  |  | 37400 | 13.85 | 18.20 | SP-A | CEE Tier 2 | OEM | - | 19.60 |  | 59000 | [8 empty] | 59000 | 59000 | 4890746 | Active | AAON | AAON, INC. | RQ-003-3-*-GA**-*** |  |  |  | 37400 | 13.85 | 18.20 | SPY-A | CEE Tier 2 | OEM | - | 18.40 |  | 57000 | [9 empty] | 57000 | 57000
4832473 | Active | AAON | AAON, INC. | RQ-003-3-*-HA**-000 |  |  |  | 37000 | 13.50 | 17.10 | SP-A | CEE Tier 2 | OEM | - | 20.10 |  | 35800 | [8 empty] | 35800 | 35800 | 4832472 | Active | AAON | AAON, INC. | RQ-003-3-*-HA**-*** |  |  |  | 37000 | 13.50 | 17.10 | SPY-A | CEE Tier 2 | OEM | - | 18.50 |  | 44500 | [9 empty] | 44500 | 44500
4890749 | Active | AAON | AAON, INC. | RQ-003-4-*-GA**-000 |  |  |  | 37400 | 13.85 | 18.20 | SP-A | CEE Tier 2 | OEM | - | Grand Total | 37400 | 59000 | 52000 | 58000 | 35200 | 52000 | 52000 | 52000 | 52000 | 52000 | 59000 | 59000 | 4890748 | Active | AAON | AAON, INC. | RQ-003-4-*-GA**-*** |  |  |  | 37400 | 13.85 | 18.20 | SPY-A | CEE Tier 2 | OEM | - | 19.15 | 26200 | [11 empty] | 26200
4832475 | Active | AAON | AAON, INC. | RQ-003-4-*-HA**-000 |  |  |  | 37000 | 13.50 | 17.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4832474 | Active | AAON | AAON, INC. | RQ-003-4-*-HA**-*** |  |  |  | 37000 | 13.50 | 17.10 | SPY-A | CEE Tier 2 | OEM | - | 19.40 |  | 44500 | [9 empty] | 44500 | 44500
4890751 | Active | AAON | AAON, INC. | RQ-003-8-*-GA**-000 |  |  |  | 37400 | 13.85 | 18.20 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4890750 | Active | AAON | AAON, INC. | RQ-003-8-*-GA**-*** |  |  |  | 37400 | 13.85 | 18.20 | SPY-A | CEE Tier 2 | OEM | - | 19.50 |  | 35800 | [9 empty] | 35800 | 35800
4832477 | Active | AAON | AAON, INC. | RQ-003-8-*-HA**-000 |  |  |  | 37000 | 13.50 | 17.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4832476 | Active | AAON | AAON, INC. | RQ-003-8-*-HA**-*** |  |  |  | 37000 | 13.50 | 17.10 | SPY-A | CEE Tier 2 | OEM | - | 19.60 |  | 59000 | [9 empty] | 59000 | 59000
4832493 | Active | AAON | AAON, INC. | RQ-004-2-*-GA**-000 |  |  |  | 49000 | 13.30 | 17.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4832492 | Active | AAON | AAON, INC. | RQ-004-2-*-GA**-*** |  |  |  | 49000 | 13.30 | 17.10 | SPY-A | CEE Tier 2 | OEM | - | 20.10 |  | 35800 | [9 empty] | 35800 | 35800
4832505 | Active | AAON | AAON, INC. | RQ-004-2-*-GB**-000 |  |  |  | 50000 | 13.60 | 17.40 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4832504 | Active | AAON | AAON, INC. | RQ-004-2-*-GB**-*** |  |  |  | 50000 | 13.60 | 17.40 | SPY-A | CEE Tier 2 | OEM | - | Grand Total | 59000 | 59000 | 58500 | 64000 | 58000 | 60000 | 64000 | 64000 | 64000 | 64000 | 64000 | 59000 | 64000
7164977 | Active | AAON | AAON, INC. | RQ-004-2-*-HB**-000 |  |  |  | 47000 | 13.00 | 17.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7164976 | Active | AAON | AAON, INC. | RQ-004-2-*-HB**-*** |  |  |  | 47000 | 13.00 | 17.00 | SPY-A | CEE Tier 2 | OEM | -
4832495 | Active | AAON | AAON, INC. | RQ-004-3-*-GA**-000 |  |  |  | 49000 | 13.30 | 17.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4832494 | Active | AAON | AAON, INC. | RQ-004-3-*-GA**-*** |  |  |  | 49000 | 13.30 | 17.10 | SPY-A | CEE Tier 2 | OEM | -
4832507 | Active | AAON | AAON, INC. | RQ-004-3-*-GB**-000 |  |  |  | 50000 | 13.60 | 17.40 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4832506 | Active | AAON | AAON, INC. | RQ-004-3-*-GB**-*** |  |  |  | 50000 | 13.60 | 17.40 | SPY-A | CEE Tier 2 | OEM | -
7164979 | Active | AAON | AAON, INC. | RQ-004-3-*-HB**-000 |  |  |  | 47000 | 13.00 | 17.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7164978 | Active | AAON | AAON, INC. | RQ-004-3-*-HB**-*** |  |  |  | 47000 | 13.00 | 17.00 | SPY-A | CEE Tier 2 | OEM | -
4832497 | Active | AAON | AAON, INC. | RQ-004-4-*-GA**-000 |  |  |  | 49000 | 13.30 | 17.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4832496 | Active | AAON | AAON, INC. | RQ-004-4-*-GA**-*** |  |  |  | 49000 | 13.30 | 17.10 | SPY-A | CEE Tier 2 | OEM | -
4832509 | Active | AAON | AAON, INC. | RQ-004-4-*-GB**-000 |  |  |  | 50000 | 13.60 | 17.40 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4832508 | Active | AAON | AAON, INC. | RQ-004-4-*-GB**-*** |  |  |  | 50000 | 13.60 | 17.40 | SPY-A | CEE Tier 2 | OEM | -
7164981 | Active | AAON | AAON, INC. | RQ-004-4-*-HB**-000 |  |  |  | 47000 | 13.00 | 17.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7164980 | Active | AAON | AAON, INC. | RQ-004-4-*-HB**-*** |  |  |  | 47000 | 13.00 | 17.00 | SPY-A | CEE Tier 2 | OEM | -
4832499 | Active | AAON | AAON, INC. | RQ-004-8-*-GA**-000 |  |  |  | 49000 | 13.30 | 17.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4832498 | Active | AAON | AAON, INC. | RQ-004-8-*-GA**-*** |  |  |  | 49000 | 13.30 | 17.10 | SPY-A | CEE Tier 2 | OEM | -
4832511 | Active | AAON | AAON, INC. | RQ-004-8-*-GB**-000 |  |  |  | 50000 | 13.60 | 17.40 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4832510 | Active | AAON | AAON, INC. | RQ-004-8-*-GB**-*** |  |  |  | 50000 | 13.60 | 17.40 | SPY-A | CEE Tier 2 | OEM | -
7164983 | Active | AAON | AAON, INC. | RQ-004-8-*-HB**-000 |  |  |  | 47000 | 13.00 | 17.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7164982 | Active | AAON | AAON, INC. | RQ-004-8-*-HB**-*** |  |  |  | 47000 | 13.00 | 17.00 | SPY-A | CEE Tier 2 | OEM | -
4832549 | Active | AAON | AAON, INC. | RQ-005-2-*-GB**-000 |  |  |  | 59000 | 13.70 | 17.45 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4832548 | Active | AAON | AAON, INC. | RQ-005-2-*-GB**-*** |  |  |  | 59000 | 13.70 | 17.45 | SPY-A | CEE Tier 2 | OEM | -
4832551 | Active | AAON | AAON, INC. | RQ-005-3-*-GB**-000 |  |  |  | 59000 | 13.70 | 17.45 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4832550 | Active | AAON | AAON, INC. | RQ-005-3-*-GB**-*** |  |  |  | 59000 | 13.70 | 17.45 | SPY-A | CEE Tier 2 | OEM | -
4832553 | Active | AAON | AAON, INC. | RQ-005-4-*-GB**-000 |  |  |  | 59000 | 13.70 | 17.45 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4832552 | Active | AAON | AAON, INC. | RQ-005-4-*-GB**-*** |  |  |  | 59000 | 13.70 | 17.45 | SPY-A | CEE Tier 2 | OEM | -
4832555 | Active | AAON | AAON, INC. | RQ-005-8-*-GB**-000 |  |  |  | 59000 | 13.70 | 17.45 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 4832554 | Active | AAON | AAON, INC. | RQ-005-8-*-GB**-*** |  |  |  | 59000 | 13.70 | 17.45 | SPY-A | CEE Tier 2 | OEM | -
6809730 | Active | AMERICAN STANDARD | AMERICAN STANDARD | THC037E3*(B,E,G)A |  |  |  | 36000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809731 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YHC037E3*(L,M,H,X,Y,Z)A |  |  |  | 36000 | 13.00 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
4661511 | Active | AMERICAN STANDARD | AMERICAN STANDARD | THC037E3*0A |  |  |  | 36000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809733 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YHC037E4*(L,M,H,X,Y,Z)A |  |  |  | 36000 | 13.00 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6809732 | Active | AMERICAN STANDARD | AMERICAN STANDARD | THC037E4*(B,E,G)A |  |  |  | 36000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809734 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YHC037EW*(L,M,H,X,Y,Z)A |  |  |  | 36000 | 13.00 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
4661513 | Active | AMERICAN STANDARD | AMERICAN STANDARD | THC037E4*0A |  |  |  | 36000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809736 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YHC047E3*(L,M,H,X,Y,Z)A |  |  |  | 49000 | 13.00 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6809735 | Active | AMERICAN STANDARD | AMERICAN STANDARD | THC047E3*(B,E,G)A |  |  |  | 49000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809738 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YHC047E4*(L,M,H,X,Y,Z)A |  |  |  | 49000 | 13.00 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
4661515 | Active | AMERICAN STANDARD | AMERICAN STANDARD | THC047E3*0A |  |  |  | 49000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809739 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YHC047EW*(L,M,H,X,Y,Z)A |  |  |  | 49000 | 13.00 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6809737 | Active | AMERICAN STANDARD | AMERICAN STANDARD | THC047E4*(B,E,G)A |  |  |  | 49000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809741 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YHC067E3*(L,M,H,X,Y,Z)A |  |  |  | 58500 | 13.00 | 17.20 | SPY-A | CEE Tier 2 | OEM | -
4661517 | Active | AMERICAN STANDARD | AMERICAN STANDARD | THC047E4*0A |  |  |  | 49000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809743 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YHC067E4*(L,M,H,X,Y,Z)A |  |  |  | 58500 | 13.00 | 17.20 | SPY-A | CEE Tier 2 | OEM | -
6809740 | Active | AMERICAN STANDARD | AMERICAN STANDARD | THC067E3*(B,E,G,J)A |  |  |  | 58500 | 13.00 | 17.20 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809744 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YHC067EW*(L,M,H,X,Y,Z)A |  |  |  | 58500 | 13.00 | 17.20 | SPY-A | CEE Tier 2 | OEM | -
4661519 | Active | AMERICAN STANDARD | AMERICAN STANDARD | THC067E3*0A |  |  |  | 58500 | 13.00 | 17.20 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7191356 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YZC036E3R(L,M,H,X,Y,Z)A |  |  |  | 35800 | 13.00 | 20.10 | SPY-A | CEE Tier 2 | OEM | -
6809742 | Active | AMERICAN STANDARD | AMERICAN STANDARD | THC067E4*(B,E,G,J)A |  |  |  | 58500 | 13.00 | 17.20 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7191431 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YZC036E4R(L,M,H,X,Y,Z)A |  |  |  | 35800 | 12.90 | 19.50 | SPY-A | CEE Tier 2 | OEM | -
4661521 | Active | AMERICAN STANDARD | AMERICAN STANDARD | THC067E4*0A |  |  |  | 58500 | 13.00 | 17.20 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7191524 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YZC048F3R(L,M,H,X,Y,Z)A |  |  |  | 44500 | 13.60 | 19.40 | SPY-A | CEE Tier 2 | OEM | -
7191327 | Active | AMERICAN STANDARD | AMERICAN STANDARD | TZC036E3R(B,E,G)A |  |  |  | 35800 | 13.00 | 20.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7191603 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YZC048F4R(L,M,H,X,Y,Z)A |  |  |  | 44500 | 13.30 | 18.50 | SPY-A | CEE Tier 2 | OEM | -
8192059 | Active | AMERICAN STANDARD | AMERICAN STANDARD | TZC036E3R0A |  |  |  | 35800 | 13.00 | 20.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 8192056 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YZC060E3R(L,M,H,X,Y,Z)A |  |  |  | 59000 | 12.90 | 19.60 | SPY-A | CEE Tier 2 | OEM | -
7191405 | Active | AMERICAN STANDARD | AMERICAN STANDARD | TZC036E4R(B,E,G)A |  |  |  | 35800 | 12.90 | 19.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7191721 | Active | AMERICAN STANDARD | AMERICAN STANDARD | YZC060E4R(L,M,H,X,Y,Z)A |  |  |  | 57000 | 12.50 | 18.40 | SPY-A | CEE Tier 2 | OEM | -
7191383 | Active | AMERICAN STANDARD | AMERICAN STANDARD | TZC036E4R0A |  |  |  | 35800 | 12.90 | 19.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7064316 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LC**04*0*1A***** |  |  |  | 35600 | 12.80 | 17.10 | SPY-A | CEE Tier 2 | OEM | -
7191503 | Active | AMERICAN STANDARD | AMERICAN STANDARD | TZC048F3R(B,E,G)A |  |  |  | 44500 | 13.60 | 19.40 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7064317 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LC**04*0*5A***** |  |  |  | 35600 | 12.80 | 17.10 | SPY-A | CEE Tier 2 | OEM | -
7191484 | Active | AMERICAN STANDARD | AMERICAN STANDARD | TZC048F3R0A |  |  |  | 44500 | 13.60 | 19.40 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7064318 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LC**04*0*6A***** |  |  |  | 35600 | 12.80 | 17.10 | SPY-A | CEE Tier 2 | OEM | -
7191578 | Active | AMERICAN STANDARD | AMERICAN STANDARD | TZC048F4R(B,E,G)A |  |  |  | 44500 | 13.30 | 18.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7064328 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LC**05*0*1A***** |  |  |  | 47500 | 13.10 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
7191562 | Active | AMERICAN STANDARD | AMERICAN STANDARD | TZC048F4R0A |  |  |  | 44500 | 13.30 | 18.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7064329 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LC**05*0*5A***** |  |  |  | 47500 | 13.10 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
8192057 | Active | AMERICAN STANDARD | AMERICAN STANDARD | TZC060E3R(B,E,G,J)A |  |  |  | 59000 | 12.90 | 19.60 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7064330 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LC**05*0*6A***** |  |  |  | 47500 | 13.10 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
8192058 | Active | AMERICAN STANDARD | AMERICAN STANDARD | TZC060E3R0A |  |  |  | 59000 | 12.90 | 19.60 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7064322 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LC**06*0*1A***** |  |  |  | 58500 | 12.70 | 17.20 | SPY-A | CEE Tier 2 | OEM | -
7191699 | Active | AMERICAN STANDARD | AMERICAN STANDARD | TZC060E4R(B,E,G,J)A |  |  |  | 57000 | 12.50 | 18.40 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7064323 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LC**06*0*5A***** |  |  |  | 58500 | 12.70 | 17.20 | SPY-A | CEE Tier 2 | OEM | -
7191625 | Active | AMERICAN STANDARD | AMERICAN STANDARD | TZC060E4R0A |  |  |  | 57000 | 12.50 | 18.40 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7064324 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LC**06*0*6A***** |  |  |  | 58500 | 12.70 | 17.20 | SPY-A | CEE Tier 2 | OEM | -
7064334 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50LC**04*0*1A***** |  |  |  | 35600 | 12.80 | 17.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 8950597 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LCD004E0C1032769 |  |  |  | 35600 | 12.80 | 17.10 | SPY-A | CEE Tier 2 | OEM | -
7064335 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50LC**04*0*5A***** |  |  |  | 35600 | 12.80 | 17.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 8950598 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LCD004E0C1032770 |  |  |  | 35600 | 12.80 | 17.10 | SPY-A | CEE Tier 2 | OEM | -
7064336 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50LC**04*0*6A***** |  |  |  | 35600 | 12.80 | 17.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 8950599 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LCD004E0C1032771 |  |  |  | 35600 | 12.80 | 17.10 | SPY-A | CEE Tier 2 | OEM | -
7064346 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50LC**05*0*1A***** |  |  |  | 47500 | 13.10 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 8950600 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LCD004E0C1032772 |  |  |  | 35600 | 12.80 | 17.10 | SPY-A | CEE Tier 2 | OEM | -
7064347 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50LC**05*0*5A***** |  |  |  | 47500 | 13.10 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 8950595 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LCD004E0C1032773 |  |  |  | 35600 | 12.80 | 17.10 | SPY-A | CEE Tier 2 | OEM | -
7064348 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50LC**05*0*6A***** |  |  |  | 47500 | 13.10 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 8950596 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 48LCE006E0C1032774 |  |  |  | 58500 | 12.70 | 17.20 | SPY-A | CEE Tier 2 | OEM | -
7064340 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50LC**06*0*1A***** |  |  |  | 58500 | 12.70 | 17.20 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488247 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3[A,B,N,S]***T**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
7064341 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50LC**06*0*5A***** |  |  |  | 58500 | 12.70 | 17.20 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488248 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3[A,B,N,S]***W**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
7064342 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50LC**06*0*6A***** |  |  |  | 58500 | 12.70 | 17.20 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488249 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3[A,B,N,S]***X**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488250 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3C***T**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488256 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4[A,B,N,S]***T**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
6488251 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3C***W**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488257 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4[A,B,N,S]***W**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
6488252 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3C***X**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488258 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4[A,B,N,S]***X**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
6488253 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3E***T**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488265 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5[A,B,N,S]***T**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488254 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3E***W**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488266 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5[A,B,N,S]***W**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488255 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3E***X**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488267 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5[A,B,N,S]***X**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488259 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4C***T**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 5319458 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHCE***-4 |  |  |  | 58000 | 12.70 | 18.05 | SPY-A | CEE Tier 2 | OEM | -
6488260 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4C***W**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 5319450 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHCE4**-4 |  |  |  | 58000 | 12.70 | 18.05 | SPY-A | CEE Tier 2 | OEM | -
6488261 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4C***X**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 5319460 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHCG***-4 |  |  |  | 58000 | 12.70 | 18.05 | SPY-A | CEE Tier 2 | OEM | -
6488262 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4E***T**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 5319452 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHCG4**-4 |  |  |  | 58000 | 12.70 | 18.05 | SPY-A | CEE Tier 2 | OEM | -
6488263 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4E***W**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 5319459 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHCW***-4 |  |  |  | 58000 | 12.70 | 18.05 | SPY-A | CEE Tier 2 | OEM | -
6488264 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4E***X**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 5319451 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHCW4**-4 |  |  |  | 58000 | 12.70 | 18.05 | SPY-A | CEE Tier 2 | OEM | -
6488268 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5C***T**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488274 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3[A,B,N,S]***T**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488269 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5C***W**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488275 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3[A,B,N,S]***W**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488270 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5C***X**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488276 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3[A,B,N,S]***X**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488271 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5E***T**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488283 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4[A,B,N,S]***T**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
6488272 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5E***W**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488284 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4[A,B,N,S]***W**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
6488273 | Active | COLEMAN | COLEMAN, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5E***X**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488285 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4[A,B,N,S]***X**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
8656952 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS004AHMY* |  |  |  | 47000 | 12.45 | 17.05 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488292 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5[A,B,N,S]***T**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
8656950 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS004AHMY4 |  |  |  | 47000 | 12.45 | 17.05 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488293 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5[A,B,N,S]***W**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
5319457 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHCY***-4 |  |  |  | 58000 | 13.00 | 18.55 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488294 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5[A,B,N,S]***X**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
5319449 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHCY4**-4 |  |  |  | 58000 | 13.00 | 18.55 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488301 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3[A,B,N,S]***T**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488277 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3C***T**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488302 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3[A,B,N,S]***W**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488278 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3C***W**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488303 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3[A,B,N,S]***X**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488279 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3C***X**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488310 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4[A,B,N,S]***T**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
6488280 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3E***T**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488311 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4[A,B,N,S]***W**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
6488281 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3E***W**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488312 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4[A,B,N,S]***X**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
6488282 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3E***X**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488319 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5[A,B,N,S]***T**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488286 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4C***T**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488320 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5[A,B,N,S]***W**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488287 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4C***W**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488321 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5[A,B,N,S]***X**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488288 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4C***X**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488328 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA3ZT[A,B,N,S]***2**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488289 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4E***T**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488329 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA3ZT[A,B,N,S]***4**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488290 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4E***W**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488330 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA3ZT[A,B,N,S]***5**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488291 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4E***X**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488337 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA4ZT[A,B,N,S]***2**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
6488295 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5C***T**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488338 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA4ZT[A,B,N,S]***4**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
6488296 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5C***W**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488339 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA4ZT[A,B,N,S]***5**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
6488297 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5C***X**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488346 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA5ZT[A,B,N,S]***2**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488298 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5E***T**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488347 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA5ZT[A,B,N,S]***4**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488299 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5E***W**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488348 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA5ZT[A,B,N,S]***5**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488300 | Active | EVCON | EVCON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5E***X**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 3607626 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LGH036H4E**G |  |  |  | 35200 | 12.50 | 17.00 | SPY-A | CEE Tier 2 | OEM | Yes
6488304 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3C***T**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 3607627 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LGH036H4E**J |  |  |  | 35200 | 12.50 | 17.00 | SPY-A | CEE Tier 2 | OEM | Yes
6488305 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3C***W**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 3607625 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LGH036H4E**Y |  |  |  | 35200 | 12.70 | 18.00 | SPY-A | CEE Tier 2 | OEM | Yes
6488306 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3C***X**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 3607637 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LGH048H4E**G |  |  |  | 49000 | 12.80 | 17.00 | SPY-A | CEE Tier 2 | OEM | Yes
6488307 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3E***T**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 3607638 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LGH048H4E**J |  |  |  | 49000 | 12.80 | 17.00 | SPY-A | CEE Tier 2 | OEM | Yes
6488308 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3E***W**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 3607636 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LGH048H4E**Y |  |  |  | 49000 | 12.80 | 17.60 | SPY-A | CEE Tier 2 | OEM | Yes
6488309 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3E***X**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 3607651 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LGH060H4E**G |  |  |  | 60000 | 12.70 | 17.00 | SPY-A | CEE Tier 2 | OEM | Yes
6488313 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4C***T**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 3607652 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LGH060H4E**J |  |  |  | 60000 | 12.70 | 17.00 | SPY-A | CEE Tier 2 | OEM | Yes
6488314 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4C***W**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 3607650 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LGH060H4E**Y |  |  |  | 60000 | 12.70 | 17.10 | SPY-A | CEE Tier 2 | OEM | Yes
6488315 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4C***X**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488355 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3[A,B,N,S]***T**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488316 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4E***T**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488356 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3[A,B,N,S]***W**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488317 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4E***W**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488357 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3[A,B,N,S]***X**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488318 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4E***X**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488364 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4[A,B,N,S]***T**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
6488322 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5C***T**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488365 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4[A,B,N,S]***W**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
6488323 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5C***W**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488366 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4[A,B,N,S]***X**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
6488324 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5C***X**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488373 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5[A,B,N,S]***T**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488325 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5E***T**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488374 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5[A,B,N,S]***W**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488326 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5E***W**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488375 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5[A,B,N,S]***X**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488327 | Active | FRASER - JOHNSTON | FRASER - JOHNSTON, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5E***X**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809713 | Active | TRANE | TRANE | YHC037E3*(L,M,H,X,Y,Z)A |  |  |  | 36000 | 13.00 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488331 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA3ZTC***2**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809715 | Active | TRANE | TRANE | YHC037E4*(L,M,H,X,Y,Z)A |  |  |  | 36000 | 13.00 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488332 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA3ZTC***4**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809716 | Active | TRANE | TRANE | YHC037EW*(L,M,H,X,Y,Z)A |  |  |  | 36000 | 13.00 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488333 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA3ZTC***5**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809718 | Active | TRANE | TRANE | YHC047E3*(L,M,H,X,Y,Z)A |  |  |  | 49000 | 13.00 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488334 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA3ZTE***2**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809720 | Active | TRANE | TRANE | YHC047E4*(L,M,H,X,Y,Z)A |  |  |  | 49000 | 13.00 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488335 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA3ZTE***4**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809721 | Active | TRANE | TRANE | YHC047EW*(L,M,H,X,Y,Z)A |  |  |  | 49000 | 13.00 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
6488336 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA3ZTE***5**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809723 | Active | TRANE | TRANE | YHC067E3*(L,M,H,X,Y,Z)A |  |  |  | 58500 | 13.00 | 17.20 | SPY-A | CEE Tier 2 | OEM | -
6488340 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA4ZTC***2**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809725 | Active | TRANE | TRANE | YHC067E4*(L,M,H,X,Y,Z)A |  |  |  | 58500 | 13.00 | 17.20 | SPY-A | CEE Tier 2 | OEM | -
6488341 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA4ZTC***4**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6809726 | Active | TRANE | TRANE | YHC067EW*(L,M,H,X,Y,Z)A |  |  |  | 58500 | 13.00 | 17.20 | SPY-A | CEE Tier 2 | OEM | -
6488342 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA4ZTC***5**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7189999 | Active | TRANE | TRANE | YZC036E3R(L,M,H,X,Y,Z)A |  |  |  | 35800 | 13.00 | 20.10 | SPY-A | CEE Tier 2 | OEM | -
6488343 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA4ZTE***2**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7190002 | Active | TRANE | TRANE | YZC036E4R(L,M,H,X,Y,Z)A |  |  |  | 35800 | 12.90 | 19.50 | SPY-A | CEE Tier 2 | OEM | -
6488344 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA4ZTE***4**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7190005 | Active | TRANE | TRANE | YZC048F3R(L,M,H,X,Y,Z)A |  |  |  | 44500 | 13.60 | 19.40 | SPY-A | CEE Tier 2 | OEM | -
6488345 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA4ZTE***5**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7190008 | Active | TRANE | TRANE | YZC048F4R(L,M,H,X,Y,Z)A |  |  |  | 44500 | 13.30 | 18.50 | SPY-A | CEE Tier 2 | OEM | -
6488349 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA5ZTC***2**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 8192055 | Active | TRANE | TRANE | YZC060E3R(L,M,H,X,Y,Z)A |  |  |  | 59000 | 12.90 | 19.60 | SPY-A | CEE Tier 2 | OEM | -
6488350 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA5ZTC***4**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 7190011 | Active | TRANE | TRANE | YZC060E4R(L,M,H,X,Y,Z)A |  |  |  | 57000 | 12.50 | 18.40 | SPY-A | CEE Tier 2 | OEM | -
6488351 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA5ZTC***5**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488162 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT037[A,B,N,S]***2**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488352 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA5ZTE***2**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488163 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT037[A,B,N,S]***4**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488353 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA5ZTE***4**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488164 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT037[A,B,N,S]***5**** |  |  |  | 38000 | 14.15 | 18.10 | SPY-A | CEE Tier 2 | OEM | -
6488354 | Active | SERIES 5 | JOHNSON CONTROLS, UNITARY PRODUCTS - COMMERCIAL | JA5ZTE***5**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | - | [13 empty] | 6488168 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT049[A,B,N,S]***2**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
3607618 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LCH036H4E**G |  |  |  | 35200 | 12.50 | 17.00 | SP-A | CEE Tier 2 | OEM | Yes | [13 empty] | 6488169 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT049[A,B,N,S]***4**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
3607619 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LCH036H4E**J |  |  |  | 35200 | 12.50 | 17.00 | SP-A | CEE Tier 2 | OEM | Yes | [13 empty] | 6488170 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT049[A,B,N,S]***5**** |  |  |  | 52000 | 14.35 | 18.00 | SPY-A | CEE Tier 2 | OEM | -
3607617 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LCH036H4E**Y |  |  |  | 35200 | 12.70 | 18.00 | SP-A | CEE Tier 2 | OEM | Yes | [13 empty] | 6488174 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT061[A,B,N,S]***2**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
3607634 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LCH048H4E**G |  |  |  | 49000 | 12.80 | 17.00 | SP-A | CEE Tier 2 | OEM | Yes | [13 empty] | 6488175 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT061[A,B,N,S]***4**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
3607659 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LCH048H4E**J |  |  |  | 49000 | 12.80 | 17.00 | SP-A | CEE Tier 2 | OEM | Yes | [13 empty] | 6488176 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT061[A,B,N,S]***5**** |  |  |  | 64000 | 13.85 | 17.50 | SPY-A | CEE Tier 2 | OEM | -
3607633 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LCH048H4E**Y |  |  |  | 49000 | 12.80 | 17.60 | SP-A | CEE Tier 2 | OEM | Yes
3607647 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LCH060H4E**G |  |  |  | 60000 | 12.70 | 17.00 | SP-A | CEE Tier 2 | OEM | Yes
3607648 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LCH060H4E**J |  |  |  | 60000 | 12.70 | 17.00 | SP-A | CEE Tier 2 | OEM | Yes
3607646 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LCH060H4E**Y |  |  |  | 60000 | 12.70 | 17.10 | SP-A | CEE Tier 2 | OEM | Yes
6488358 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3C***T**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | -
6488359 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3C***W**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | -
6488360 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3C***X**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | -
6488361 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3E***T**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | -
6488362 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3E***W**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | -
6488363 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A3E***X**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | -
6488367 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4C***T**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | -
6488368 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4C***W**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | -
6488369 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4C***X**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | -
6488370 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4E***T**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | -
6488371 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4E***W**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | -
6488372 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A4E***X**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | -
6488376 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5C***T**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6488377 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5C***W**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6488378 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5C***X**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6488379 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5E***T**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6488380 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5E***W**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6488381 | Active | LUXAIRE | LUXAIRE, UNITARY PRODUCTS GROUP - COMMERCIAL | ZV-A5E***X**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6809712 | Active | TRANE | TRANE | THC037E3*(B,E,G)A |  |  |  | 36000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | -
4661495 | Active | TRANE | TRANE | THC037E3*0A |  |  |  | 36000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6809714 | Active | TRANE | TRANE | THC037E4*(B,E,G)A |  |  |  | 36000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | -
4661497 | Active | TRANE | TRANE | THC037E4*0A |  |  |  | 36000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6809717 | Active | TRANE | TRANE | THC047E3*(B,E,G)A |  |  |  | 49000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | -
4661499 | Active | TRANE | TRANE | THC047E3*0A |  |  |  | 49000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6809719 | Active | TRANE | TRANE | THC047E4*(B,E,G)A |  |  |  | 49000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | -
4661501 | Active | TRANE | TRANE | THC047E4*0A |  |  |  | 49000 | 13.00 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6809722 | Active | TRANE | TRANE | THC067E3*(B,E,G,J)A |  |  |  | 58500 | 13.00 | 17.20 | SP-A | CEE Tier 2 | OEM | -
4661503 | Active | TRANE | TRANE | THC067E3*0A |  |  |  | 58500 | 13.00 | 17.20 | SP-A | CEE Tier 2 | OEM | -
6809724 | Active | TRANE | TRANE | THC067E4*(B,E,G,J)A |  |  |  | 58500 | 13.00 | 17.20 | SP-A | CEE Tier 2 | OEM | -
4661505 | Active | TRANE | TRANE | THC067E4*0A |  |  |  | 58500 | 13.00 | 17.20 | SP-A | CEE Tier 2 | OEM | -
7189998 | Active | TRANE | TRANE | TZC036E3R(B,E,G)A |  |  |  | 35800 | 13.00 | 20.10 | SP-A | CEE Tier 2 | OEM | -
7189997 | Active | TRANE | TRANE | TZC036E3R0A |  |  |  | 35800 | 13.00 | 20.10 | SP-A | CEE Tier 2 | OEM | -
7190001 | Active | TRANE | TRANE | TZC036E4R(B,E,G)A |  |  |  | 35800 | 12.90 | 19.50 | SP-A | CEE Tier 2 | OEM | -
7190000 | Active | TRANE | TRANE | TZC036E4R0A |  |  |  | 35800 | 12.90 | 19.50 | SP-A | CEE Tier 2 | OEM | -
7190004 | Active | TRANE | TRANE | TZC048F3R(B,E,G)A |  |  |  | 44500 | 13.60 | 19.40 | SP-A | CEE Tier 2 | OEM | -
7190003 | Active | TRANE | TRANE | TZC048F3R0A |  |  |  | 44500 | 13.60 | 19.40 | SP-A | CEE Tier 2 | OEM | -
7190007 | Active | TRANE | TRANE | TZC048F4R(B,E,G)A |  |  |  | 44500 | 13.30 | 18.50 | SP-A | CEE Tier 2 | OEM | -
7190006 | Active | TRANE | TRANE | TZC048F4R0A |  |  |  | 44500 | 13.30 | 18.50 | SP-A | CEE Tier 2 | OEM | -
8192054 | Active | TRANE | TRANE | TZC060E3R(B,E,G,J)A |  |  |  | 59000 | 12.90 | 19.60 | SP-A | CEE Tier 2 | OEM | -
8192053 | Active | TRANE | TRANE | TZC060E3R0A |  |  |  | 59000 | 12.90 | 19.60 | SP-A | CEE Tier 2 | OEM | -
7190010 | Active | TRANE | TRANE | TZC060E4R(B,E,G,J)A |  |  |  | 57000 | 12.50 | 18.40 | SP-A | CEE Tier 2 | OEM | -
7190009 | Active | TRANE | TRANE | TZC060E4R0A |  |  |  | 57000 | 12.50 | 18.40 | SP-A | CEE Tier 2 | OEM | -
6488165 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT037C00*2**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | -
6488166 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT037C00*4**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | -
6488167 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT037C00*5**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | -
6488180 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT037E***2**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | -
6488181 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT037E***4**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | -
6488182 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT037E***5**** |  |  |  | 38000 | 14.15 | 18.10 | SP-A | CEE Tier 2 | OEM | -
6488171 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT049C00*2**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | -
6488172 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT049C00*4**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | -
6488173 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT049C00*5**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | -
6488183 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT049E***2**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | -
6488184 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT049E***4**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | -
6488185 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT049E***5**** |  |  |  | 52000 | 14.35 | 18.00 | SP-A | CEE Tier 2 | OEM | -
6488177 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT061C00*2**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6488178 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT061C00*4**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6488179 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT061C00*5**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6488186 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT061E***2**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6488187 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT061E***4**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | -
6488188 | Active | PREDATOR | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | ZT061E***5**** |  |  |  | 64000 | 13.85 | 17.50 | SP-A | CEE Tier 2 | OEM | -

## CEEAHRICommercialHPs
Consortium for Energy Effiency Efficiency (CEE) AHRI Commercial Heat Pump Data
Final pull on March 23, 2016
AHRIReferenceNumber | ModelStatus | OEMTradeName | OutdoorUnitOEMName | ModelNumber | IndoorUnitOEMName | CoilModelNumber | FurnaceModelNumber | Capacity95FHigh | EER95F | SEER | HighHeat47F | HSPF | LowHeat17F | ARIType | TierValue | CEEManufacturerType | EnergyStar
6345796 | Active | AIRQUEST | AIRQUEST | PHR542***H***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | - | Max of Capacity95FHigh | Column Labels
6345798 | Active | AIRQUEST | AIRQUEST | PHR548***H***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | - | Row Labels | AIRQUEST | AIRQUEST; ARCOAIRE; COMFORTMAKER; DAY & NIGHT; HEIL; ICP COMMERCIAL; KEEPRITE; TEMPSTAR | AMERICAN STANDARD | ARCOAIRE | BRYANT | BRYANT HEATING & COOLING SYSTEMS | CARRIER | CARRIER CORPORATION | COMFORTMAKER | DAIKIN | DAY & NIGHT | HEIL | KEEPRITE | KENMORE | TEMPSTAR | TRANE | Grand Total
6345800 | Active | AIRQUEST | AIRQUEST | PHR560***H***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | - | 15.00 | 57000 | 58500 |  | 57000 | 57000 | 58500 | 57000 | 58500 | 57000 |  | 57000 | 57000 | 57000 | 57000 | 57000 |  | 58500
7180051 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4DCZ6036B3 |  |  |  | 36000 | 12.20 | 16.00 | 31000 | 8.30 | 19200 | HSP-A | CEE Tier 2 | OEM | - | 15.50 | 47500 |  |  | 47500 | 47500 |  | 47500 |  | 47500 |  | 47500 | 47500 | 47500 | 47500 | 47500 |  | 47500
7180056 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4DCZ6048B3 |  |  |  | 47500 | 12.00 | 16.00 | 42000 | 8.50 | 23200 | HSP-A | CEE Tier 2 | OEM | - | 15.80 |  | 47000 |  |  |  | 47000 |  | 47000 | [8 empty] | 47000
1505064 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCZ6036A3 |  |  |  | 36000 | 12.20 | 16.40 | 34000 | 9.00 | 20800 | HSP-A | CEE Tier 2 | OEM | - | 16.00 |  |  | 47500 | [12 empty] | 47500 | 47500
1505066 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCZ6036A4 |  |  |  | 36000 | 12.20 | 16.40 | 34000 | 9.00 | 20800 | HSP-A | CEE Tier 2 | OEM | - | 16.10 | [9 empty] | 34400 | [6 empty] | 34400
7180049 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCZ6036B3 |  |  |  | 36000 | 12.20 | 16.00 | 31000 | 8.30 | 19200 | HSP-A | CEE Tier 2 | OEM | - | 16.40 |  |  | 36000 | [12 empty] | 36000 | 36000
7180050 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCZ6036B4 |  |  |  | 36000 | 12.20 | 16.00 | 31000 | 8.30 | 19200 | HSP-A | CEE Tier 2 | OEM | - | 16.50 | [9 empty] | 34400 | [6 empty] | 34400
1505074 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCZ6048A3 |  |  |  | 47500 | 12.00 | 16.00 | 44500 | 9.00 | 27000 | HSP-A | CEE Tier 2 | OEM | - | 16.60 | [9 empty] | 46000 | [6 empty] | 46000
1505076 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCZ6048A4 |  |  |  | 47500 | 12.00 | 16.00 | 44500 | 9.00 | 27000 | HSP-A | CEE Tier 2 | OEM | - | 17.60 | [9 empty] | 57000 | [6 empty] | 57000
7180054 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCZ6048B3 |  |  |  | 47500 | 12.00 | 16.00 | 42000 | 8.50 | 23200 | HSP-A | CEE Tier 2 | OEM | - | 18.05 | [9 empty] | 57000 | [6 empty] | 57000
7180055 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCZ6048B4 |  |  |  | 47500 | 12.00 | 16.00 | 42000 | 8.50 | 23200 | HSP-A | CEE Tier 2 | OEM | - | Grand Total | 57000 | 58500 | 47500 | 57000 | 57000 | 58500 | 57000 | 58500 | 57000 | 57000 | 57000 | 57000 | 57000 | 57000 | 57000 | 47500 | 58500
6345807 | Active | ARCOAIRE | ARCOAIRE | PHR542***H***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345809 | Active | ARCOAIRE | ARCOAIRE | PHR548***H***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | - | Max of Capacity95FHigh | Column Labels
6345811 | Active | ARCOAIRE | ARCOAIRE | PHR560***H***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | - | Row Labels | AIRQUEST | AIRQUEST; ARCOAIRE; COMFORTMAKER; DAY & NIGHT; HEIL; ICP COMMERCIAL; KEEPRITE; TEMPSTAR | AMERICAN STANDARD | ARCOAIRE | BRYANT | BRYANT HEATING & COOLING SYSTEMS | CARRIER | CARRIER CORPORATION | COMFORTMAKER | DAIKIN | DAY & NIGHT | HEIL | KEEPRITE | KENMORE | TEMPSTAR | TRANE | Grand Total
4935348 | Active | BRYANT HEATING & COOLING SYSTEMS | BRYANT HEATING & COOLING SYSTEMS | 549JE05**********A |  |  |  | 47000 | 12.80 | 15.80 | 46000 | 8.20 | 23800 | HSP-A | CEE Tier 1 | OEM | Yes | 8.20 | 47500 | 58500 |  | 47500 | 47500 | 58500 | 47500 | 58500 | 47500 |  | 47500 | 47500 | 47500 | 47500 | 47500 |  | 58500
4935384 | Active | BRYANT HEATING & COOLING SYSTEMS | BRYANT HEATING & COOLING SYSTEMS | 549JE06**********A |  |  |  | 58500 | 12.50 | 15.00 | 55000 | 8.20 | 28600 | HSP-A | CEE Tier 1 | OEM | Yes | 8.30 |  |  | 36000 | [12 empty] | 36000 | 36000
4935347 | Active | BRYANT HEATING & COOLING SYSTEMS | BRYANT HEATING & COOLING SYSTEMS | 549JP05**********A |  |  |  | 47000 | 12.80 | 15.80 | 46000 | 8.20 | 23800 | HSP-A | CEE Tier 1 | OEM | Yes | 8.40 | [9 empty] | 57000 | [6 empty] | 57000
4935383 | Active | BRYANT HEATING & COOLING SYSTEMS | BRYANT HEATING & COOLING SYSTEMS | 549JP06**********A |  |  |  | 58500 | 12.50 | 15.00 | 55000 | 8.20 | 28600 | HSP-A | CEE Tier 1 | OEM | Yes | 8.50 | 57000 |  | 47500 | 57000 | 57000 |  | 57000 |  | 57000 | 57000 | 57000 | 57000 | 57000 | 57000 | 57000 | 47500 | 57000
4935345 | Active | BRYANT HEATING & COOLING SYSTEMS | BRYANT HEATING & COOLING SYSTEMS | 549JT05**********A |  |  |  | 47000 | 12.80 | 15.80 | 46000 | 8.20 | 23800 | HSP-A | CEE Tier 1 | OEM | Yes | 8.90 | [9 empty] | 46000 | [6 empty] | 46000
4935381 | Active | BRYANT HEATING & COOLING SYSTEMS | BRYANT HEATING & COOLING SYSTEMS | 549JT06**********A |  |  |  | 58500 | 12.50 | 15.00 | 55000 | 8.20 | 28600 | HSP-A | CEE Tier 1 | OEM | Yes | 9.00 |  |  | 47500 | [12 empty] | 47500 | 47500
6345772 | Active | BRYANT | BRYANT HEATING AND COOLING SYSTEMS | 607EEXA42****A |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | - | 9.10 | [9 empty] | 34400 | [6 empty] | 34400
6345775 | Active | BRYANT | BRYANT HEATING AND COOLING SYSTEMS | 607EEXA48****A |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | - | 9.20 | [9 empty] | 34400 | [6 empty] | 34400
6345778 | Active | BRYANT | BRYANT HEATING AND COOLING SYSTEMS | 607EEXA60****A |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | - | Grand Total | 57000 | 58500 | 47500 | 57000 | 57000 | 58500 | 57000 | 58500 | 57000 | 57000 | 57000 | 57000 | 57000 | 57000 | 57000 | 47500 | 58500
6345771 | Active | BRYANT | BRYANT HEATING AND COOLING SYSTEMS | 607EPXA42****A |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345774 | Active | BRYANT | BRYANT HEATING AND COOLING SYSTEMS | 607EPXA48****A |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345777 | Active | BRYANT | BRYANT HEATING AND COOLING SYSTEMS | 607EPXA60****A |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
6345759 | Active | BRYANT | BRYANT HEATING AND COOLING SYSTEMS | 677EPWA42****A |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345761 | Active | BRYANT | BRYANT HEATING AND COOLING SYSTEMS | 677EPWA48****A |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345763 | Active | BRYANT | BRYANT HEATING AND COOLING SYSTEMS | 677EPWA60****A |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
6335194 | Active | CARRIER | CARRIER AIR CONDITIONING | 48VR*A42***50 |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6335196 | Active | CARRIER | CARRIER AIR CONDITIONING | 48VR*A48***50 |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6335198 | Active | CARRIER | CARRIER AIR CONDITIONING | 48VR*A60***50 |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
6335180 | Active | CARRIER | CARRIER AIR CONDITIONING | 50VR*A42***50 |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6335181 | Active | CARRIER | CARRIER AIR CONDITIONING | 50VR*A42***60 |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6335183 | Active | CARRIER | CARRIER AIR CONDITIONING | 50VR*A48***50 |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6335184 | Active | CARRIER | CARRIER AIR CONDITIONING | 50VR*A48***60 |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6335186 | Active | CARRIER | CARRIER AIR CONDITIONING | 50VR*A60***50 |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
6335187 | Active | CARRIER | CARRIER AIR CONDITIONING | 50VR*A60***60 |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
4890852 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50HCQ*05***1A* |  |  |  | 47000 | 12.80 | 15.80 | 46000 | 8.20 | 23800 | HSP-A | CEE Tier 1 | OEM | Yes
4890850 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50HCQ*05***5A* |  |  |  | 47000 | 12.80 | 15.80 | 46000 | 8.20 | 23800 | HSP-A | CEE Tier 1 | OEM | Yes
4890851 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50HCQ*05***6A* |  |  |  | 47000 | 12.80 | 15.80 | 46000 | 8.20 | 23800 | HSP-A | CEE Tier 1 | OEM | Yes
4890856 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50HCQ*06***1A* |  |  |  | 58500 | 12.50 | 15.00 | 55000 | 8.20 | 28600 | HSP-A | CEE Tier 1 | OEM | Yes
4890854 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50HCQ*06***5A* |  |  |  | 58500 | 12.50 | 15.00 | 55000 | 8.20 | 28600 | HSP-A | CEE Tier 1 | OEM | Yes
4890855 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50HCQ*06***6A* |  |  |  | 58500 | 12.50 | 15.00 | 55000 | 8.20 | 28600 | HSP-A | CEE Tier 1 | OEM | Yes
6345818 | Active | COMFORTMAKER | COMFORTMAKER | PHR542***H***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345820 | Active | COMFORTMAKER | COMFORTMAKER | PHR548***H***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345822 | Active | COMFORTMAKER | COMFORTMAKER | PHR560***H***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
5376633 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS003AHHE***-3 |  |  |  | 34400 | 12.85 | 16.10 | 30000 | 9.10 | 20400 | HSP-A | CEE Tier 2 | OEM | -
6721804 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS003AHHE4**-3 |  |  |  | 34400 | 12.85 | 16.10 | 34000 | 9.10 | 20400 | HSP-A | CEE Tier 2 | OEM | -
5376635 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS003AHHG***-3 |  |  |  | 34400 | 12.85 | 16.10 | 30000 | 9.10 | 20400 | HSP-A | CEE Tier 2 | OEM | -
6721808 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS003AHHG4**-3 |  |  |  | 34400 | 12.85 | 16.10 | 34000 | 9.10 | 20400 | HSP-A | CEE Tier 2 | OEM | -
5376634 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS003AHHW***-3 |  |  |  | 34400 | 12.85 | 16.10 | 30000 | 9.10 | 20400 | HSP-A | CEE Tier 2 | OEM | -
6721806 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS003AHHW4**-3 |  |  |  | 34400 | 12.85 | 16.10 | 34000 | 9.10 | 20400 | HSP-A | CEE Tier 2 | OEM | -
5376632 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS003AHHY***-3 |  |  |  | 34400 | 13.15 | 16.50 | 30000 | 9.20 | 20400 | HSP-A | CEE Tier 2 | OEM | -
6721802 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS003AHHY4**-3 |  |  |  | 34400 | 13.15 | 16.50 | 34000 | 9.20 | 20400 | HSP-A | CEE Tier 2 | OEM | -
5376643 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS004AHHY***-4 |  |  |  | 46000 | 12.10 | 16.60 | 43000 | 8.90 | 24200 | HSP-A | CEE Tier 2 | OEM | -
6721818 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS004AHHY4**-4 |  |  |  | 46000 | 12.10 | 16.60 | 43000 | 8.90 | 24200 | HSP-A | CEE Tier 2 | OEM | -
5319467 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHHE***-4 |  |  |  | 57000 | 12.35 | 17.60 | 53500 | 8.40 | 33000 | HSP-A | CEE Tier 2 | OEM | -
5319475 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHHE4**-4 |  |  |  | 57000 | 12.35 | 17.60 | 53500 | 8.40 | 33000 | HSP-A | CEE Tier 2 | OEM | -
5319469 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHHG***-4 |  |  |  | 57000 | 12.35 | 17.60 | 53500 | 8.40 | 33000 | HSP-A | CEE Tier 2 | OEM | -
5319477 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHHG4**-4 |  |  |  | 57000 | 12.35 | 17.60 | 53500 | 8.40 | 33000 | HSP-A | CEE Tier 2 | OEM | -
5319468 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHHW***-4 |  |  |  | 57000 | 12.35 | 17.60 | 53500 | 8.40 | 33000 | HSP-A | CEE Tier 2 | OEM | -
5319476 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHHW4**-4 |  |  |  | 57000 | 12.35 | 17.60 | 53500 | 8.40 | 33000 | HSP-A | CEE Tier 2 | OEM | -
5319466 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHHY***-4 |  |  |  | 57000 | 12.65 | 18.05 | 53500 | 8.50 | 33000 | HSP-A | CEE Tier 2 | OEM | -
5319474 | Active | DAIKIN | DAIKIN APPLIED AMERICAS INC. | DPS005AHHY4**-4 |  |  |  | 57000 | 12.65 | 18.05 | 53500 | 8.50 | 33000 | HSP-A | CEE Tier 2 | OEM | -
6345829 | Active | DAY & NIGHT | DAY & NIGHT | PHR542***H***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345831 | Active | DAY & NIGHT | DAY & NIGHT | PHR548***H***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345833 | Active | DAY & NIGHT | DAY & NIGHT | PHR560***H***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
6345785 | Active | HEIL | HEIL | PHR542***H***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345787 | Active | HEIL | HEIL | PHR548***H***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345789 | Active | HEIL | HEIL | PHR560***H***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
4935367 | Active | AIRQUEST; ARCOAIRE; COMFORTMAKER; DAY & NIGHT; HEIL; ICP COMMERCIAL; KEEPRITE; TEMPSTAR | INTERNATIONAL COMFORT PRODUCTS | RHH048H******** |  |  |  | 47000 | 12.80 | 15.80 | 46000 | 8.20 | 23800 | HSP-A | CEE Tier 1 | OEM | Yes
4935368 | Active | AIRQUEST; ARCOAIRE; COMFORTMAKER; DAY & NIGHT; HEIL; ICP COMMERCIAL; KEEPRITE; TEMPSTAR | INTERNATIONAL COMFORT PRODUCTS | RHH048L******** |  |  |  | 47000 | 12.80 | 15.80 | 46000 | 8.20 | 23800 | HSP-A | CEE Tier 1 | OEM | Yes
4935365 | Active | AIRQUEST; ARCOAIRE; COMFORTMAKER; DAY & NIGHT; HEIL; ICP COMMERCIAL; KEEPRITE; TEMPSTAR | INTERNATIONAL COMFORT PRODUCTS | RHH048S******** |  |  |  | 47000 | 12.80 | 15.80 | 46000 | 8.20 | 23800 | HSP-A | CEE Tier 1 | OEM | Yes
4935403 | Active | AIRQUEST; ARCOAIRE; COMFORTMAKER; DAY & NIGHT; HEIL; ICP COMMERCIAL; KEEPRITE; TEMPSTAR | INTERNATIONAL COMFORT PRODUCTS | RHH060H******** |  |  |  | 58500 | 12.50 | 15.00 | 55000 | 8.20 | 28600 | HSP-A | CEE Tier 1 | OEM | Yes
4935404 | Active | AIRQUEST; ARCOAIRE; COMFORTMAKER; DAY & NIGHT; HEIL; ICP COMMERCIAL; KEEPRITE; TEMPSTAR | INTERNATIONAL COMFORT PRODUCTS | RHH060L******** |  |  |  | 58500 | 12.50 | 15.00 | 55000 | 8.20 | 28600 | HSP-A | CEE Tier 1 | OEM | Yes
4935401 | Active | AIRQUEST; ARCOAIRE; COMFORTMAKER; DAY & NIGHT; HEIL; ICP COMMERCIAL; KEEPRITE; TEMPSTAR | INTERNATIONAL COMFORT PRODUCTS | RHH060S******** |  |  |  | 58500 | 12.50 | 15.00 | 55000 | 8.20 | 28600 | HSP-A | CEE Tier 1 | OEM | Yes
6345840 | Active | KEEPRITE | KEEPRITE | PHR542***H***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345842 | Active | KEEPRITE | KEEPRITE | PHR548***H***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345844 | Active | KEEPRITE | KEEPRITE | PHR560***H***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
6345851 | Active | KENMORE | KENMORE | PHR542***H***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345853 | Active | KENMORE | KENMORE | PHR548***H***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345855 | Active | KENMORE | KENMORE | PHR560***H***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
6345862 | Active | TEMPSTAR | TEMPSTAR | PHR542***H***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345864 | Active | TEMPSTAR | TEMPSTAR | PHR548***H***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345866 | Active | TEMPSTAR | TEMPSTAR | PHR560***H***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
7180038 | Active | TRANE | TRANE | 4DCZ6036B3 |  |  |  | 36000 | 12.20 | 16.00 | 31000 | 8.30 | 19200 | HSP-A | CEE Tier 2 | OEM | -
7180043 | Active | TRANE | TRANE | 4DCZ6048B3 |  |  |  | 47500 | 12.00 | 16.00 | 42000 | 8.50 | 23200 | HSP-A | CEE Tier 2 | OEM | -
1505063 | Active | TRANE | TRANE | 4WCZ6036A3 |  |  |  | 36000 | 12.20 | 16.40 | 34000 | 9.00 | 20800 | HSP-A | CEE Tier 2 | OEM | -
1505065 | Active | TRANE | TRANE | 4WCZ6036A4 |  |  |  | 36000 | 12.20 | 16.40 | 34000 | 9.00 | 20800 | HSP-A | CEE Tier 2 | OEM | -
7180036 | Active | TRANE | TRANE | 4WCZ6036B3 |  |  |  | 36000 | 12.20 | 16.00 | 31000 | 8.30 | 19200 | HSP-A | CEE Tier 2 | OEM | -
7180037 | Active | TRANE | TRANE | 4WCZ6036B4 |  |  |  | 36000 | 12.20 | 16.00 | 31000 | 8.30 | 19200 | HSP-A | CEE Tier 2 | OEM | -
1505073 | Active | TRANE | TRANE | 4WCZ6048A3 |  |  |  | 47500 | 12.00 | 16.00 | 44500 | 9.00 | 27000 | HSP-A | CEE Tier 2 | OEM | -
1505075 | Active | TRANE | TRANE | 4WCZ6048A4 |  |  |  | 47500 | 12.00 | 16.00 | 44500 | 9.00 | 27000 | HSP-A | CEE Tier 2 | OEM | -
7180041 | Active | TRANE | TRANE | 4WCZ6048B3 |  |  |  | 47500 | 12.00 | 16.00 | 42000 | 8.50 | 23200 | HSP-A | CEE Tier 2 | OEM | -
7180042 | Active | TRANE | TRANE | 4WCZ6048B4 |  |  |  | 47500 | 12.00 | 16.00 | 42000 | 8.50 | 23200 | HSP-A | CEE Tier 2 | OEM | -

## CEEAHRIResidentialCooling
Consortium for Energy Efficiency (CEE) AHRI Residential Cooling Data
| Source: | https://www.ahridirectory.org/ahridirectory/pages/ac/cee/defaultSearch.aspx
Lists all units with SEER ≥17 serving residential applications:
Final pull on March 23, 2016
AHRIReferenceNumber | ModelStatus | OEMTradeName | OutdoorUnitOEMName | ModelNumber | IndoorUnitOEMName | CoilModelNumber | FurnaceModelNumber | Capacity95FHigh | EER95F | SEER | ARIType | TierValue | CEEManufacturerType | EnergyStar | Count of OEMTradeName | Column Labels
4890733 | Active | AAON | AAON, INC. | RQ-002-1-*-GA**-000 |  |  |  | 26200 | 14.75 | 19.15 | SP-A | CEE Tier 2 | OEM | - | Row Labels | AAON | ENERGENCE | Grand Total
4832459 | Active | AAON | AAON, INC. | RQ-002-1-*-HA**-000 |  |  |  | 25400 | 13.40 | 17.10 | SP-A | CEE Tier 2 | OEM | - | 17.00 | 2 |  | 2
4890741 | Active | AAON | AAON, INC. | RQ-002-9-*-GA**-000 |  |  |  | 26200 | 14.75 | 19.15 | SP-A | CEE Tier 2 | OEM | - | 17.10 | 6 | 1 | 7
4832467 | Active | AAON | AAON, INC. | RQ-002-9-*-HA**-000 |  |  |  | 25400 | 13.40 | 17.10 | SP-A | CEE Tier 2 | OEM | - | 17.40 | 2 |  | 2
4890743 | Active | AAON | AAON, INC. | RQ-003-1-*-GA**-000 |  |  |  | 37400 | 13.85 | 18.20 | SP-A | CEE Tier 2 | OEM | - | 17.45 | 2 |  | 2
4832469 | Active | AAON | AAON, INC. | RQ-003-1-*-HA**-000 |  |  |  | 37000 | 13.50 | 17.10 | SP-A | CEE Tier 2 | OEM | - | 17.60 |  | 1 | 1
4890753 | Active | AAON | AAON, INC. | RQ-003-9-*-GA**-000 |  |  |  | 37400 | 13.85 | 18.20 | SP-A | CEE Tier 2 | OEM | - | 18.00 |  | 1 | 1
4832479 | Active | AAON | AAON, INC. | RQ-003-9-*-HA**-000 |  |  |  | 37000 | 13.50 | 17.10 | SP-A | CEE Tier 2 | OEM | - | 18.20 | 2 |  | 2
4832491 | Active | AAON | AAON, INC. | RQ-004-1-*-GA**-000 |  |  |  | 49000 | 13.30 | 17.10 | SP-A | CEE Tier 2 | OEM | - | 19.15 | 2 |  | 2
4832503 | Active | AAON | AAON, INC. | RQ-004-1-*-GB**-000 |  |  |  | 50000 | 13.60 | 17.40 | SP-A | CEE Tier 2 | OEM | - | Grand Total | 16 | 3 | 19
7164975 | Active | AAON | AAON, INC. | RQ-004-1-*-HB**-000 |  |  |  | 47000 | 13.00 | 17.00 | SP-A | CEE Tier 2 | OEM | -
4832501 | Active | AAON | AAON, INC. | RQ-004-9-*-GA**-000 |  |  |  | 49000 | 13.30 | 17.10 | SP-A | CEE Tier 2 | OEM | -
4832513 | Active | AAON | AAON, INC. | RQ-004-9-*-GB**-000 |  |  |  | 50000 | 13.60 | 17.40 | SP-A | CEE Tier 2 | OEM | -
7164985 | Active | AAON | AAON, INC. | RQ-004-9-*-HB**-000 |  |  |  | 47000 | 13.00 | 17.00 | SP-A | CEE Tier 2 | OEM | -
4832547 | Active | AAON | AAON, INC. | RQ-005-1-*-GB**-000 |  |  |  | 59000 | 13.70 | 17.45 | SP-A | CEE Tier 2 | OEM | -
4832557 | Active | AAON | AAON, INC. | RQ-005-9-*-GB**-000 |  |  |  | 59000 | 13.70 | 17.45 | SP-A | CEE Tier 2 | OEM | -
3607616 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LCH036H4E**P |  |  |  | 35200 | 12.70 | 18.00 | SP-A | CEE Tier 2 | OEM | Yes
3607631 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LCH048H4E**P |  |  |  | 49000 | 12.80 | 17.60 | SP-A | CEE Tier 2 | OEM | Yes
3607645 | Active | ENERGENCE | LENNOX INDUSTRIES, INC. | LCH060H4E**P |  |  |  | 60000 | 12.70 | 17.10 | SP-A | CEE Tier 2 | OEM | Yes

## CEEAHRIResidentialHP
Consortium for Energy Efficiency (CEE) Residential Heat Pump Data
Final pull on March 23, 2016
AHRIReferenceNumber | ModelStatus | OEMTradeName | OutdoorUnitOEMName | ModelNumber | IndoorUnitOEMName | CoilModelNumber | FurnaceModelNumber | Capacity95FHigh | EER95F | SEER | HighHeat47F | HSPF | LowHeat17F | ARIType | TierValue | CEEManufacturerType | EnergyStar
6345795 | Active | AIRQUEST | AIRQUEST | PHR542***K***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | - | Max of Capacity95FHigh | Column Labels
6345797 | Active | AIRQUEST | AIRQUEST | PHR548***K***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | - | Row Labels | AIRQUEST | AIRQUEST; ARCOAIRE; COMFORTMAKER; DAY & NIGHT; HEIL; ICP COMMERCIAL; KEEPRITE; TEMPSTAR | AMERICAN STANDARD | ARCOAIRE | BRYANT | BRYANT HEATING & COOLING SYSTEMS | CARRIER | CARRIER CORPORATION | COMFORTMAKER | DAIKIN | DAY & NIGHT | HEIL | KEEPRITE | KENMORE | TEMPSTAR | TRANE | AMANA | BRYANT HEATING AND COOLING SYSTEMS | GOODMAN; JANITROL; AMANA DISTINCTIONS; EVERREST; ONE HOUR AIR CONDITIONING AND HEATING; ENERGI AIR | RHEEM; RUUD; WEATHERKING | THERMAL ZONE | XENON | YORK | Grand Total
6345799 | Active | AIRQUEST | AIRQUEST | PHR560***K***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | - | 15.00 | 57000 | 58500 | 47500 | 57000 | 57000 | 58500 | 57000 | 58500 | 57000 |  | 57000 | 57000 | 57000 | 57000 | 57000 | 47500 |  | 57000 |  | 56000 | 56000 |  | 58500 | 58500
8143322 | Active | AMANA | AMANA HEATING AND AIR CONDITIONING | APH1636M41A* |  |  |  | 33600 | 12.00 | 16.00 | 33600 | 8.20 | 19400 | HSP-A | CEE Tier 2 | OEM | Yes | 15.50 | 47500 |  |  | 47500 | 47500 |  | 47500 |  | 47500 |  | 47500 | 47500 | 47500 | 47500 | 47500 |  |  | 47500 | [5 empty] | 47500
8143323 | Active | AMANA | AMANA HEATING AND AIR CONDITIONING | APH1642M41A* |  |  |  | 41000 | 12.00 | 16.00 | 38000 | 8.20 | 21600 | HSP-A | CEE Tier 2 | OEM | Yes | 15.80 |  | 47000 |  |  |  | 47000 |  | 47000 | [15 empty] | 47000
8143324 | Active | AMANA | AMANA HEATING AND AIR CONDITIONING | APH1648M41A* |  |  |  | 47000 | 12.00 | 16.00 | 45500 | 8.20 | 27000 | HSP-A | CEE Tier 2 | OEM | Yes | 16.00 |  |  | 47500 | [6 empty] | 47000 | [5 empty] | 47500 | 47000 |  | 47000 | 45500 | 45500 | 47000 |  | 47500
7795572 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4DCZ6036C1 |  |  |  | 36000 | 12.20 | 16.00 | 31000 | 8.30 | 19200 | HSP-A | CEE Tier 2 | OEM | - | 16.40 |  |  | 36000 | [12 empty] | 36000 | [7 empty] | 36000
7795573 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4DCZ6048C1 |  |  |  | 47500 | 12.00 | 16.00 | 42000 | 8.50 | 23200 | HSP-A | CEE Tier 2 | OEM | - | Grand Total | 57000 | 58500 | 47500 | 57000 | 57000 | 58500 | 57000 | 58500 | 57000 | 47000 | 57000 | 57000 | 57000 | 57000 | 57000 | 47500 | 47000 | 57000 | 47000 | 56000 | 56000 | 47000 | 58500 | 58500
8955003 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCY5024A1 |  |  |  | 25000 | 13.00 | 15.00 | 22400 | 8.30 | 13100 | HSP-A | CEE Tier 1 | OEM | -
8955004 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCY5030A1 |  |  |  | 30000 | 12.00 | 15.00 | 28000 | 8.20 | 16700 | HSP-A | CEE Tier 1 | OEM | -
8955005 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCY5036A1 |  |  |  | 36000 | 12.00 | 15.00 | 32600 | 8.40 | 21800 | HSP-A | CEE Tier 1 | OEM | -
8955006 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCY5042A1 |  |  |  | 41500 | 12.00 | 15.00 | 37000 | 8.40 | 21200 | HSP-A | CEE Tier 1 | OEM | -
8955007 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCY5048A1 |  |  |  | 47500 | 12.00 | 15.00 | 42500 | 8.40 | 23200 | HSP-A | CEE Tier 1 | OEM | -
1505062 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCZ6036A1 |  |  |  | 36000 | 12.20 | 16.40 | 34000 | 9.00 | 20800 | HSP-A | CEE Tier 2 | OEM | -
7180047 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCZ6036B1 |  |  |  | 36000 | 12.20 | 16.00 | 31000 | 8.30 | 19200 | HSP-A | CEE Tier 2 | OEM | - | Max of Capacity95FHigh | Column Labels
1505072 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCZ6048A1 |  |  |  | 47500 | 12.00 | 16.00 | 44500 | 9.00 | 27000 | HSP-A | CEE Tier 2 | OEM | - | Row Labels | AIRQUEST | AIRQUEST; ARCOAIRE; COMFORTMAKER; DAY & NIGHT; HEIL; ICP COMMERCIAL; KEEPRITE; TEMPSTAR | AMERICAN STANDARD | ARCOAIRE | BRYANT | BRYANT HEATING & COOLING SYSTEMS | CARRIER | CARRIER CORPORATION | COMFORTMAKER | DAIKIN | DAY & NIGHT | HEIL | KEEPRITE | KENMORE | TEMPSTAR | TRANE | AMANA | BRYANT HEATING AND COOLING SYSTEMS | GOODMAN; JANITROL; AMANA DISTINCTIONS; EVERREST; ONE HOUR AIR CONDITIONING AND HEATING; ENERGI AIR | RHEEM; RUUD; WEATHERKING | THERMAL ZONE | XENON | YORK | Grand Total
7180052 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WCZ6048B1 |  |  |  | 47500 | 12.00 | 16.00 | 42000 | 8.50 | 23200 | HSP-A | CEE Tier 2 | OEM | - | 8.20 | 47500 | 58500 | 30000 | 47500 | 47500 | 58500 | 47500 | 58500 | 47500 | 47000 | 47500 | 47500 | 47500 | 47500 | 47500 | 30000 | 47000 | 47500 | 47000 | 29200 | 29200 | 47000 | 58500 | 58500
8107730 | Active | AMERICAN STANDARD | AMERICAN STANDARD | 4WHC4024A1 |  |  |  | 24800 | 13.60 | 16.00 | 21200 | 8.20 | 11700 | HSP-A | CEE Tier 2 | OEM | - | 8.30 |  |  | 36000 | [12 empty] | 36000 | [7 empty] | 36000
6345806 | Active | ARCOAIRE | ARCOAIRE | PHR542***K***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | - | 8.40 |  |  | 47500 | [12 empty] | 47500 | [7 empty] | 47500
6345808 | Active | ARCOAIRE | ARCOAIRE | PHR548***K***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | - | 8.50 | 57000 |  | 47500 | 57000 | 57000 |  | 57000 |  | 57000 |  | 57000 | 57000 | 57000 | 57000 | 57000 | 47500 |  | 57000 |  | 56000 | 56000 |  |  | 57000
6345810 | Active | ARCOAIRE | ARCOAIRE | PHR560***K***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | - | 9.00 |  |  | 47500 | [12 empty] | 47500 | [7 empty] | 47500
4935346 | Active | BRYANT HEATING & COOLING SYSTEMS | BRYANT HEATING & COOLING SYSTEMS | 549JJ05**********A |  |  |  | 47000 | 12.80 | 15.80 | 46000 | 8.20 | 23800 | HSP-A | CEE Tier 1 | OEM | Yes | Grand Total | 57000 | 58500 | 47500 | 57000 | 57000 | 58500 | 57000 | 58500 | 57000 | 47000 | 57000 | 57000 | 57000 | 57000 | 57000 | 47500 | 47000 | 57000 | 47000 | 56000 | 56000 | 47000 | 58500 | 58500
4935382 | Active | BRYANT HEATING & COOLING SYSTEMS | BRYANT HEATING & COOLING SYSTEMS | 549JJ06**********A |  |  |  | 58500 | 12.50 | 15.00 | 55000 | 8.20 | 28600 | HSP-A | CEE Tier 1 | OEM | Yes
6345770 | Active | BRYANT | BRYANT HEATING AND COOLING SYSTEMS | 607ENXA42****A |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345773 | Active | BRYANT | BRYANT HEATING AND COOLING SYSTEMS | 607ENXA48****A |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345776 | Active | BRYANT | BRYANT HEATING AND COOLING SYSTEMS | 607ENXA60****A |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
6345762 | Discontinued | BRYANT | BRYANT HEATING AND COOLING SYSTEMS | 677ENWA60****A |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
8170665 | Active | BRYANT HEATING AND COOLING SYSTEMS | BRYANT HEATING AND COOLING SYSTEMS | 677ENWB42****A |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
8170666 | Active | BRYANT HEATING AND COOLING SYSTEMS | BRYANT HEATING AND COOLING SYSTEMS | 677ENWB48****A |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
8170667 | Active | BRYANT HEATING AND COOLING SYSTEMS | BRYANT HEATING AND COOLING SYSTEMS | 677ENWB60****A |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
6335197 | Discontinued | CARRIER | CARRIER AIR CONDITIONING | 48VR*A60***30 |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
7850746 | Active | CARRIER | CARRIER AIR CONDITIONING | 48VR*B42***30 |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
7850747 | Active | CARRIER | CARRIER AIR CONDITIONING | 48VR*B48***30 |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
7850748 | Active | CARRIER | CARRIER AIR CONDITIONING | 48VR*B60***30 |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
6335179 | Active | CARRIER | CARRIER AIR CONDITIONING | 50VR*A42***30 |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6335182 | Active | CARRIER | CARRIER AIR CONDITIONING | 50VR*A48***30 |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6335185 | Active | CARRIER | CARRIER AIR CONDITIONING | 50VR*A60***30 |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
4890849 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50HCQ*05***3A* |  |  |  | 47000 | 12.80 | 15.80 | 46000 | 8.20 | 23800 | HSP-A | CEE Tier 1 | OEM | Yes
4890853 | Active | CARRIER CORPORATION | CARRIER CORPORATION | 50HCQ*06***3A* |  |  |  | 58500 | 12.50 | 15.00 | 55000 | 8.20 | 28600 | HSP-A | CEE Tier 1 | OEM | Yes
6345817 | Active | COMFORTMAKER | COMFORTMAKER | PHR542***K***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345819 | Active | COMFORTMAKER | COMFORTMAKER | PHR548***K***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345821 | Active | COMFORTMAKER | COMFORTMAKER | PHR560***K***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
8143327 | Active | DAIKIN | DAIKIN MANUFACTURING COMPANY, L.P. | DP16HM3641A* |  |  |  | 33600 | 12.00 | 16.00 | 33600 | 8.20 | 19400 | HSP-A | CEE Tier 2 | OEM | Yes
8143328 | Active | DAIKIN | DAIKIN MANUFACTURING COMPANY, L.P. | DP16HM4241A* |  |  |  | 41000 | 12.00 | 16.00 | 38000 | 8.20 | 21600 | HSP-A | CEE Tier 2 | OEM | Yes
8143329 | Active | DAIKIN | DAIKIN MANUFACTURING COMPANY, L.P. | DP16HM4841A* |  |  |  | 47000 | 12.00 | 16.00 | 45500 | 8.20 | 27000 | HSP-A | CEE Tier 2 | OEM | Yes
6345828 | Active | DAY & NIGHT | DAY & NIGHT | PHR542***K***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345830 | Active | DAY & NIGHT | DAY & NIGHT | PHR548***K***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345832 | Active | DAY & NIGHT | DAY & NIGHT | PHR560***K***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
8143314 | Active | GOODMAN; JANITROL; AMANA DISTINCTIONS; EVERREST; ONE HOUR AIR CONDITIONING AND HEATING; ENERGI AIR | GOODMAN MANUFACTURING CO., LP. | GPH1636M41A* |  |  |  | 33600 | 12.00 | 16.00 | 33600 | 8.20 | 19400 | HSP-A | CEE Tier 2 | OEM | Yes
8143315 | Active | GOODMAN; JANITROL; AMANA DISTINCTIONS; EVERREST; ONE HOUR AIR CONDITIONING AND HEATING; ENERGI AIR | GOODMAN MANUFACTURING CO., LP. | GPH1642M41A* |  |  |  | 41000 | 12.00 | 16.00 | 38000 | 8.20 | 21600 | HSP-A | CEE Tier 2 | OEM | Yes
8143316 | Active | GOODMAN; JANITROL; AMANA DISTINCTIONS; EVERREST; ONE HOUR AIR CONDITIONING AND HEATING; ENERGI AIR | GOODMAN MANUFACTURING CO., LP. | GPH1648M41A* |  |  |  | 47000 | 12.00 | 16.00 | 45500 | 8.20 | 27000 | HSP-A | CEE Tier 2 | OEM | Yes
6345784 | Active | HEIL | HEIL | PHR542***K***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345786 | Active | HEIL | HEIL | PHR548***K***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345788 | Active | HEIL | HEIL | PHR560***K***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
4935366 | Active | AIRQUEST; ARCOAIRE; COMFORTMAKER; DAY & NIGHT; HEIL; ICP COMMERCIAL; KEEPRITE; TEMPSTAR | INTERNATIONAL COMFORT PRODUCTS | RHH048K******** |  |  |  | 47000 | 12.80 | 15.80 | 46000 | 8.20 | 23800 | HSP-A | CEE Tier 1 | OEM | Yes
4935402 | Active | AIRQUEST; ARCOAIRE; COMFORTMAKER; DAY & NIGHT; HEIL; ICP COMMERCIAL; KEEPRITE; TEMPSTAR | INTERNATIONAL COMFORT PRODUCTS | RHH060K******** |  |  |  | 58500 | 12.50 | 15.00 | 55000 | 8.20 | 28600 | HSP-A | CEE Tier 1 | OEM | Yes
6345839 | Active | KEEPRITE | KEEPRITE | PHR542***K***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345841 | Active | KEEPRITE | KEEPRITE | PHR548***K***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345843 | Active | KEEPRITE | KEEPRITE | PHR560***K***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
6345850 | Active | KENMORE | KENMORE | PHR542***K***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345852 | Active | KENMORE | KENMORE | PHR548***K***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345854 | Active | KENMORE | KENMORE | PHR560***K***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
4398659 | Active | RHEEM; RUUD; WEATHERKING | RHEEM SALES COMPANY, INC. | RQRM-A024JK |  |  |  | 24000 | 13.00 | 16.00 | 23800 | 8.20 | 11700 | HSP-A | CEE Tier 2 | OEM | -
4141682 | Active | RHEEM; RUUD; WEATHERKING | RHEEM SALES COMPANY, INC. | RQRM-A030JK |  |  |  | 29200 | 13.00 | 16.00 | 28800 | 8.20 | 16000 | HSP-A | CEE Tier 2 | OEM | -
4398660 | Active | RHEEM; RUUD; WEATHERKING | RHEEM SALES COMPANY, INC. | RQRM-A042JK |  |  |  | 42000 | 13.00 | 16.00 | 39500 | 8.50 | 22400 | HSP-A | CEE Tier 2 | OEM | -
4141684 | Active | RHEEM; RUUD; WEATHERKING | RHEEM SALES COMPANY, INC. | RQRM-A048JK |  |  |  | 45500 | 13.00 | 16.00 | 43500 | 8.50 | 23800 | HSP-A | CEE Tier 2 | OEM | Yes
4398694 | Active | RHEEM; RUUD; WEATHERKING | RHEEM SALES COMPANY, INC. | RQRM-A060JK |  |  |  | 56000 | 12.00 | 15.00 | 55000 | 8.50 | 31600 | HSP-A | CEE Tier 1 | OEM | -
6345861 | Active | TEMPSTAR | TEMPSTAR | PHR542***K***A* |  |  |  | 42000 | 12.00 | 15.00 | 42000 | 8.20 | 24000 | HSP-A | CEE Tier 1 | OEM | -
6345863 | Active | TEMPSTAR | TEMPSTAR | PHR548***K***A* |  |  |  | 47500 | 12.50 | 15.50 | 47000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
6345865 | Active | TEMPSTAR | TEMPSTAR | PHR560***K***A* |  |  |  | 57000 | 12.00 | 15.00 | 57000 | 8.50 | 32400 | HSP-A | CEE Tier 1 | OEM | -
7795564 | Active | TRANE | TRANE | 4DCZ6036C1 |  |  |  | 36000 | 12.20 | 16.00 | 31000 | 8.30 | 19200 | HSP-A | CEE Tier 2 | OEM | -
7795565 | Active | TRANE | TRANE | 4DCZ6048C1 |  |  |  | 47500 | 12.00 | 16.00 | 42000 | 8.50 | 23200 | HSP-A | CEE Tier 2 | OEM | -
8954997 | Active | TRANE | TRANE | 4WCY5024A1 |  |  |  | 25000 | 13.00 | 15.00 | 22400 | 8.30 | 13100 | HSP-A | CEE Tier 1 | OEM | -
8955001 | Active | TRANE | TRANE | 4WCY5030A1 |  |  |  | 30000 | 12.00 | 15.00 | 28000 | 8.20 | 16700 | HSP-A | CEE Tier 1 | OEM | -
8955002 | Active | TRANE | TRANE | 4WCY5036A1 |  |  |  | 36000 | 12.00 | 15.00 | 32600 | 8.40 | 21800 | HSP-A | CEE Tier 1 | OEM | -
8954998 | Active | TRANE | TRANE | 4WCY5042A1 |  |  |  | 41500 | 12.00 | 15.00 | 37000 | 8.40 | 21200 | HSP-A | CEE Tier 1 | OEM | -
8954999 | Active | TRANE | TRANE | 4WCY5048A1 |  |  |  | 47500 | 12.00 | 15.00 | 42500 | 8.40 | 23200 | HSP-A | CEE Tier 1 | OEM | -
1505061 | Active | TRANE | TRANE | 4WCZ6036A1 |  |  |  | 36000 | 12.20 | 16.40 | 34000 | 9.00 | 20800 | HSP-A | CEE Tier 2 | OEM | -
7180034 | Active | TRANE | TRANE | 4WCZ6036B1 |  |  |  | 36000 | 12.20 | 16.00 | 31000 | 8.30 | 19200 | HSP-A | CEE Tier 2 | OEM | -
1505071 | Active | TRANE | TRANE | 4WCZ6048A1 |  |  |  | 47500 | 12.00 | 16.00 | 44500 | 9.00 | 27000 | HSP-A | CEE Tier 2 | OEM | -
7180039 | Active | TRANE | TRANE | 4WCZ6048B1 |  |  |  | 47500 | 12.00 | 16.00 | 42000 | 8.50 | 23200 | HSP-A | CEE Tier 2 | OEM | -
8107726 | Active | TRANE | TRANE | 4WHC4024A1 |  |  |  | 24800 | 13.60 | 16.00 | 21200 | 8.20 | 11700 | HSP-A | CEE Tier 2 | OEM | -
4398664 | Active | THERMAL ZONE | UNITED REFRIGERATION, INC. | TZHH-624JL |  |  |  | 24000 | 13.00 | 16.00 | 23800 | 8.20 | 11700 | HSP-A | CEE Tier 2 | OEM | -
4141748 | Active | THERMAL ZONE | UNITED REFRIGERATION, INC. | TZHH-630JL |  |  |  | 29200 | 13.00 | 16.00 | 28800 | 8.20 | 16000 | HSP-A | CEE Tier 2 | OEM | -
4398668 | Active | THERMAL ZONE | UNITED REFRIGERATION, INC. | TZHH-642JL |  |  |  | 42000 | 13.00 | 16.00 | 39500 | 8.50 | 22400 | HSP-A | CEE Tier 2 | OEM | -
4141756 | Active | THERMAL ZONE | UNITED REFRIGERATION, INC. | TZHH-648JL |  |  |  | 45500 | 13.00 | 16.00 | 43500 | 8.50 | 23800 | HSP-A | CEE Tier 2 | OEM | -
4398698 | Active | THERMAL ZONE | UNITED REFRIGERATION, INC. | TZHH-660JL |  |  |  | 56000 | 12.00 | 15.00 | 55000 | 8.50 | 31600 | HSP-A | CEE Tier 1 | OEM | -
8382114 | Active | XENON | XENON | GPH1636M41A* |  |  |  | 33600 | 12.00 | 16.00 | 33600 | 8.20 | 19400 | HSP-A | CEE Tier 2 | OEM | -
8382115 | Active | XENON | XENON | GPH1642M41A* |  |  |  | 41000 | 12.00 | 16.00 | 38000 | 8.20 | 21600 | HSP-A | CEE Tier 2 | OEM | -
8382116 | Active | XENON | XENON | GPH1648M41A* |  |  |  | 47000 | 12.00 | 16.00 | 45500 | 8.20 | 27000 | HSP-A | CEE Tier 2 | OEM | -
8936441 | Active | YORK | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | XYE05A1*********** |  |  |  | 47000 | 12.50 | 15.00 | 46000 | 8.20 | 26000 | HSP-A | CEE Tier 1 | OEM | -
8936445 | Active | YORK | YORK, UNITARY PRODUCTS GROUP - COMMERCIAL | XYE06A1*********** |  |  |  | 58500 | 12.50 | 15.00 | 55000 | 8.20 | 30000 | HSP-A | CEE Tier 1 | OEM | -