## README
Commercial Air Source Heat Pump
Measure Characterization:
| Measure Description | Commercial Air Source Heat Pump
| Baseline | Standard Efficient Air Source Heat Pump
| Measure Scenario(s) | ROB, NC
| Baseline Efficiency Levels | IECC IECC 2009 and/or jurisdiction-specific. (IECC 2012 did not make any substantial change to the baseline requirement.) Baseline efficiencies vary by size.
| Measure Level Description | High efficiency Split or Packaged Air Source Heat Pumps meeting CEE Tier requirements
| Measure Efficiency Levels | CEE Tier 1 & Tier 2 (see CEE Criteria Tab). Tier 2 for units with capacities larger than 65,000 Btu/h are based on the Cool Choice program.
| Sizes | <5.4 tons
5.4 - 11.25 tons
11.25 - 20 tons
20 - 63 tons
| Distinguishing Features | With or without electric resistance backup heating versus all other types of backup heat
| Installation Scenarios | Split System or Single Package
| Sources | NY TRM, Efficiency Maine TRM, Massachusetts TRM
| Comments | DX or VRF, Ducted only, non-ducted (e.g., mini-splits) excluded
| Incremental Labor Cost | No
| Cost Basis | Incremental
Incremental Cost Methodology
Incremental measure costs (not the full cost) are used when an energy-efficient appliance or measure promoted through the program is installed in lieu of the standard (less efficient) appliance/measure. The equation for calculating incremental measure costs is simply:
Incremental measure cost = high efficient measure material cost - base case material cost
Measure: A measure is defined as the efficient alternative to the baseline option of installation. In this case, it is defined as an air source heat pump with SEER in line with the CEE Criteria (see CEE Criteria Tab).
Baseline: The baseline condition is defined as the standard equipment that would have been installed without the utility EE activity. The baseline equipment in this instance is an air source heat pump with SEER in line with the current minimum Federal standard.
Summary of Results Tab
The summary of results tab presents the incremental cost for the commercial air source heat pumps. Incremental costs are presented in 7 categories allowing NEEP constituents to choose the market that best represents their services territory.
The regions presented represent the results of analyzing RSMeans City Cost Index (CCI). Navigant's analysis of the CCI determined that NEEP's overall service territories could be categorized into 6 unique regions (7 including a Non-Regional Specific category).
Data Analysis Tab
Raw Data
A total of 38 cost points were collected through contractor interviews and invoices provided by NEEP constituents. Of the total number of cost points, 22 were commercial installations, while 16 were residential split ASHP systems. Only material costs were used from residential data. There are no differences in a commercial versus residential split ASHP systems in the sizes presented here. The residential data, however, does not include economizer costs, which is found in some installation scenarios.
The data collected from program administrator invoices clearly points to smaller sized units being incentivized under their prescriptive programs. As such, Navigant developed incremental cost for air source heat pump units 3, 4, and 5 tons. Our contractor interview confirmed that not many units over 20 tons are being installed. Furthermore, Itron, in their February 28, 2014 Measure Cost Study for the California Public Utilities Commission notes that manufacturers have discontinued manufacturing packaged heat pump units over 20 tons.
Formatted Data
Primary cost data was collected from contractors across four states (MD, MA, RI, and NY). Due to the inherent differences in cost from one region to another, Navigant adjusted all material and labor cost points to represent Base Cost Factor (BCF) data using RSMeans CCI. For example, if the cost provided from a contractor in Pennsylvania for an air source heat pump was $5000, than the NRS cost would be:
BCF = Original State Cost ($) / Average Adjustment Factor for Original State
BCF = $5000 / 0.99
BCF = $5050
The same method was used to adjust all labor cost.
Material Analysis
The analysis identified and removed any potential outlier data points through a review of the data. Any assumed values were based on model information and further research.
A linear regression was used to develop the material cost for the measure. A regression was done for air source heat pump units up to 5 tons in size.
The regression analysis resulted in one incremental cost per size category. Although the actual material costs vary within a size category, the typical incremental costs does not.
Labor Analysis
Navigant conducted contractor interviews to identify no incremental difference in the time to install efficient versus base scenario equipment. In general, efficient equipment took just as much time to install as compared with base equipment. Per the contractor interview, labor required to install a baseline unit and an efficient unit is the same.
Results
Navigant defined the unit sizes based on program records provided by program administrator. This data shows too few units greater than 5 tons to complete a robust analysis for air source heat pump systems greater than 5 tons.

## Summary of Results
Commercial Air Source Heat Pump
Does this measure have incremental labor cost (Yes/No)? | No
Size Category (Tons) | Market 1 Northern New England Incremental Cost ($/Unit)
| CEE Tier 1 | CEE Tier 2
3 | 423.1406 | 846.2811
4 | 423.1406 | 846.2811
5 | 423.1406 | 846.2811
Size Category (Tons) | Market 2 Central/Southern New England Incremental Cost ($/Unit)
| CEE Tier 1 | CEE Tier 2
3 | 497.3793 | 994.7586
4 | 497.3793 | 994.7586
5 | 497.3793 | 994.7586
Size Category (Tons) | Market 3 New England City Incremental Cost ($/Unit)
| CEE Tier 1 | CEE Tier 2
3 | 527.6582 | 1055.3165
4 | 527.6582 | 1055.3165
5 | 527.6582 | 1055.3165
Size Category (Tons) | Market 4 NY Metro Incremental Cost ($/Unit)
| CEE Tier 1 | CEE Tier 2
3 | 590.6028 | 1181.2057
4 | 590.6028 | 1181.2057
5 | 590.6028 | 1181.2057
Size Category (Tons) | Market 5 NY Upstate Incremental Cost ($/Unit)
| CEE Tier 1 | CEE Tier 2
3 | 467.1706 | 934.3412
4 | 467.1706 | 934.3412
5 | 467.1706 | 934.3412
Size Category (Tons) | Market 6 Mid-Atlantic Cost ($/Unit)
| CEE Tier 1 | CEE Tier 2
3 | 442.8351 | 885.6702
4 | 442.8351 | 885.6702
5 | 442.8351 | 885.6702
Base Cost Factor Costs:
Size Category (Tons) | Base Cost Factor -BCF ($/Unit)
| CEE Tier 1 | CEE Tier 2
3 | 467.9896 | 935.9791
4 | 467.9896 | 935.9791
5 | 467.9896 | 935.9791
Market | Market Code | Regions | Material Adjustment Factor | Labor Adjustment Factor | Total
Northern New England | 1 | ME, VT, NH | 0.97583 | 0.81533 | 0.90417
Central/Southern New England | 2 | MA (exc Boston), RI, most CT | 0.9836 | 1.1632 | 1.0628
New England City | 3 | Boston, Providence | 1.008 | 1.2795 | 1.1275
NY Metro | 4 | NYC, Metro, Suburbs, Southeast CT, | 1.0278 | 1.5593 | 1.262
NY Upstate | 5 | Buffalo, Rochester etc. | 0.9865 | 1.0135 | 0.99825
Mid-Atlantic | 6 | MD, DE, DC | 0.99275 | 0.88775 | 0.94625
National Average | - | - | 1 | 1 | 1
Summary of incremental cost data analysis for commercial Air Source Heat Pump:
Regional adjustment factors are applied to national average incremental costs. Regional adjustment factors were developed using RSMeans Masterformat City Cost Indexes based on weighted average of division category .

## Data Analysis
Raw Data | [18 empty] | Formatted Data | [16 empty] | Material Analysis |  |  |  | Labor Analysis |  | Regional Adjustment Factors | [5 empty] | Results
Commercial Air Source Heat Pumps | [18 empty] | Note: All costs and Labor were adjusted to reflect National values based on RSMeans City Cost Indexes (CCI). | [16 empty] | Commercial Air Source Heat Pumps
Assumed
[8 empty] | Outliers | [19 empty] | Calculated based on full installed cost
Primary Data | [18 empty] | Commercial Air Source Heat Pumps | [16 empty] | Regression for units up to 5 tons |  |  |  | Commercial Air Source Heat Pumps |  | Reference: RSMeans Masterformat City Cost Indexes based on weighted average of division category | [5 empty] | Commercial Air Source Heat Pumps
Region | ID | Make | Model Number | Condenser | Evaporator | Size Category | Efficiency Tier | SEER | EER | Tons | IEER | Total Equip Cost | Other Materials | Labor Rate ($/Hr) | Tot Labor Hours | Installed Cost | Sector | Notes | Region | ID | Make | Size Category | CEE Tier | SEER/EER | Tons | EER | IEER | Equip Cost ($/AC) | Non Regional Specific Adjusted Equipment Cost ($/AC) | Other Materials | Labor Rate ($/Hr) | Base Cost Factor Labor Rate ($/Hr) | Tot Labor Hours | Installed Cost | $/Ton |  | SEER |  |  | Efficient Measure |  | Region | Market Code | Reference City | Material | Installation | Total | CEE Tier 1 |  |  | Efficient Measure |  |  | Baseline Measure |  |  | Estimated Incremental Cost Results ($/AC)
MA | 1 | TRANE | TTA120E300A |  |  | 2 | 2 |  | 12.2 | 10 | 11.7 | 7327 |  |  |  |  | Commercial |  | MA | 20 | Goodman/Carrier | 1 | 0 | 13 | 2.7 |  |  | 1500 | 1506.3266 | 2200 | 70 | 57.3136 | 16 | 2620 | 557.8987 | Tons | 13 | 14 | 15 | Labor Rate ($/Hr) | 57.3136 | Maine | 1 | Portland | 99.2 | 92.1 | 96.1 | Size Category | Tons | SEER/EER Rating | Efficient Material Cost | Efficient Labor Cost | Efficient Installed Cost | Base Material Cost | Base Labor Cost | Base Installed Cost | Material Cost | Labor Cost | Installed Cost
MA | 2 | MITSUBISHI | N/A | MUY-GE24NA | MSY-GE24NA | 1 | 2 | 19 | 12.5 | 2 | [5 empty] | 4583 | Commercial |  | MD | 4 | YORK | 1 | 0 | 13 | 4 | 11 |  | 4636 | 4669.8565 |  | 95 | 107.0121 |  |  | 1167.4641 | 3 | 2763.4463 | 3231.4359 | 3699.4255 | Labor Hours (Hr) - Size 1 | 16 | Maine | 1 | Rockland | 94.2 | 87.5 | 91.2 | 1 | 3 | 14 | 3231.4359 | 917.0181 | 4148.4539 | 2763.4463 | 917.0181 | 3680.4644 | 467.9896 | 0 | 467.9896
MA | 3 | CARRIER | N/A | 25HCB660A003 | CNVP6124ACA | 1 | 2 | 16 | 12.5 | 5 | [5 empty] | 13158 | Commercial |  | MA | 15 | Goodman/Carrier | 1 | 1 | 14 | 2.7 |  |  | 1935 | 1943.1613 | 2200 | 70 | 57.3136 | 16 | 3055 | 719.6894 | 4 | 4260.1079 | 4728.0975 | 5196.087 | Labor Hours (Hr) - Size 2 | 32 | Massachusetts | 3 | Boston | 101.5 | 139.2 | 118.1 | 1 | 4 | 14 | 4728.0975 | 917.0181 | 5645.1155 | 4260.1079 | 917.0181 | 5177.126 | 467.9896 | 0 | 467.9896
MD | 4 | YORK | X9048C00P2AAA2 |  |  | 1 | 0 | 13 | 11 | 4 |  | 4636 |  | 95 |  |  | Commercial | 7.7 HSPF, includes 15 kW electric heat ($423.9) packaged RTU unit. | MD | 10 | Carrier | 1 | 1 | 14.5 | 4.7 | 12 |  | 7426.788 | 7481.0254 |  |  | 0 |  | 9729 | 1591.7075 | 5 | 5756.7695 | 6224.759 | 6692.7486 | Labor Hours (Hr) - Size 3 | 60 | Massachusetts | 2 | Fall River | 99.9 | 127.9 | 112.3 | 1 | 5 | 14 | 6224.759 | 917.0181 | 7141.7771 | 5756.7695 | 917.0181 | 6673.7875 | 467.9896 | 0 | 467.9896
MD | 5 | CARRIER | 50HCQA06A2A5-0A0A0 |  |  | 1 | 2 | 15.2 | 12.5 | 5 | [5 empty] | 11600 | Commercial |  | NY | 24 | AMANA | 1 | 1 | 16 | 4.75 | 12 |  | 4680.9488 | 4647.833 |  |  | 0 |  | 10443.18 | 978.4912 |  |  |  |  | Labor Hours (Hr) - Size 4 | NA | Massachusetts | 2 | Greenfield | 96.9 | 109.9 | 102.6 | [8 empty] | Average | 467.9896 | 0 | 467.9896
MA | 6 | AMERICAN STANDARD | 4A6H5036G100A |  |  | 1 | 2 | 15 |  | 3 | [5 empty] | 15000 | Commercial |  | MD | 9 | Carrier | 1 | 2 | 14.5 | 4.7 | 12 |  | 10429.8699 | 10506.0387 |  |  | 0 |  | 13663 | 2235.3274 | [6 empty] | Massachusetts | 2 | Pittsfield | 99.1 | 107.1 | 102.7
MA | 7 | COLEMAN | HC8B036F3 |  |  | 1 | 2 | 16.9 | 13 | 3 |  | 3784 |  |  |  |  | Commercial | 10 HSPF | MA | 17 | Goodman/Carrier | 1 | 2 | 15 | 2.7 |  |  | 2580 | 2590.8817 | 2200 | 70 | 57.3136 | 16 | 3700 | 959.5858 | Material Regression units up to 5 tons |  |  |  | Baseline Measure |  | New Hampshire | 1 | Manchester | 100.6 | 94 | 97.2 | CEE Tier 2 |  |  | Efficient Measure |  |  | Baseline Measure |  |  | Estimated Incremental Cost Results ($/AC)
RI | 8 | CARRIER | 25HNB/FE4A |  |  | 1 | 2 | 16 | 12.7 | 5 |  | 5097 |  |  |  |  | Commercial |  | MD | 11 | Carrier | 1 | 2 | 15 | 2.9 | 12.5 |  | 5427.5324 | 5467.1694 |  |  | 0 |  | 7110 | 1885.2308 | 1496.6616 | 467.9896 | -7810.4027 |  | Labor Rate ($/Hr) | 57.3136 | New Hampshire | 1 | Claremont | 94.9 | 70.7 | 84.2 | Size Category | Tons | SEER/EER Rating | Efficient Material Cost | Efficient Labor Cost | Efficient Installed Cost | Base Material Cost | Base Labor Cost | Base Installed Cost | Material Cost | Labor Cost | Installed Cost
MD | 9 | Carrier | 25HCC560A**30 |  |  | 1 | 2 | 14.5 | 12 | 4.7 | [5 empty] | 13663 | Commercial | Single Package | MA | 6 | AMERICAN STANDARD | 1 | 2 | 15 | 3 |  |  | 11450.4903 | 11498.7852 |  |  | 0 |  | 15000 | 3832.9284 | 644.4269 | 427.3445 | 6772.5154 |  | Labor Hours (Hr) - Size 1 | 16 | Rhode Island | 2 | Newport | 98.7 | 116.7 | 106.6 | 1 | 3 | 15 | 3699.4255 | 917.0181 | 4616.4435 | 2763.4463 | 917.0181 | 3680.4644 | 935.9791 | 0 | 935.9791
MD | 10 | Carrier | 25HCC560A**30 |  |  | 1 | 1 | 14.5 | 12 | 4.7 | [5 empty] | 9729 | Commercial | Split System | NY | 26 | LUXAIRE | 1 | 2 | 15 | 3.3 | 12.5 |  | 2353.2086 | 2336.5606 |  |  | 0 |  | 5250 | 708.0487 | 0.22712 | 2674.3612 | #N/A |  | Labor Hours (Hr) - Size 2 | 32 | Rhode Island | 3 | Providence | 100.1 | 116.7 | 107.4 | 1 | 4 | 15 | 5196.087 | 917.0181 | 6113.1051 | 4260.1079 | 917.0181 | 5177.126 | 935.9791 | 0 | 935.9791
MD | 11 | Carrier | 25HCC536A**30 |  |  | 1 | 2 | 15 | 12.5 | 2.9 | [5 empty] | 7110 | Commercial | Split System | NY | 27 | Lennox | 1 | 2 | 15 | 3.6 | 12.5 |  | 2319.5913 | 2303.1812 |  |  | 0 |  | 5175 | 639.7726 | 3.6733 | 25 | #N/A |  | Labor Hours (Hr) - Size 3 | 60 | New York | 5 | Albany | 97 | 99.8 | 98.2 | 1 | 5 | 15 | 6692.7486 | 917.0181 | 7609.7667 | 5756.7695 | 917.0181 | 6673.7875 | 935.9791 | 0 | 935.9791
NY | 12 | Daikin | RXYQ72PBYD |  |  | 2 | 2 |  | 12.8 | 6 | 19 |  |  |  |  | 44800 | Commercial |  | NY | 29 | LENNOX | 1 | 2 | 15 | 3.6 | 13 |  | 4668.3177 | 4635.2912 |  |  | 0 |  | 10415 | 1287.5809 | 52545052.1317 | 178805191.7876 | #N/A |  | Labor Hours (Hr) - Size 4 | NA | New York | 4 | Brooklyn | 103 | 164.8 | 130.2 | [8 empty] | Average | 935.9791 | 0 | 935.9791
NY | 13 | Daikin | RXYQ240PBYD |  |  | 3 | 2 |  | 11.6 | 20 | 16 |  |  |  |  | 105900 | Commercial |  | NY | 28 | ARMSTRONG | 1 | 2 | 15 | 4 | 12.5 |  | 4269.3928 | 4239.1885 |  |  | 0 |  | 9525 | 1059.7971 | [6 empty] | New York | 5 | Buffalo | 100 | 104.1 | 101.8
NY | 14 | Heil | NXH560GKA |  |  | 1 | 2 | 15 | 12.5 | 5 | [5 empty] | 13515 | Commercial |  | NY | 35 | TRANE | 1 | 2 | 15 | 4.7917 | 12.5 |  | 3070.377 | 3048.6553 |  |  | 0 |  | 6850 | 636.2411 |  |  |  |  | Interview Notes: |  | New York | 4 | New York | 104.2 | 167 | 131.9
MA | 15 | Goodman/Carrier |  |  |  | 1 | 1 | 14 |  | 2.7 |  | 1935 | 2200 | 70 | 16 | 3055 | Commercial |  | NY | 31 | LENNOX | 1 | 2 | 15 | 4.9167 | 12.5 |  | 3966.8374 | 3938.7736 |  |  | 0 |  | 8850 | 801.1065 |  |  |  |  | Labor does not change between baseline and efficient install |  | New York | 5 | Rochester | 100.1 | 96 | 98.3
MA | 16 | Goodman/Carrier |  |  |  | 2 | 1 |  | 11.3 | 8.3 |  | 11825 | 2200 | 70 | 32 | 14065 | Commercial |  | NY | 23 | Lennox | 1 | 2 | 15 | 5 | 12.5 |  | 4699.6938 | 4666.4453 |  |  | 0 |  | 10485 | 933.2891 | Equipment/Labor Ratio (used to convert "Installed Cost" to "Equipment Cost" for commercial units) | [5 empty] | New York | 5 | Niagara Falls | 97.5 | 105.5 | 101
MA | 17 | Goodman/Carrier |  |  |  | 1 | 2 | 15 |  | 2.7 |  | 2580 | 2200 | 70 | 16 | 3700 | Commercial |  | NY | 14 | Heil | 1 | 2 | 15 | 5 | 12.5 |  | 10316.8918 | 10243.9039 |  |  | 0 |  | 13515 | 2048.7808 | ID | Total Equipment Cost ($) | Total Project Cost ($) | % of Total |  |  | New York | 4 | Long Island City | 102.5 | 164.8 | 130
MA | 18 | Goodman/Carrier |  |  |  | 2 | 2 |  | 12 | 8.3 |  | 12900 | 2200 | 70 | 32 | 15140 | Commercial |  | MD | 5 | CARRIER | 1 | 2 | 15.2 | 5 | 12.5 |  | 8855.0458 | 8919.7138 |  |  | 0 |  | 11600 | 1783.9428 | 15 | 1935 | 3055 | 63.34% |  |  | Vermont | 1 | Burlington | 100.5 | 77.8 | 90.5
MA | 19 | Goodman/Carrier |  |  |  | 3 | 2 |  | 12 | 15.6 |  | 16125 | 2200 | 70 | 60 | 20325 | Commercial |  | NY | 34 | TEMPSTAR | 1 | 2 | 15.5 | 3.5 | 13 |  | 2913.4964 | 2892.8846 |  |  | 0 |  | 6500 | 826.5384 | 16 | 11825 | 14065 | 84.07% |  |  | Vermont | 1 | Guildhall | 96.1 | 67.1 | 83.3
MA | 20 | Goodman/Carrier |  |  |  | 1 | 0 | 13 |  | 2.7 |  | 1500 | 2200 | 70 | 16 | 2620 | Commercial |  | NY | 33 | LENNOX | 1 | 2 | 15.5 | 3.625 | 13 |  | 1523.9827 | 1513.2012 |  |  | 0 |  | 3400 | 417.4348 | 17 | 2580 | 3700 | 69.73% |  |  | Connecticut | 4 | Stamford | 101.4 | 127.1 | 112.7
MA | 21 | Goodman/Carrier |  |  |  | 2 | 0 |  | 11 | 8.3 |  | 8000 | 2200 | 70 | 32 | 10240 | Commercial |  | NY | 30 | MAYTAG | 1 | 2 | 16 | 4 | 12.5 |  | 3496.1957 | 3471.4615 |  |  | 0 |  | 7800 | 867.8654 | 18 | 12900 | 15140 | 85.2% |  |  | Connecticut | 2 | New London | 97.2 | 120 | 107.2
MA | 22 | Goodman/Carrier |  |  |  | 3 | 0 |  | 10.6 | 15.6 |  | 10000 | 2200 | 70 | 60 | 14200 | Commercial |  | RI | 8 | CARRIER | 1 | 2 | 16 | 5 | 12.7 |  | 5097 | 5118.4977 |  |  | 0 |  |  | 1023.6995 | 19 | 16125 | 20325 | 79.34% |  |  | Delaware | 6 | Wilmington | 98.6 | 108.9 | 103.1
NY | 23 | Lennox | TPA060H4N42Y | 5812C09881 | CBX27UH-060 | 1 | 2 | 15 | 12.5 | 5 | [5 empty] | 10485 | Residential | Split System. Includes Air Handler and thermostat | MA | 3 | CARRIER | 1 | 2 | 16 | 5 | 12.5 |  | 10044.3701 | 10086.7344 |  |  | 0 |  | 13158 | 2017.3469 |  |  | Average | 0.76337 |  |  | Maryland | 6 | Easton | 97.3 | 69.7 | 85.1
NY | 24 | AMANA | ASZC160601 |  |  | 1 | 1 | 16 | 12 | 4.75 | [5 empty] | 10443.18 | Residential | Split System. Includes Air Handler and thermostat | NY | 25 | CARRIER | 1 | 2 | 16.8 | 3.9 | 13.1 |  | 6678.6302 | 6631.3816 |  |  | 0 |  | 14900 | 1700.3542 | [6 empty] | Maryland | 6 | Baltimore | 100.1 | 84.1 | 93
NY | 25 | CARRIER | 25HNB948A003 |  |  | 1 | 2 | 16.8 | 13.1 | 3.9 | [5 empty] | 14900 | Residential | Split System. Includes Air Handler and thermostat | MA | 7 | COLEMAN | 1 | 2 | 16.9 | 3 | 13 |  | 3784 | 3799.9598 |  |  | 0 |  |  | 1266.6533 | Data from NEEP residential ASHP analysis | [5 empty] | D.C. | 6 | Washington | 101.1 | 92.4 | 97.3
NY | 26 | LUXAIRE | THJF4254133A | W161839252 | AHE6003XH21A | 1 | 2 | 15 | 12.5 | 3.3 | [5 empty] | 5250 | Residential | Split system. | NY | 32 | COLEMAN | 1 | 2 | 17 | 3.9167 | 12.5 |  | 5671.9051 | 5631.7787 |  |  | 0 |  | 12654 | 1437.9009 | Equipment/Labor Ratio (used to convert "Installed Cost" to "Equipment Cost" for residential units) | [5 empty] | Geographically Normalized Average |  |  | 100 | 100 | 100
NY | 27 | Lennox | 14HPX042 | 1909G01225 | CBX27 04042 | 1 | 2 | 15 | 12.5 | 3.6 | [5 empty] | 5175 | Residential | Split system. Includes air handler. | NY | 36 | CARRIER | 1 | 2 | 17.9 | 3.875 | 13 |  | 7866.4402 | 7810.7884 |  |  | 0 |  | 17550 | 2015.6873 | Interview # | Total Equipment Cost ($) | Total Project Cost ($) | % of Total
NY | 28 | ARMSTRONG | 4SHP14LE148P |  |  | 1 | 2 | 15 | 12.5 | 4 | [5 empty] | 9525 | Residential | Split system. | NY | 38 | CARRIER | 1 | 2 | 18.3 | 3.9583 | 13.5 |  | 7844.0287 | 7788.5354 |  |  | 0 |  | 17500 | 1967.63 | 1 | 4000 | 6500 | 0.61538 |  |  | City Cost Index number is a percentage ratio of a specific city’s cost to the national average cost of the same item at a stated time period.
NY | 29 | LENNOX | XP14-042-230 |  |  | 1 | 2 | 15 | 13 | 3.6 | [5 empty] | 10415 | Residential | Split system | [17 empty] | 3 | 4000 | 10500 | 0.38095
NY | 30 | MAYTAG | PSH4BF048KA |  |  | 1 | 2 | 16 | 12.5 | 4 | [5 empty] | 7800 | Residential | Split system. | [17 empty] | 11 | 3510 | 9100 | 0.38571
NY | 31 | LENNOX | 14HPX-060-230 |  |  | 1 | 2 | 15 | 12.5 | 4.9167 | [5 empty] | 8850 | Residential | Split system | [17 empty] | 11 | 3780 | 9200 | 0.41087
NY | 32 | COLEMAN | HC8B048F1 |  |  | 1 | 2 | 17 | 12.5 | 3.9167 | [5 empty] | 12654 | Residential | Split system. | [19 empty] | Average: | 0.44823
NY | 33 | LENNOX | XP14-042-230 |  |  | 1 | 2 | 15.5 | 13 | 3.625 | [5 empty] | 3400 | Residential | $4100 extra for air handler | [23 empty] | Market | Market Code | Example | Material Adjustment Factor | Labor Adjustment Factor | Total
NY | 34 | TEMPSTAR | T4H442GKD |  |  | 1 | 2 | 15.5 | 13 | 3.5 | [5 empty] | 6500 | Residential | split | [23 empty] | Northern New England | 1 | ME, VT, NH | 0.97583 | 0.81533 | 0.90417
NY | 35 | TRANE | 4TWR5061 |  |  | 1 | 2 | 15 | 12.5 | 4.7917 | [5 empty] | 6850 | Residential | split | [23 empty] | Central/Southern New England | 2 | MA exc Boston, RI, most CT | 0.9836 | 1.1632 | 1.0628
NY | 36 | CARRIER | 25VNA048A300 |  |  | 1 | 2 | 17.9 | 13 | 3.875 | [5 empty] | 17550 | Residential | split | [23 empty] | New England City | 3 | Boston, Providence | 1.008 | 1.2795 | 1.1275
NY | 37 | BRYANT | 226ANA048 |  |  | 1 | 2 | 16 | 12.5 | 3.9167 | [5 empty] | 49065 | Residential | Split | [23 empty] | NY Metro | 4 | NYC, metro suburbs Southwest CT | 1.0278 | 1.5593 | 1.262
NY | 38 | CARRIER | 25VNACM8A003 |  |  | 1 | 2 | 18.3 | 13.5 | 3.9583 | [5 empty] | 17500 | Residential | Split | [23 empty] | NY Upstate | 5 | Buffalo, Rochester etc. | 0.9865 | 1.0135 | 0.99825
[42 empty] | Mid-Atlantic | 6 | MD, DE DC | 0.99275 | 0.88775 | 0.94625
[42 empty] | Geographically Normalized Average | - | - | 1 | 1 | 1
[43 empty] | Raw Data Regions | Material Adjustment Factor | Labor Adjustment Factor | Average Adjustment Factor
[43 empty] | MA | 0.9958 | 1.2213 | 1.1086
[43 empty] | CT | 1.0057 | 1.3612 | 1.1835
[43 empty] | Base Cost Factor | 1 | 1 | 1
[43 empty] | NH | 0.97583 | 0.81533 | 0.89558
[43 empty] | NY | 1.0071 | 1.2864 | 1.1467
[43 empty] | VT | 0.97583 | 0.81533 | 0.89558
[43 empty] | MD | 0.99275 | 0.88775 | 0.94025
[43 empty] | RI | 0.9958 | 1.2213 | 1.1086
Note on G6: Steven Nguyen: 1 < 65,000 65,000 >= 2 > 135,000 135,000 >= 3 > 240,000 240,000 >= 4 > 760,000
Note on H6: Heather Lisle: 0 = Baseline 1 = CEE Tier 1 2 = CEE Tier 2
Note on X6: Heather Lisle: 1 < 65,000 65,000 >= 2 > 135,000 135,000 >= 3 > 240,000 240,000 >= 4 > 760,000
Note on AI7: Steven Nguyen: Does not change between base and efficient.
Note on K9: Steven Nguyen: 6(CONDENSER), 5(EVAPORATOR)
Note on AD9: Steven Nguyen: Lower end of size range. Higher end is estimated at 15% increase. Averaged for unit in middle of size range.
Note on AF9: Steven Nguyen: $1200 for Ducting and $1000 for backup heat
Note on AG9: Steven Nguyen: Includes 20% Markup
Note on A18: Steven Nguyen: New York City
Note on M21: Steven Nguyen: Lower end of size range. Higher end is estimated at 15% increase. Averaged for unit in middle of size range.
Note on N21: Steven Nguyen: $1200 for Ducting and $1000 for backup heat
Note on O21: Steven Nguyen: Includes 20% Markup
Note on Q21: Steven Nguyen: Does not include other material costs.
Note on P26: Steven Nguyen: Does not change between base and efficient.
Note on R29: Steven Nguyen: Residential data was not used in the analysis.
Note on AA29: Steven Nguyen: 6(CONDENSER), 5(EVAPORATOR)

## CEE Criteria
Consortium for Energy Efficiency (CEE) High Efficiency Commercial Air Conditioning and Heat Pump (HECAC) Initiative | Date Published
http://library.cee1.org/sites/default/files/library/5347/CEE_CommHVAC_HECAC__InitDescip.pdf | 2012-01-06

## Baseline
Source: http://publicecodes.cyberregs.com/icod/iecc/2012/icod_iecc_2012_ce4_sec003.htm
IECC 2012
TABLE C403.2.3(2) MINIMUM EFFICIENCY REQUIREMENTS: ELECTRICALLY OPERATED UNITARY AND APPLIED HEAT PUMPS
EQUIPMENT TYPE | SIZE CATEGORY | HEATING SECTION TYPE | SUBCATEGORY OR | MINIMUM | TEST PROCEDUREa
|  |  | RATING CONDITION | EFFICIENCY
Air cooled | < 65,000 Btu/hb | All | Split System | 13.0 SEER | AHRI2
(cooling mode) |  |  | Single Packaged | 13.0 SEER | 10/240
Air cooled | ≥ 65,000 Btu/h and | Electric Resistance | Split System and | 11.0 EER | AHRI
(cooling mode) | < 135,000 Btu/h | (or None) | Single Package | 11.2 IEER | 340/360
|  | All other | Split System and | 10.8 EER
|  |  | Single Package | 11.0 IEER
| ≥ 135,000 Btu/h and | Electric Resistance | Split System and | 10.6 EER
| < 240,000 Btu/h | (or None) | Single Package | 10.7 IEER
|  | All other | Split System and | 10.4 EER
|  |  | Single Package | 10.5 IEER
| ≥ 240,000 Btu/h | Electric Resistance(or None) | Split System and | 9.5 EER
|  |  | Single Package | 9.6 IEER
|  | All other | Split System and | 9.3 EER
|  |  | Single Package | 9.4 IEER
Water source | < 17,000 Btu/h | All | 86oF entering water | 11.2 EER | ISO 13256-1
(cooling mode) | ≥ 17,000 Btu/h and | All | 86oF entering water | 12.0 EER
< 65,000 Btu/h
| ≥ 65,000 Btu/h and | All | 86oF entering water | 12.0 EER
< 135,000 Btu/h
Air cooled | < 65,000 Btu/hb | — | Split System | 7.7 HSPF | AHRI
(heating mode) |  | — | Single Package | 7.7 HSPF | 210/240
TABLE C403.2.3(2)—continued MINIMUM EFFICIENCY REQUIREMENTS: ELECTRICALLY OPERATED UNITARY AND APPLIED HEAT PUMPS
EQUIPMENT TYPE | SIZE CATEGORY | HEATING SECTION TYPE | SUB-CATEGORY OR | MINIMUM | TEST PROCEDUREa
|  |  | RATING CONDITION | EFFICIENCY
Air cooled | ≥ 65,000 Btu/h and | — | 47ºF db/43ºF wb | 3.3 COP | AHRI
(heating mode) | < 135,000 Btu/h |  | Outdoor Air |  | 340/360
| (cooling capacity) |  | 17ºF db/15ºF wb | 2.25 COP
Outdoor Air
| ≥ 135,000 Btu/h | — | 47ºF db/43ºF wb | 3.2 COP
| (cooling capacity) |  | Outdoor Air
|  |  | 17ºF db/15ºF wb | 2.05 COP
Outdoor Air