## Chiller EFLH (hidden)
|  | Amarillo | Fort Worth | Houston | Brownsville | El Paso | Average Texas | Dover, DE | Wilmington, DE | Baltimore, MD | Hagerstown, MD | Patuxent River, MD | Salisbury, MD | Washington D.C.
Building Type | Principal Building Activity | Air Cooled Chillers
Education | College | 1115 | 1587 | 1858 | 2340 | 1278 | 1635.6 | 627.0487 | 708.234 | 799.0395 | 688.2063 | 905.2158 | 811.7516 | 704.0684
| Primary School | 576 | 726 | 818 | 937 | 751 | 761.6 | 291.9787 | 329.7818 | 372.0644 | 320.456 | 421.5042 | 377.9836 | 327.8421
| Secondary School | 802 | 1170 | 1297 | 1503 | 1039 | 1162.2 | 445.5588 | 503.2463 | 567.7694 | 489.0152 | 643.2146 | 576.8022 | 500.2863
Healthcare | Hospital | 2006 | 2784 | 3116 | 3455 | 2355 | 2743.2 | 1051.6752 | 1187.8379 | 1340.1352 | 1154.2476 | 1518.2122 | 1361.4558 | 1180.8513
Large Multifamily | Midrise Apartment | 421 | 1060 | 1295 | 1534 | 841 | 1030.2 | 394.9533 | 446.0887 | 503.2835 | 433.474 | 570.1598 | 511.2904 | 443.4649
Lodging | Large Hotel | 1283 | 2086 | 2499 | 2908 | 1815 | 2118.2 | 812.0656 | 917.2055 | 1034.804 | 891.2684 | 1172.3087 | 1051.267 | 911.8107
| Nursing Home | 428 | 1077 | 1315 | 1558 | 854 | 1046.4 | 401.1639 | 453.1035 | 511.1977 | 440.2904 | 579.1256 | 519.3305 | 450.4385
Mercantile | Stand-Alone Retail | 489 | 936 | 1224 | 1394 | 722 | 953 | 365.3567 | 412.6602 | 465.569 | 400.9908 | 527.4338 | 472.9758 | 410.233
Office | Large Office | 1208 | 1711 | 1820 | 2027 | 1442 | 1641.6 | 629.3489 | 710.8321 | 801.9707 | 690.7309 | 908.5365 | 814.7294 | 706.6512
Public Assembly | Public Assembly | 774 | 976 | 1100 | 1260 | 1010 | 1024 | 392.5763 | 443.404 | 500.2546 | 430.8653 | 566.7284 | 508.2133 | 440.7961
Religious Worship | Religious Worship | 294 | 563 | 737 | 839 | 435 | 573.6 | 219.9041 | 248.3755 | 280.2207 | 241.3519 | 317.4565 | 284.6789 | 246.9147
Other | Other | 256 | 410 | 514 | 601 | 391 | 434.4 | 166.5382 | 188.1003 | 212.2174 | 182.7811 | 240.4168 | 215.5936 | 186.994
|  | Amarillo | Fort Worth | Houston | Brownsville | El Paso | Average Texas | Dover, DE | Wilmington, DE | Baltimore, MD | Hagerstown, MD | Patuxent River, MD | Salisbury, MD | Washington D.C.
Building Type | Principal Building Activity | Air Cooled Chillers
Education | College | 1243 | 1761 | 2099 | 2583 | 1458 | 1828.8 | 701.1168 | 791.8919 | 893.4235 | 769.4984 | 1012.1415 | 907.6372 | 787.2342
| Primary School | 971 | 1412 | 1627 | 1845 | 1113 | 1393.6 | 534.2719 | 603.4452 | 680.8153 | 586.3807 | 771.2819 | 691.6465 | 599.8959
| Secondary School | 1772 | 2234 | 1726 | 2577 | 2196 | 2101 | 805.4716 | 909.7577 | 1026.4013 | 884.0312 | 1162.7894 | 1042.7306 | 904.4068
Healthcare | Hospital | 2711 | 3683 | 4171 | 4637 | 2992 | 3638.8 | 1395.0262 | 1575.6432 | 1777.6626 | 1531.0864 | 2013.8782 | 1805.9439 | 1566.3757
Large Multifamily | Midrise Apartment | 1098 | 2053 | 2467 | 2840 | 1553 | 2002.2 | 767.5941 | 866.9761 | 978.1346 | 842.4594 | 1108.109 | 993.6959 | 861.8768
Lodging | Large Hotel | 1553 | 2627 | 3201 | 3713 | 2038 | 2626.4 | 1006.897 | 1137.2621 | 1283.0749 | 1105.1021 | 1453.5698 | 1303.4877 | 1130.573
| Nursing Home | 1115 | 2085 | 2506 | 2884 | 1577 | 2033.4 | 779.5554 | 880.4861 | 993.3767 | 855.5873 | 1125.3765 | 1009.1806 | 875.3073
Mercantile | Stand-Alone Retail | 719 | 1328 | 1712 | 1953 | 948 | 1332 | 510.6559 | 576.7717 | 650.7218 | 560.4615 | 737.1897 | 661.0743 | 573.3792
Office | Large Office | 1506 | 2062 | 2312 | 2570 | 1683 | 2026.6 | 776.9485 | 877.5416 | 990.0547 | 852.7261 | 1121.6131 | 1005.8057 | 872.3802
Public Assembly | Public Assembly | 1306 | 1898 | 2188 | 2481 | 1496 | 1873.8 | 718.3687 | 811.3774 | 915.4073 | 788.4329 | 1037.0466 | 929.9708 | 806.6051
Religious Worship | Religious Worship | 433 | 799 | 1031 | 1176 | 571 | 802 | 307.467 | 347.2754 | 391.801 | 337.455 | 443.8635 | 398.0342 | 345.2328
Other | Other | 668 | 1136 | 1440 | 1663 | 894 | 1160.2 | 444.7921 | 502.3802 | 566.7924 | 488.1737 | 642.1077 | 575.8096 | 499.4254
| CDD | 1347.915 | 2570.235 | 2801.7 | 3661.62 | 2236.028 | 2523.4996 | 967.4475 | 1092.705 | 1232.805 | 1061.805 | 1396.62 | 1252.418 | 1086.278

## M-A TRM V6
Source: MID-ATLANTIC TECHNICAL REFERENCE MANUAL VERSION 6.0 April 2017
Unitary HVAC Systems, Gas Boiler, Gas Furnace
Full Load Cooling Hours by Location and Equipment Capacity
City, State | HOURSCool by Equipment Capacity
| < 135 kBtu/h | >= 135 kBtu/h
Dover, DE | 910 | 1636
Wilmington, DE | 980 | 1762
Baltimore, MD | 1014 | 1823
Hagerstown, MD | 885 | 1591
Patuxent River, MD | 1151 | 2069
Salisbury, MD | 1008 | 1812
Washington D.C. | 1275 | 2292
[1] Full load cooling hours estimated by adjusting the “Mid-Atlantic” hours from “C&I Unitary HVAC Load Shape Project Final Report, KEMA, 2011” by the full-load cooling hour estimates from the ENERGY STAR Central AC Calculator, 2013. For scaling purposes, the analysis assumes the initial Mid-Atlantic values are consistent with Baltimore, MD as suggested by the KEMA study. Because the ENERGY STAR calculator does not provide full load hours estimates for all cities of interest, a second scaling was performed using cooling degree day estimates from Typical Meteorological Year 3 (TMY3) data published by the National Renewable Energy Laboratory.
Full Load Heating Hours by Location and Building Type
Building Type | Dover, DE | Wilmington, DE | Baltimore, MD | Hagerstown, MD | Patuxent River, MD | Salisbury, MD | Washington D.C.
Assembly | 676 | 692 | 620 | 657 | 451 | 507 | 559
Auto Repair | 2292 | 2344 | 2106 | 2229 | 1543 | 1728 | 1901
Big Box Retail | 286 | 298 | 241 | 271 | 107 | 151 | 192
Fast Food Restaurant | 957 | 983 | 866 | 926 | 590 | 681 | 766
Full Service Restaurant | 988 | 1016 | 891 | 956 | 597 | 694 | 784
Grocery | 286 | 298 | 241 | 271 | 107 | 151 | 192
Light Industrial | 867 | 885 | 803 | 845 | 608 | 672 | 732
Motel | 659 | 667 | 632 | 650 | 547 | 575 | 601
Primary School | 978 | 993 | 926 | 960 | 767 | 819 | 868
Religious Worship | 750 | 754 | 737 | 746 | 698 | 711 | 723
Small Office | 511 | 524 | 466 | 496 | 329 | 374 | 416
Small Retail | 657 | 674 | 595 | 636 | 410 | 471 | 528
Warehouse | 556 | 576 | 487 | 533 | 278 | 347 | 411
Other | 805 | 823 | 739 | 783 | 541 | 606 | 667
[1] HOURS estimates developed from data presented in "New York Standard Approach for Estimating Energy Savings from Energy Efficiency Programs", TecMarket Works, October 15, 2010, adjusted to Mid-Atlantic region using heating degree day estimates from Typical Meteorological Year 3 (TMY3) data published by the National Renewable Energy Laboratory.
Electric Chillers
Default Electric Chiller Full Load Cooling Hours
| System Typea | Dover, DE | Wilmington, DE | Baltimore, MD | Hagerstown, MD | Patuxent River, MD | Salisbury, MD | Washington D.C.
Building Type
Community College | CAV w/o economizer | 1010 | 1048 | 1121 | 1044 | 1202 | 1117 | 1274
Community College | CAV w/ economizer | 752 | 781 | 836 | 777 | 897 | 833 | 952
Community College | VAV w/ economizer | 585 | 607 | 649 | 605 | 695 | 647 | 736
High School | CAV w/o economizer | 819 | 830 | 851 | 829 | 875 | 850 | 896
High School | CAV w/ economizer | 428 | 440 | 463 | 439 | 489 | 462 | 511
High School | VAV w/ economizer | 306 | 316 | 336 | 315 | 359 | 335 | 379
Hospital | CAV w/o economizer | 2094 | 2135 | 2213 | 2130 | 2302 | 2210 | 2379
Hospital | CAV w/ economizer | 1307 | 1341 | 1406 | 1338 | 1479 | 1403 | 1543
Hospital | VAV w/ economizer | 1142 | 1165 | 1208 | 1162 | 1257 | 1206 | 1300
Hotel | CAV w/o economizer | 3166 | 3165 | 3163 | 3165 | 3161 | 3163 | 3159
Hotel | CAV w/ economizer | 2972 | 2972 | 2971 | 2972 | 2971 | 2971 | 2971
Hotel | VAV w/ economizer | 2953 | 2958 | 2967 | 2957 | 2977 | 2966 | 2986
Large Retail | CAV w/o economizer | 1719 | 1730 | 1750 | 1729 | 1772 | 1749 | 1792
Large Retail | CAV w/ economizer | 987 | 1011 | 1057 | 1009 | 1109 | 1055 | 1155
Large Retail | VAV w/ economizer | 817 | 838 | 877 | 835 | 921 | 875 | 959
Office Building | CAV w/o economizer | 2162 | 2193 | 2252 | 2189 | 2318 | 2249 | 2377
Office Building | CAV w/ economizer | 700 | 710 | 729 | 709 | 750 | 728 | 768
Office Building | VAV w/ economizer | 670 | 685 | 716 | 684 | 749 | 714 | 779
University | CAV w/o economizer | 1103 | 1135 | 1198 | 1132 | 1267 | 1194 | 1329
University | CAV w/ economizer | 796 | 822 | 871 | 819 | 925 | 868 | 974
University | VAV w/ economizer | 626 | 645 | 682 | 643 | 724 | 680 | 760
[1] HOURS estimates developed from data presented in "New York Standard Approach for Estimating Energy Savings from Energy Efficiency Programs", TecMarket Works, October 15, 2010, adjusted to Mid-Atlantic region using cooling degree day estimates from Typical Meteorological Year 3 (TMY3) data published by the National Renewable Energy Laboratory.

## Pennsylvania TRM
Source: TECHNICAL REFERENCE MANUAL, State of Pennsylvania Act 129 Energy Efficiency and Conservation Program & Act 213 Alternative Energy Portfolio Standards, June 2016
Table 3‑25: Air Conditioning EFLHs for Pennsylvania Cities
Space and/or Building Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport
Assembly | 753 | 607 | 820 | 1087 | 706 | 629 | 685
Education - Community College | 603 | 436 | 620 | 695 | 557 | 515 | 594
Education - Primary School | 250 | 154 | 277 | 302 | 255 | 204 | 208
Education - Relocatable Classroom | 301 | 198 | 326 | 359 | 303 | 229 | 246
Education - Secondary School | 249 | 204 | 327 | 375 | 262 | 219 | 264
Education - University | 677 | 520 | 693 | 773 | 630 | 550 | 595
Grocery | 654 | 636 | 453 | 536 | 638 | 434 | 442
Health/Medical - Hospital | 1030 | 1038 | 892 | 1059 | 788 | 1022 | 1013
Health/Medical - Nursing Home | 477 | 481 | 540 | 684 | 511 | 467 | 476
Lodging - Hotel | 1386 | 1392 | 1523 | 1732 | 1478 | 1348 | 1384
Manufacturing – Bio Tech/High Tech | 785 | 548 | 766 | 858 | 710 | 594 | 627
Manufacturing – 1 Shift/Light Industrial | 355 | 274 | 465 | 506 | 349 | 296 | 329
Multi-Family (Common Areas)[1] | 1395 | 769 | 1482 | 1647 | 1176 | 991 | 1052
Office - Large | 480 | 433 | 601 | 754 | 749 | 595 | 490
Office - Small | 435 | 391 | 529 | 653 | 692 | 404 | 442
Restaurant - Fast-Food | 545 | 478 | 574 | 790 | 602 | 524 | 569
Restaurant - Sit-Down | 555 | 548 | 605 | 791 | 662 | 519 | 618
Retail - Multistory Large | 763 | 595 | 803 | 807 | 673 | 629 | 694
Retail - Single-Story Large | 747 | 574 | 771 | 988 | 738 | 640 | 642
Retail - Small | 695 | 692 | 652 | 938 | 1036 | 541 | 608
Storage - Conditioned | 174 | 114 | 235 | 346 | 192 | 130 | 178
Warehouse - Refrigerated | 3130 | 3080 | 3163 | 3200 | 3116 | 3094 | 3135
[1] US Department of Energy. Energy Star Calculator and Bin Analysis Models. The Equivalent Full Load Hours (ELFH) for Pennsylvania are calculated based on the degree day scaling methodology. The EFLH values reported in the Connecticut Program Savings Documentation were adjusted using full load hours (FLH) from the US DOE ENERGY STAR Calculator to account for differences in weather conditions.
Table 3‑27: Heat Pump EFLHs for Pennsylvania Cities, NOTE: These are heating full load hours. Cooling EFLHs for HPs are equal to AC EFLHs above
Space and/or Building Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport
Assembly | 1178 | 1437 | 1098 | 1121 | 1163 | 1401 | 1066
Education - Community College | 816 | 966 | 620 | 521 | 734 | 977 | 783
Education - Primary School | 795 | 830 | 651 | 557 | 819 | 879 | 543
Education - Relocatable Classroom | 360 | 165 | 863 | 726 | 1056 | 1003 | 745
Education - Secondary School | 752 | 1002 | 710 | 654 | 776 | 893 | 677
Education - University | 621 | 748 | 483 | 407 | 567 | 670 | 527
Grocery | 733 | 534 | 1269 | 1217 | 564 | 1737 | 1419
Health/Medical - Hospital | 147 | 95 | 361 | 345 | 418 | 106 | 154
Health/Medical - Nursing Home | 944 | 1304 | 854 | 805 | 1023 | 1193 | 958
Lodging - Hotel | 2371 | 3077 | 2159 | 2017 | 2411 | 2591 | 2403
Manufacturing - Bio Tech/High Tech | 178 | 193 | 138 | 111 | 172 | 176 | 141
Manufacturing – 1 Shift/Light Industrial | 633 | 752 | 609 | 567 | 627 | 705 | 550
Multi-Family (Common Areas)[1] | 277 | 322 | 263 | 259 | 264 | 281 | 278
Office - Large | 218 | 292 | 230 | 22 | 30 | 176 | 231
Office - Small | 423 | 551 | 430 | 38 | 62 | 481 | 448
Restaurant - Fast-Food | 1227 | 1627 | 1112 | 1078 | 1363 | 1612 | 1295
Restaurant - Sit-Down | 1074 | 1747 | 968 | 908 | 1316 | 1390 | 1187
Retail - Multistory Large | 687 | 828 | 582 | 447 | 620 | 736 | 587
Retail - Single-Story Large | 791 | 979 | 674 | 735 | 849 | 929 | 654
Retail - Small | 949 | 1133 | 689 | 109 | 164 | 900 | 785
Storage - Conditioned | 847 | 1114 | 843 | 900 | 978 | 1008 | 800
Warehouse - Refrigerated | 363 | 534 | 307 | 222 | 409 | 439 | 328
[1] US Department of Energy. Energy Star Calculator and Bin Analysis Models. The Equivalent Full Load Hours (ELFH) for Pennsylvania are calculated based on the degree day scaling methodology. The EFLH values reported in the Connecticut Program Savings Documentation were adjusted using full load hours (FLH) from the US DOE ENERGY STAR Calculator to account for differences in weather conditions.
Table 3‑30: Chiller EFLHs for Pennsylvania Cities
Space and/or Building Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport
Education - Community College | 634 | 453 | 661 | 734 | 564 | 502 | 608
Education - Secondary School | 275 | 214 | 344 | 389 | 282 | 244 | 316
Education - University | 695 | 526 | 730 | 805 | 635 | 545 | 629
Health/Medical - Hospital | 1240 | 1100 | 1362 | 1556 | 1185 | 1134 | 1208
Health/Medical - Nursing Home | 459 | 408 | 520 | 622 | 472 | 418 | 462
Lodging - Hotel | 1397 | 1317 | 1511 | 1654 | 1432 | 1352 | 1415
Manufacturing – Bio Tech/High Tech | 708 | 527 | 700 | 780 | 631 | 574 | 614
Office - Large | 463 | 411 | 546 | 604 | 451 | 427 | 472
Office - Small | 429 | 374 | 495 | 567 | 434 | 393 | 433
Retail - Multistory Large | 749 | 609 | 836 | 897 | 699 | 659 | 742

## M-A Cooling AC EFLH Update
Revised Mid-Atlantic TRM EFLH Cooling, AC
Space and/or Building Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | PA AVERAGE | Dover, DE | Wilmington, DE | Baltimore, MD | Hagerstown, MD | Patuxent River, MD | Salisbury, MD | Washington D.C.
Assembly | 753 | 607 | 820 | 1087 | 706 | 629 | 685 | 755.2857 | 937.3035 | 922.3712 | 944.9064 | 860.8195 | 1102.8264 | 908.558 | 1143.4708
Education - Community College | 603 | 436 | 620 | 695 | 557 | 515 | 594 | 574.2857 | 712.6839 | 701.3301 | 718.4649 | 654.5289 | 838.5402 | 690.8271 | 869.4444
Education - Primary School | 250 | 154 | 277 | 302 | 255 | 204 | 208 | 235.7143 | 292.5195 | 287.8594 | 294.8923 | 268.6499 | 344.177 | 283.5484 | 356.8615
Education - Relocatable Classroom | 301 | 198 | 326 | 359 | 303 | 229 | 246 | 280.2857 | 347.8323 | 342.291 | 350.6538 | 319.4492 | 409.2577 | 337.1649 | 424.3408
Education - Secondary School | 249 | 204 | 327 | 375 | 262 | 219 | 264 | 271.4286 | 336.8407 | 331.4744 | 339.573 | 309.3545 | 396.325 | 326.5103 | 410.9314
Education - University | 677 | 520 | 693 | 773 | 630 | 550 | 595 | 634 | 786.7889 | 774.2545 | 793.1709 | 722.5869 | 925.7317 | 762.6594 | 959.8493
Grocery | 654 | 636 | 453 | 536 | 638 | 434 | 442 | 541.8571 | 672.4403 | 661.7276 | 677.8948 | 617.5692 | 791.1898 | 651.8177 | 820.3489
Health/Medical - Hospital | 1030 | 1038 | 892 | 1059 | 788 | 1022 | 1013 | 977.4286 | 1212.9809 | 1193.6569 | 1222.8201 | 1114.0017 | 1427.1872 | 1175.7809 | 1479.7857
Health/Medical - Nursing Home | 477 | 481 | 540 | 684 | 511 | 467 | 476 | 519.4286 | 644.6066 | 634.3374 | 649.8354 | 592.0067 | 758.4409 | 624.8377 | 786.393
Lodging - Hotel | 1386 | 1392 | 1523 | 1732 | 1478 | 1348 | 1384 | 1463.2857 | 1815.9257 | 1786.9961 | 1830.6557 | 1667.7462 | 2136.6089 | 1760.2344 | 2215.3529
Manufacturing – Bio Tech/High Tech | 785 | 548 | 766 | 858 | 710 | 594 | 627 | 698.2857 | 866.5669 | 852.7616 | 873.5961 | 795.8551 | 1019.5982 | 839.9908 | 1057.1752
Manufacturing – 1 Shift/Light Industrial | 355 | 274 | 465 | 506 | 349 | 296 | 329 | 367.7143 | 456.3304 | 449.0606 | 460.032 | 419.0939 | 536.9161 | 442.3356 | 556.7039
Multi-Family (Common Areas)[1] | 1395 | 769 | 1482 | 1647 | 1176 | 991 | 1052 | 1216 | 1509.0461 | 1485.0054 | 1521.2868 | 1385.908 | 1775.536 | 1462.7663 | 1840.9728
Office - Large | 480 | 433 | 601 | 754 | 749 | 595 | 490 | 586 | 727.2213 | 715.6358 | 733.1201 | 667.88 | 855.6448 | 704.9186 | 887.1793
Office - Small | 435 | 391 | 529 | 653 | 692 | 404 | 442 | 506.5714 | 628.651 | 618.636 | 633.7504 | 577.3531 | 739.6676 | 609.3714 | 766.9278
Restaurant - Fast-Food | 545 | 478 | 574 | 790 | 602 | 524 | 569 | 583.1429 | 723.6756 | 712.1466 | 729.5457 | 664.6236 | 851.473 | 701.4817 | 882.8537
Restaurant - Sit-Down | 555 | 548 | 605 | 791 | 662 | 519 | 618 | 614 | 761.969 | 749.83 | 768.1498 | 699.7924 | 896.5288 | 738.6007 | 929.5701
Retail - Multistory Large | 763 | 595 | 803 | 807 | 673 | 629 | 694 | 709.1429 | 880.0405 | 866.0206 | 887.179 | 808.2292 | 1035.4512 | 853.0512 | 1073.6124
Retail - Single-Story Large | 747 | 574 | 771 | 988 | 738 | 640 | 642 | 728.5714 | 904.1512 | 889.7472 | 911.4853 | 830.3725 | 1063.8197 | 876.4225 | 1103.0265
Retail - Small | 695 | 692 | 652 | 938 | 1036 | 541 | 608 | 737.4286 | 915.1429 | 900.5637 | 922.5661 | 840.4672 | 1076.7524 | 887.077 | 1116.4358
Storage - Conditioned | 174 | 114 | 235 | 346 | 192 | 130 | 178 | 195.5714 | 242.7026 | 238.836 | 244.6712 | 222.898 | 285.5626 | 235.2593 | 296.0869
Warehouse - Refrigerated | 3130 | 3080 | 3163 | 3200 | 3116 | 3094 | 3135 | 3131.1429 | 3885.7229 | 3823.8192 | 3917.2421 | 3568.6479 | 4571.9217 | 3766.5545 | 4740.4184
HDD (Base 65F) | 5552 | 6080 | 5046 | 4512 | 5583 | 6086 | 5850 | 5529.8571 | 4503 | 4756 | 4552 | 4953 | 4068 | 4363 | 3996
Design Temp Heating DB 99% | 12.6 | 10.4 | 15.6 | 18 | 9.9 | 9.1 | 10.3 | 12.2714 | 18.4 | 17.3 | 17.9 | 16.1 | 20.9 | 18.4 | 20.7
CDD (Base 65F) | 838 | 659 | 1110 | 1332 | 782 | 637 | 751 | 872.7143 | 1170 | 1142 | 1261 | 1092 | 1399 | 1171 | 1555
Design Temp Cooling DB 1% | 88.3 | 84.2 | 89.7 | 90.8 | 87 | 86.2 | 88.2 | 87.7714 | 89.6 | 89.4 | 91.3 | 90 | 90 | 90.4 | 91.8
Source: 2013 ASHRAE Handbook - Fundamentals (IP)
Cadmus ACEEE Paper Calculation (EFLHcool) | 863.176 | 823.75 | 1078.5425 | 1239.0698 | 853.0909 | 721.1321 | 776.8966 | 919.7992 | 1141.4634 | 1123.2787 | 1150.7224 | 1048.32 | 1343.04 | 1106.4567 | 1392.5373
Source: Korn, D. and J. Walczyk. 2016. "Exactly What Is a Full Load Cooling Hour and Does Size Really Matter?" Proceedings of the 2016 ACEEE Summer Study on Energy Efficiency in Buildings.
Note on E16: kbrander: value listed in the TRM appears to have a typo, added a 5 to the end to make numbers more reasonable
Note on F16: kbrander: value listed in the TRM appears to have a typo, added a 5 to the end to make numbers more reasonable
Note on E17: kbrander: value listed in the TRM appears to have a typo, added a 5 to the end to make numbers more reasonable
Note on F17: kbrander:

## M-A Heating HP EFLH Update
Revised Mid-Atlantic TRM EFLH Heating, HP
Space and/or Building Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | PA AVERAGE | Dover, DE | Wilmington, DE | Baltimore, MD | Hagerstown, MD | Patuxent River, MD | Salisbury, MD | Washington D.C.
Assembly | 1178 | 1437 | 1098 | 1121 | 1163 | 1401 | 1066 | 1209.1429 | 1114.104 | 1149.5641 | 1114.2716 | 1167.8019 | 1063.5357 | 1079.4661 | 1039.9955
Education - Community College | 816 | 966 | 620 | 521 | 734 | 977 | 783 | 773.8571 | 713.0318 | 735.7264 | 713.1391 | 747.3987 | 680.6679 | 690.8634 | 665.602
Education - Primary School | 795 | 830 | 651 | 557 | 819 | 879 | 543 | 724.8571 | 667.8832 | 689.1408 | 667.9837 | 700.0741 | 637.5685 | 647.1185 | 623.4567
Education - Relocatable Classroom | 360 | 165 | 863 | 726 | 1056 | 1003 | 745 | 702.5714 | 647.3492 | 667.9532 | 647.4466 | 678.5503 | 617.9665 | 627.2229 | 604.2885
Education - Secondary School | 752 | 1002 | 710 | 654 | 776 | 893 | 677 | 780.5714 | 719.2184 | 742.1099 | 719.3265 | 753.8835 | 686.5736 | 696.8576 | 671.3771
Education - University | 621 | 748 | 483 | 407 | 567 | 670 | 527 | 574.7143 | 529.5416 | 546.3961 | 529.6213 | 555.0646 | 505.5061 | 513.078 | 494.3173
Grocery | 733 | 534 | 1269 | 1217 | 564 | 1737 | 1419 | 1067.5714 | 983.6601 | 1014.9684 | 983.8081 | 1031.0708 | 939.0125 | 953.0778 | 918.2285
Health/Medical - Hospital | 147 | 95 | 361 | 345 | 418 | 106 | 154 | 232.2857 | 214.028 | 220.8402 | 214.0602 | 224.3438 | 204.3134 | 207.3738 | 199.7912
Health/Medical - Nursing Home | 944 | 1304 | 854 | 805 | 1023 | 1193 | 958 | 1011.5714 | 932.0617 | 961.7277 | 932.2019 | 976.9855 | 889.7562 | 903.0836 | 870.0624
Lodging - Hotel | 2371 | 3077 | 2159 | 2017 | 2411 | 2591 | 2403 | 2432.7143 | 2241.5025 | 2312.8457 | 2241.8396 | 2349.5391 | 2139.7624 | 2171.8133 | 2092.4012
Manufacturing – Bio Tech/High Tech | 178 | 193 | 138 | 111 | 172 | 176 | 141 | 158.4286 | 145.9761 | 150.6222 | 145.998 | 153.0119 | 139.3503 | 141.4376 | 136.266
Manufacturing – 1 Shift/Light Industrial | 633 | 752 | 609 | 567 | 627 | 705 | 550 | 634.7143 | 584.8256 | 603.4396 | 584.9136 | 613.0132 | 558.2808 | 566.6432 | 545.9239
Multi-Family (Common Areas)[1] | 277 | 322 | 263 | 259 | 264 | 281 | 278 | 277.7143 | 255.8859 | 264.0303 | 255.9244 | 268.2192 | 244.2714 | 247.9303 | 238.8648
Office - Large | 218 | 292 | 230 | 225 | 305 | 176 | 231 | 239.5714 | 220.7411 | 227.7669 | 220.7743 | 231.3804 | 210.7218 | 213.8781 | 206.0577
Office - Small | 423 | 551 | 430 | 385 | 625 | 481 | 448 | 477.5714 | 440.0342 | 454.0398 | 440.1004 | 461.2431 | 420.0614 | 426.3534 | 410.7638
Restaurant - Fast-Food | 1227 | 1627 | 1112 | 1078 | 1363 | 1612 | 1295 | 1330.5714 | 1225.9883 | 1265.0094 | 1226.1727 | 1285.0788 | 1170.3416 | 1187.8718 | 1144.4374
Restaurant - Sit-Down | 1074 | 1747 | 968 | 908 | 1316 | 1390 | 1187 | 1227.1429 | 1130.6892 | 1166.6771 | 1130.8593 | 1185.1865 | 1079.3681 | 1095.5356 | 1055.4775
Retail - Multistory Large | 687 | 828 | 582 | 447 | 620 | 736 | 587 | 641 | 590.6173 | 609.4156 | 590.7061 | 619.084 | 563.8096 | 572.2548 | 551.3303
Retail - Single-Story Large | 791 | 979 | 674 | 735 | 849 | 929 | 654 | 801.5714 | 738.5678 | 762.0751 | 738.6789 | 774.1655 | 705.0447 | 715.6054 | 689.4394
Retail - Small | 949 | 1133 | 689 | 109 | 164 | 900 | 785 | 675.5714 | 622.4714 | 642.2836 | 622.565 | 652.4734 | 594.2179 | 603.1185 | 581.0655
Storage - Conditioned | 847 | 1114 | 843 | 900 | 978 | 1008 | 800 | 927.1429 | 854.2693 | 881.4592 | 854.3978 | 895.4436 | 815.4946 | 827.7097 | 797.4446
Warehouse - Refrigerated | 363 | 534 | 307 | 222 | 409 | 439 | 328 | 371.7143 | 342.4975 | 353.3986 | 342.549 | 359.0053 | 326.9518 | 331.8491 | 319.7151
HDD (Base 65F) | 5552 | 6080 | 5046 | 4512 | 5583 | 6086 | 5850 | 5529.8571 | 4503 | 4756 | 4552 | 4953 | 4068 | 4363 | 3996
Design Temp Heating DB 99% | 12.6 | 10.4 | 15.6 | 18 | 9.9 | 9.1 | 10.3 | 12.2714 | 18.4 | 17.3 | 17.9 | 16.1 | 20.9 | 18.4 | 20.7
CDD (Base 65F) | 838 | 659 | 1110 | 1332 | 782 | 637 | 751 | 872.7143 | 1170 | 1142 | 1261 | 1092 | 1399 | 1171 | 1555
Design Temp Cooling DB 1% | 88.3 | 84.2 | 89.7 | 90.8 | 87 | 86.2 | 88.2 | 87.7714 | 89.6 | 89.4 | 91.3 | 90 | 90 | 90.4 | 91.8
Source: 2013 ASHRAE Handbook - Fundamentals (IP)
Cadmus ACEEE Paper Calculation (EFLHheat) | 2542.9008 | 2672.5275 | 2451.498 | 2304 | 2431.7967 | 2612.9517 | 2566.7276 | 2516.9764 | 2319.1416 | 2392.956 | 2319.4904 | 2430.9202 | 2213.8776 | 2247.0386 | 2164.8758
Source: Korn, D. and J. Walczyk. 2016. "Exactly What Is a Full Load Cooling Hour and Does Size Really Matter?" Proceedings of the 2016 ACEEE Summer Study on Energy Efficiency in Buildings.
Note on E16: kbrander: value listed in the TRM appears to have a typo, added a 5 to the end to make numbers more reasonable
Note on F16: kbrander: value listed in the TRM appears to have a typo, added a 5 to the end to make numbers more reasonable
Note on E17: kbrander: value listed in the TRM appears to have a typo, added a 5 to the end to make numbers more reasonable
Note on F17: kbrander:

## M-A Cooling Chlr EFLH Update
Revised Mid-Atlantic TRM EFLH Cooling, Chillers
Space and/or Building Type | Allentown | Erie | Harrisburg | Philadelphia | Pittsburgh | Scranton | Williamsport | PA AVERAGE | Dover, DE | Wilmington, DE | Baltimore, MD | Hagerstown, MD | Patuxent River, MD | Salisbury, MD | Washington D.C.
Education - Community College | 634 | 453 | 661 | 734 | 564 | 502 | 608 | 593.7143 | 736.7946 | 725.0567 | 742.7712 | 676.6722 | 866.9088 | 714.1984 | 898.8584
Education - Secondary School | 275 | 214 | 344 | 389 | 282 | 244 | 316 | 294.8571 | 365.9153 | 360.0859 | 368.8835 | 336.0566 | 430.5341 | 354.6933 | 446.4013
Education - University | 695 | 526 | 730 | 805 | 635 | 545 | 629 | 652.1429 | 809.304 | 796.4109 | 815.8687 | 743.2648 | 952.2229 | 784.484 | 987.3168
Health/Medical - Hospital | 1240 | 1100 | 1362 | 1556 | 1185 | 1134 | 1208 | 1255 | 1557.4448 | 1532.6331 | 1570.0781 | 1430.3573 | 1832.4816 | 1509.6807 | 1900.0171
Health/Medical - Nursing Home | 459 | 408 | 520 | 622 | 472 | 418 | 462 | 480.1429 | 595.8534 | 586.3608 | 600.6867 | 547.2318 | 701.0781 | 577.5796 | 726.9161
Lodging - Hotel | 1397 | 1317 | 1511 | 1654 | 1432 | 1352 | 1415 | 1439.7143 | 1786.6738 | 1758.2102 | 1801.1664 | 1640.8812 | 2102.1912 | 1731.8796 | 2179.6668
Manufacturing – Bio Tech/High Tech | 708 | 527 | 700 | 780 | 631 | 574 | 614 | 647.7143 | 803.8082 | 791.0027 | 810.3283 | 738.2174 | 945.7566 | 779.1568 | 980.6121
Office - Large | 463 | 411 | 546 | 604 | 451 | 427 | 472 | 482 | 598.1581 | 588.6288 | 603.0101 | 549.3484 | 703.7897 | 579.8136 | 729.7277
Office - Small | 429 | 374 | 495 | 567 | 434 | 393 | 433 | 446.4286 | 554.0142 | 545.1882 | 558.5081 | 508.8067 | 651.8503 | 537.0236 | 675.8741
Retail - Multistory Large | 749 | 609 | 836 | 897 | 699 | 659 | 742 | 741.5714 | 920.2841 | 905.623 | 927.7491 | 845.189 | 1082.8016 | 892.0606 | 1122.7079
HDD (Base 65F) | 5552 | 6080 | 5046 | 4512 | 5583 | 6086 | 5850 | 5529.8571 | 4503 | 4756 | 4552 | 4953 | 4068 | 4363 | 3996
Design Temp Heating DB 99% | 12.6 | 10.4 | 15.6 | 18 | 9.9 | 9.1 | 10.3 | 12.2714 | 18.4 | 17.3 | 17.9 | 16.1 | 20.9 | 18.4 | 20.7
CDD (Base 65F) | 838 | 659 | 1110 | 1332 | 782 | 637 | 751 | 872.7143 | 1170 | 1142 | 1261 | 1092 | 1399 | 1171 | 1555
Design Temp Cooling DB 1% | 88.3 | 84.2 | 89.7 | 90.8 | 87 | 86.2 | 88.2 | 87.7714 | 89.6 | 89.4 | 91.3 | 90 | 90 | 90.4 | 91.8
Source: 2013 ASHRAE Handbook - Fundamentals (IP)
Cadmus ACEEE Paper Calculation (EFLHcool) | 863.176 | 823.75 | 1078.5425 | 1239.0698 | 853.0909 | 721.1321 | 776.8966 | 919.7992 | 1141.4634 | 1123.2787 | 1150.7224 | 1048.32 | 1343.04 | 1106.4567 | 1392.5373
Source: Korn, D. and J. Walczyk. 2016. "Exactly What Is a Full Load Cooling Hour and Does Size Really Matter?" Proceedings of the 2016 ACEEE Summer Study on Energy Efficiency in Buildings.