## Master Summary
Measure | Itron Recommendations |  |  | TRM Version 6.0 Information |  |  | Itron Background Calculations |  | Notes
| Discussion | EmPOWER Incentive Categories (as of Feb 2017) | TRM Recommendation | Mid-A TRM Baselines | Mid Atlantic V6 Incremental Costs | Mid-Atlantic TRM V6 Source | Itron Incremental Cost Non-Regression ($2017) | Baseline, Measure, and Incremental Cost Calculations based on Itron MCS
Room Air Conditioner - Time of Sale | Consider using Itron value (~$20) -- Current values seem too high. EIA AEO assumes $20 incremental cost between Energy Star and standard unit; $0 difference between Energy Star and current practice unit. RTF study is half of Itron values, but based on old study. Mid-Atlantic, IL TRM and CA values are also based on older studies with much higher, incremental costs. | RAC rebates are no longer offered by EmPOWER. | Not Applicable | Federal standard. | $54 for units less than 6,000 Btu/hr., and $39 for units greater or equal to 6,000 Btu/hr. | MidA TRM RAC source: "Elko, Alex et al. Evaluation of Energy-Efficiency Standards for Room Air Conditioners in US” Sept 2012. Use average of Efficiency levels 4 and 5 to approximate current energy star standards." | NA | See Room AC Calculations | Note - Mid-A TRM specifies difference between With a and without reverse cycle. - Mid-A TRM uses CEER efficiency requirements, Itron model uses EER. Cost Calculations uses CEER requirements in place of EER. No labor cost associated with Incremental Cost, Time of Sale Calculated
Room Air Conditioner - Early Replacement | If DC or DE interested, Itron can provide tables with total costs for various categories of RACs -- see Room Air Conditioner - Time of Sale sheets. Also, for early replacement, the incremental costs should be equal to the full cost of the new unit minus the discounted future cost (at end of the RUL) of the base unit. | RAC rebates are no longer offered by EmPOWER. | Not Applicable | Dual baseline. EUL = 12 and RUL = 3. | Incremental cost is full cost of new unit minus the NPV of the deferred replacement cost = (Actual Cost of ENERGY STAR unit - $40 ) * 69% . | NA
Central Furnace Efficient Fan Motor | Current TRM value is based on a source that is more than a decade old. At $200, it is twice as high as Itron's current estimate for time of sale IMC ($98). Consider revising TRM TOS incremental cost to $98. For retrofit baseline condition, consider using $287 for initial incremental cost. | No specific incentives offered by EmPOWER, but to achieve SEER 18 could require retrofit of fan motors. TRM defines measures as: "A high efficiency brushless permanent magnet fan motor (BPM or ECM)." | TOS @ $98. Early replacement @ $287. See Efficienct_Fan_Motor. | A standard low-efficiency permanent split capacitor (PSC) fan motor. Retrofit and Time of Sale. | Assumed to be $200 | MidA TRM Source: Sachs and Smith, April 2003; Saving Energy with Efficient Furnace Air Handlers: A Status Update and Program Recommendations. | NA | See Efficient Fan Motor | Mid-A TRM Baseline Definition is "A standard low-efficiency permanent split capacitor (PSC) fan motor" and Efficient Definition is "A high efficiency brushless permanent magnet fan motor (BPM or ECM)". No specific specs were given are given. Therefor Incremental Cost was taken directly from the Itron MCS, which uses a Brushless fan motor as an example. Labor cost is the same for Res HVAC fam motors + Labor Costs | 1198
Air Source Heat Pump - Residential - Split System | Consider using Itron values which are revised to reflect changes in federal standards and inflation, and are provided for multiple efficiency levels and capacities. | ≥ 16 SEER and ≥ 13 EER and ≥ 9.0 HSPF ($675); ≥ 18 SEER and ≥ 13 EER and ≥ 9.5 HSPF ($1,125) | See Residential ASHP | Time of Sale and Early Replacement. Dual baseline assumes EUL = 18 years and RUL = 6 years. | See Residential Air-source Incremental Costs | Based upon average cost per ton from “2010-2012 WA017 Ex Ante Measure Cost Study Draft Report”, Itron, February 28, 2014. Note SEER 17 and 18 are extrapolated from other data points. | NA | Use link on Column D | Used 12000 btuh per 1 ton of refrigeration to convert Mid-A TRM tons to MCS btuh. Early Retirement incremental costs is the incremental cost of the measure plus the labor for disposal and removal
Central Air Conditioner - Residential | Consider using Itron values which are revised to reflect changes in federal standards and inflation. Itron values are provided for multiple efficiency levels and capacities, with and without ECM fans and with and without 80 AFUE furnaces (ECMs are required to achieve SEER 16). | ≥ 16 SEER and ≥ 13 EER ($450); ≥ 18 SEER and ≥ 13 EER ($900) | See Residential CAC | Time of Sale and Early Replacement. Dual baseline assumes EUL = 18 years and RUL = 6 years. | See TRM V6 Res CAC | Time of Sale: Costs based upon average cost per ton from “2010-2012 WA017 Ex Ante Measure Cost Study Draft Report”, Itron, February 28, 2014. Note SEER 17 and 18 are extrapolated from other data points. Early Replacement: Costs based upon average cost per ton for Equipment and Labor from Itron Measure Cost Study Results Matrix Volume 1 (part of “2010-2012 WA017 Ex Ante Measure Cost Study Draft Report”, Itron, February 28, 2014). | NA | Use link on Column D | Itron Calculations are based on Split System DX regressions. This was deemed appropriate for use because the Capacity range for these calculations are 1.4 to 4.8 tons (17000-58000 BTUH)
Geothermal Heat Pump | Consider enhancing the VEIC source documentation, which does not include dates or other discussion of methods used. We have no better sources and the values seem reasonable, but level of detail is insufficient to match to corresponding EmPOWER rebate levels. | 18 EER and 4.7 COP ($250/ton); 20 EER and 5.0 COP ($300/ton) | Not Available | Time of Sale is federal standard ASHP. | New Construction and Time of Sale: The actual installed cost of the Ground Source Heat Pump, including the ground loop and desuperheater if installed, should be used (default of $3957 per ton ), minus the assumed installed cost of the baseline equipment ($2355 per ton for ASHP ). | Measure cost based on data provided to VEIC in ‘Results of Home geothermal and air source heat pump rebate incentives documented by Illinois electric cooperatives’. Baseline ASHP cost is based upon average cost per ton for Equipment and Labor for SEER 14 ASHP from Itron Measure Cost Study Results Matrix Volume 1 (part of “2010-2012 WA017 Ex Ante Measure Cost Study Draft Report”, Itron, February 28, 2014). | NA | NA
Ductless MiniSplit Heat Pumps | Consider updating. As a benchmark, Homewyse.com calculator gives ~$400 difference between SEER 15 and SEER 20 units, with total installed cost for SEER 15 about $6k and SEER 20 at $6.4k, assuming 18kBTU capacity units. TRM assumes ~$600 for all capacities for SEERs 18 and 20. Also, note that incremental costs in TRM are relative to a 13 SEER baseline unit -- the federal standard baseline changed to SEER 14 in 2015. Homewyse values are based on four distributor web sites, which are listed on Homewyse webpage (see https://www.homewyse.com/costs/cost_of_ductless_heat_pump_systems.html). | ≥ 14.5 SEER and ≥ 12 EER and ≥ 8.2 HSPF ($180); ≥ 18 SEER and ≥ 12.5 EER and ≥ 9.0 HSPF ($360); Multizone ≥ 15.5 SEER and ≥ 12.5 EER and ≥ 8.6 HSPF ($540) | EmPOWER rebate categories include SEER 14.5-plus units and SEER 18-plus units. At this point in time, the IMC between a 14.5 (lower tier EmPOWER unit) and a 14 SEER federal standard unit is likely close to zero. The IMC for 18 SEER units should be no higher than $400, based on Homewyse.com. Data was not available to enable us to estimate cost differences based on HSPF. | Time of Sale and Early Replacement. Dual baseline assumes EUL = 18 years and RUL = 6 years. | See Res Mini Ductless Heat Pump | Time of Sale/NC: Incremental costs against a SEER 13 mini-split as presented in NEEP Incremental Cost Study Phase Two Final Report, January 2013. Results for 1 and 1.5 ton are based upon 21 SEER (most represented) and 18 SEER for 2 ton (only value provided). Values for 2.5 and 3 ton are assumed consistent with the other sizes. Early Replacement Source: Based upon review of Ductless Heat Pumps for Residential Customers in Connecticut, Swift, Joseph R and Rebecca A. Meyer, The Connecticut Light & Power Company, 2010 ACEEE Summer Study on Energy Efficiency in Buildings (2-292). Also supported by findings in NEEP Northeast/Mid-Atlantic Air-Source Heat Pump Market Strategies Report, January 2014 and NEEP Incremental Cost Study Phase Two Final Report, January 2013. If existing heating and cooling load is replaced at the end of its life, then a baseline cost should be determined and subtracted from the full install cost. | NA | NA | The Mid A references the Navigant NEEP phase 2 study for the Commercial Mini Ductless HP Costs, However the phase two study they are pretty clear that the measures are residential ductless mini split HP.
Duct Sealing Measures (Residential) | OK as is in TRM, but EmPOWER programs may need to consider other options. | HPwES program currently offers cost-based incentives, but transitioning to performance-based incentives. | Project costs have been known in past because incentives were cost-based. It is unclear if costs will still be known under new performance based incentive program. | Retrofit. | "The incremental cost for this measure should be the actual labor and material cost to seal the ducts." | Gas Source: Navigant. 2015. Incremental Cost Study Phase Four, Draft Report. Burlington, MA. | 272.4433 | NA | For Mastic seal (Itron MCS does not apply to Aeroseal
Shell Measures (Residential) | OK as is in TRM, but EmPOWER programs may need to consider other options. | HPwES program currently offers cost-based incentives, but transitioning to performance-based incentives. | Project costs have been known in past because incentives were cost-based. It is unclear if costs will still be known under new performance based incentive program. | Retrofit. | "The incremental cost for this measure should be the actual labor and material cost to seal the ducts."
Condensing Natural Gas Furnace | Consider revising values to reflect Final Rule Technical Support Document (TSD) dated August 2016, adjusted for Maryland and inflation. Also, consider adding TSD maintenance costs ($4.19 annual). | AFUE 92% or higher and input rating of 300,000 BTU or lower. | Include DOE TSD August 2016 total and component installed cost values for AFUE 80, 90, 92, 95 and 98, along with a separate annual maintenance cost value. | Time of Sale (federal baseline). The baseline condition is a non-condensing gas furnace with an AFUE of 80% (AFUE 81% if weatherized). | AFUE 90% ($630), AFUE 92% ($802), AFUE 96% ($1,747) | Costs derived from Page E-3 of Appendix E of Residential Furnaces and Boilers Final Rule Technical Support Document: http://www1.eere.energy.gov/buildings/appliance_standards/residential/fb_tsd_0907.html
Residential Small Gas water Heater - Gas Storage | The current TRM values are in line with Itron calculator values. Consider adjusting for inflation. Itron calculator available upon request if greater detail is desired. | These are not EmPOWER measures. | Not Applicable | Time of Sale (federal standard) | Gas Storage $400 Condensing gas storage $685 Tankless whole-house unit $605 | MidA TRM source: Source for cost info; DOE, 2010 Residential Heating Products Final Rule Technical Support Document, Table 8.2.14 (http://www1.eere.energy.gov/ | NA | See Small Gas WH Calculations
Residential Small Gas water Heater - Gas Tankless |  |  | Not Applicable | [5 empty] | Mid-A TRM - Baseline splits two between 20-55 gal and 55 to 100 gal
Residential Heat Pump Water Heaters | Consider using Itron detailed values, which can be aligned with program measure eligibility. Current MidA TRM IMC value ($1000) for TOS is OK, but may be on the high side for 40-gallon units and source is unclear and appears dated. | $500 rebate for HPWH: EF >=2.0 if under 55 gallons, EF>=2.2 if over 55 gallons. | $1,338 for 40-gallon units , $2,253 for 60-gallon units. | Time of Sale (federal standard) only. | "The incremental capital cost for this measure is $1,000, for a HPWH with an energy factor of 2.0" | DOE, 2010 Residential Heating Products Final Rule Technical Support Document, Table 8.2.14 http://www1.eere.energy.gov/buildings/appliance_standards/residential/pdfs/htgp_finalrule_ch8.pdf | NA | See Residential Heat Pump Water Heater | Incremental costs only calculated for an EF = 2.0 for direct comparison with Mid-A TRM Incremental cost. Itron MCS baseline was Small Electric Storage Water Heater 40 Gal; EF = 0.92; Recover Eff = 0.98: $421. Mid-A TRM states that to assume 40 gal if size not available
Refrigerator - Res - ER/Retrofit | Consider using Itron values if revisions or more detail is desired. The current TRM values are in line with Itron calculations and the Illinois TRM. | EmPOWER makes no distinction between early replacement and time of sale purchases. Rebates are $100 for Energy Star and $150 for CEE Tier 2. (Note that rebate levels exceed the current TRM TOS incremental costs.) | See Refrigerator Calculations | Dual baseline. RUL = 4 years; EUL =12 years. | "The initial full measure cost for an Energy Star refrigerator is assumed to be $748 and Tier 2 is $862. The avoided replacement cost (after 4 years) of a baseline replacement refrigerator is $722" | Full ENERGY STAR and baseline costs based on “2010-2012 WA017 Ex Ante Measure Cost Study Draft Report”, Itron, February 28, 2014. See “Refrigerator Default Calcs.xlsx”. Full CEE Tier 2 cost is based upon incremental cost estimate derived from “TECHNICAL REPORT: Analysis of Amended Energy Conservation Standards for Residential Refrigerator-Freezers”. http://www1.eere.energy.gov/buildings/appliance_standards/pdfs/refrigerator_report_1.pdf | NA | See Refrigerator Calculations | Tier 2 efficiency is 85% of the energy consumption of the baseline as stated in the Mid-A TRM. No Labor Costs for Refrigerator Included.
Refrigerator - Time of Sale |  |  |  | Time of Sale (federal standard). | "The incremental cost for this measure is assumed to be $26 for an ENERGY STAR unit and $140 for a CEE Tier 2 unit" | Based on Department of Energy, “TECHNICAL REPORT: Analysis of Amended Energy Conservation Standards for Residential Refrigerator-Freezers”, October 2005. | NA |  | Tier 2 efficiency is 85% of the energy consumption of the baseline as stated in the Mid-A TRM. No Labor Costs for Refrigerator Included.
Freezer | No new data is available. Energy Star refrigerator incremental costs are roughly half what they were prior to 2014 standards changes (see Refrigerator measure for sources). Assuming similar trend for freezers, consider halving the pre-2014 value of $36. |  | 17 | Time of Sale (federal standard).
Clothes Washer - RES - Time of Sale | This measure needs further discussion. Itron values are much lower than TRM V.6 values, EmPOWER rebates, and Energy Star calculator values. Energy Star which cites "Cadmus research in available models, 2016." This is based on Cadmus review in 2015 of 4 retailer websites - Sears, Home Depot, Lowes Best Buy. Energy Star criteria is less stringent than the CEE/BGE rebate requirements, which suggests the incremental cost of CEE Tier 3 units would be even higher. For Time of Sale, the Energy Star calculator gives incremental costs of $50 for front-loading units and $190 for top-loading units. | EmPOWER makes no distinction between early replacement and time of sale purchases. IMEF =>2.74 and IWF <=3.2 ($75). IMEF >=2.92 and IWF <=3.2 ($100). See https://bgesmartenergy.com/residential/appliance-rebates/clothes-washers | See Residential Clothes Washer | Time of Sale (federal standard). | ENERGY STAR, CEE Tier 1 $48 ENERGY STAR Most Efficient, CEE TIER 2 $269 CEE TIER 3 $297 | Mid A TRM "Based on weighted average of top loading and front loading units (based on available product from the CEC Appliance database) and cost data from Life-Cycle Cost and Payback Period Excel-based analytical tool. See ‘2015 Mid Atlantic Early Replacement Clothes Washer Analysis.xls’ for details.." | NA | See Residential Clothes Washer | Itron calculations calls for MEF. IMEF used in place due to lack of reliable conversion between IMEF and MEF. No Labor Costs Included in Itron MCS. Contains scenarios with Mid-A TRM baseline condition (2015 Federal standards) and 2018 or after Federal Standards as a the baseline condition. No Labor Costs associated with the
Clothes Washer - RES - Early Replacement |  |  |  | Dual baseline. RUL = 5 years; EUL =14 years. | ENERGY STAR, CEE Tier 1 $879 ENERGY STAR Most Efficient, CEE TIER 2 $1100 CEE TIER 3 $1128 |  | NA |  | "The existing unit efficiency is assumed to be 1.0 IMEF for front loaders and 0.84 IMEF for top loaders. This is based on the Federal Standard for clothes washers from 2004 - 2015" with a RUL of 5 years
Low Flow Showerheads | Consider adjusting current TRM values for inflation. | Installed free of charge as part of HPwES, QHEC and Limited Income programs. |  |  | As a retrofit measure, the incremental cost will be the actual cost of installing the new showerhead. As a time of sale measure, the incremental cost is assumed to be $6" | Source "Navigant Consulting, Ontario Energy Board, “Measures and Assumptions for Demand Side Management (DSM) Planning”, April 2009." | 37.629 | NA | Mid-A TRM assumes baseline of 2.5GPM or an actual measurement for direct install. No incremental cost available for time of sale purchase in Itron MCS. From Itron MCS (avg materials = 18.50, avg Labor = 15.67)
Commercial Air Conditioners - Air Cooled - Split and single package | Consider using Itron values based on Itron regression. Current TRM value is based on Navigant (2014). CEE requirements have since changed and the assumed baseline of IECC 2012 is not used in Maryland. Note Itron regression was not estimated for split CAC units over 65k BTU; Itron used packaged unit incremental cost regression equations to estimate costs for split system units. | See http://www.bgesmartenergy.com/sites/default/files/public/BGE_IC_Tech_Sheet_HVAC.pdf | See Commercial AC | Time of Sale/New (based on IECC model code) | See Mid-A TRM Commercial Unitary HVAC incremental Costs | Navigant. May 2014. Incremental Cost Study Phase Three Final Report. Prepared for NEEP Regional Evaluation, Measurement & Verification Forum. In all cases, incremental costs are presented relative to the baseline efficiencies presented in the Baseline Efficiencies by System Type and Unit Capacity table for the relevant size categories. AC CEE efficiency tiers as presented in Consortium for Energy Efficiency. 2016. CEE Commercial Unitary Air-Conditioning and Heat Pumps Specification, Effective January 12, 2016. HP Ibid. In the absence of better data, incremental costs for air-source heat pumps >=65,000 Btu/h are assumed equal to the air-cooled unitary AC equipment for the corresponding size categories. Therefore, the CEE tiers presented here reflect cooling mode requirements for AC equipment. Note:" Incremental costs for water- and Evaporatively-cooled ACs, PTACs, and PTHPs will be addressed in subsequent versions of the TRM. In the interim, incremental costs for these equipment types should be determined on a site-specific basis." | NA |  | No specific Efficient Condition is given in the Mid- A Mid-A TRM. System with an efficiency that is higher than the baseline is considered to be an efficient condition. *Important* - calculation for split systems uses the ITRON MCS Split System equations. Capacity is a continuous variable for a BTUH range of 17400-59000 BTUH for HP and 17000-58000 DX systems. This document contains cost estimates that uses the ITROM MSC equations to estimate costs of measure with BTUH above the ranges specified. The results for split systems may not be accurate as a result.
Commercial Air Conditioners - Water Cooled - Split and single package |  |  | Not Available | Time of Sale/New (based on IECC model code) |  |  | NA | NA
Commercial Air Conditioners - Air Evaporatively Cooled - Split and single package |  |  | Not Available | Time of Sale/New (based on IECC model code) |  |  | NA | NA
Commercial Heat Pumps - Air Cooled Split and Single packaged |  |  | See Commercial HP | Time of Sale/New (based on IECC model code) |  |  | NA
Comm Ductless Mini Split Heat Pump | Itron does not have data to support a recommendation, especially given the numerous baseline possibilities associated with t his measure. Note that the current TRM values are based on data from 2013. | BGE gives $100 rebate for SEER 16/8.2 HSPF Ductless Minisplit Heat Pumps and for SEER 16 Minisplit Air Conditioners. | Not Available | IMCs provided for SEER 13, 18, 21 and 26 and 9, 12, 18 and 24 kBTUH capacities. | See Comm Mid A TRM Mini Ductless Heat Pump | Measure Cost Source: Navigant, Inc. Incremental Cost Study Phase 2. January 16, 2013. Table 16. Baseline source: Energy Star Calculator. http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/CalculatorConsumerRoomAC.xls) Energy Star Calculator. 46% added to value to reflect labor, based on ratio of equipment to labor cost for measure EffFurn-cond-90AFUE in DEER database. http://www.energystar.gov/buildings/sites/default/uploads/files/Furnace_Calculator.xls?8178-e52c If existing case is electric resistance heat, assume project replaces existing functional baseboard.
Variable Frequency Drive (VFD) | Consider revising HP categories to be consistent with EmPOWER and other jurisdictions. Also, consider including bypass and non-bypass IMC values. The current TRM IMC values assume no bypass, but manufacturers often recommend bypass and IMC values will be higher with bypass and the TRM does include part load factors that are heavily influenced by bypass. I was unable to determine if VFDs with bypass comprise a significant share of EmPOWER savings since it is not reported -- This is interesting given the importance in determining savings)-- bypass is the first consideration in the TRM part load ratio table, which significantly affects savings. Itron IMC provides breakdown based on HP, bypass and NEMA motor types 1, 3 and 12 (see NEMA definitions in file). However, based on conversations with evaluators, the EMPOWER utilities and evaluators have minimal data on VFD bypass or other features to use that level granularity. | 2HP ($500), 3HP ($600), 4HP ($700), 5HP ($800), 7.5HP ($900), 10HP ($1,100), 15HP ($1,350), 20HP ($1,500), 25HP ($1,600), 30HP ($1,800), 40HP ($2,000), 50HP ($2,500), 60HP ($3,000), 75HP ($3,750), 100HP ($5,000), >100HP-200HP ($50 per HP). | See VFD | Retrofit | 5hp $2,125 15 hp$3,193 25hp $4,260 50hp $6,448 75hp $8,407 100 hp $10,493 200hp $17,266 | MidA TRM Source: Navigant. 2013. Incremental Cost Study Phase Two Final Report. Burlington, MA. | NA | See VFD Calculations | Itron - splits measures VFD between >10hp and <=10hp. IL-TRM only specifies deemed IMC values for up to 20 HP
Occupancy Sensor | Consider using Itron values. Current TRM values are dated (2011) and there are some discrepancies in source document. | See http://www.bgesmartenergy.com/sites/default/files/public/BGE_IC_Tech_Sheet_Lighting.pdf | Without Ultrasonic: 130.01 With Ultrasonic: $176.08 |  | "The incremental cost for this measure is assumed to be $115 per control for wall occupancy sensors, $200 per control for fixture-mounted and remote-mounted occupancy sensors." | MidA TRM Source: Northeast Energy Efficiency Partnerships Incremental Cost Study Report, Navigant, 2011. Sensors costs assume the simple average of cost for those sensors using only passive infrared technology and those using both passive infrared and ultrasonic technology. | NA | See Occupancy Sensor | Incremental Cost is the cost is the of the measure (absence of measure).
Electric Chillers - Water Cooled | Consider using Itron values corresponding with EmPOWER incentives. Also, clarify/confirm that IMCs are for EER Full Load (FLV), not EER Part Load (IPLV). | Incentives for water cooled chillers are based on kW/ton with additional incentives based on 0.01 kW incremental reductions. See http://www.bgesmartenergy.com/sites/default/files/public/BGE_IC_Tech_Sheet_HVAC.pdf. | See Electric Chillers Water-Cooled Time of Sale | Time of Sale. For Maryland, the baseline condition is a standard efficiency air or water chilling package equal to the requirements presented in the International Energy Conservation Code 2015 (IECC 2015), Table C403.2.3(7). For Washington, D.C. and Delaware, the baseline condition is a standard efficiency air or water chilling package equal to the requirements presented in the International Energy Conservation Code 2012 (IECC 2012), Table C403.2.3(7). | See Elec Chillers TRM Incremental Cost | MidA TRM source: Navigant. 2013. Incremental Cost Study Phase Two Final Report. Burlington, MA. Table values adapted from published values to align with baseline code requirements (“Path A”) by interpolating or extrapolating from nearest pair of published efficiency values. “N/A” indicates either an efficiency value below baseline requirements or a gap in the published data from the source document. | NA | See Electric Chillers Water-Cooled Time of Sale | Costs presented in the calculations do not contain labor costs added to them. Labor Costs are the same between all efficiencies within a given mount and capacity. The labor costs for these measures have been provided in the Calculations workbook. If Incremental costs need to be calculated for changing mount type apply the correct costs accordingly.
Electric Chillers - Air Cooled |  | Minimum eligibility requirement is 10.4 EER for air cooled (10.3 VFD air cooled), with additional incentive based on 0.1 EER incremental increases. See http://www.bgesmartenergy.com/sites/default/files/public/BGE_IC_Tech_Sheet_HVAC.pdf. | See Electric Chillers Air-Cooled Time of Sale |  |  |  | NA | See Electric Chillers Air-Cooled Time of Sale | Mid-A TRM uses EER for specification Itron equation uses kW/ton . EER to kW/ton conversions used for analysis. Costs presented in the calculations do not contain labor costs added to them. Labor Costs are the same between all efficiencies within a given mount and capacity. The labor costs for these measures have been provided in the Calculations workbook. If Incremental costs need to be calculated for changing mount type apply the correct costs accordingly.
Electric Chillers - Water Cooled - Early Replacement | Use Itron values corresponding with EmPOWER incentives. Also, clarify/confirm that IMCs are for EER Full Load (FLV), not EER Part Load (IPLV). | Incentives for water cooled chillers are based on kW/ton with additional incentives based on 0.01 kW incremental reductions. See http://www.bgesmartenergy.com/sites/default/files/public/BGE_IC_Tech_Sheet_HVAC.pdf. | See Electric Chillers Water-Cooled ER | Dual baseline. | "The incremental cost for this measure should be the actual cost of the replacement unit and any cost of installation labor." | NA | NA | See Electric Chillers Water-Cooled ER | Itron MCS only has Labor costs for 100, 200, and 300 Capacity Chillers. There for the labor costs were rounded to the closest Capacity size for labor. Early Replacement Incremental Costs assume installation and replacement for ground mounted chillers. Roof and Basement labor costs are provided if they are in the Itron MCS.
Electric Chillers - Air Cooled - Early Replacement |  | Minimum eligibility requirement is 10.4 EER for air cooled, with additional incentive based on 0.1 EER incremental increases. See http://www.bgesmartenergy.com/sites/default/files/public/BGE_IC_Tech_Sheet_HVAC.pdf. | See Electric Chillers Air-Cooled Early Replacement | Dual baseline. |  |  | NA | See Electric Chillers Air-Cooled Early Replacement | Itron MCS only has Labor costs for 100, 200, and 300 Capacity Chillers. There for the labor costs were rounded to the closest Capacity size for labor. Early Replacement Incremental Costs assume installation and replacement for ground mounted chillers. Roof and Basement labor costs are provided if they are in the Itron MCS.
Clothes Washer - Com | This needs further discussion. Itron values are much lower than TRM V.6 values and values currently used in the Energy Star calculator, which cites "Cadmus research in available models, 2016." For Time of Sale, the Energy Star calculator gives incremental costs of $200 for front-loading units and $200 for top-loading units. | CEE Tier 1 ($100) and CEE Tier 2 ($200). See http://www.bgesmartenergy.com/sites/default/files/public/BGE_IC_Tech_Sheet_Kitchen_Refrig_Appliance_PlugLoad.pdf | CEE has suspended Commercial Clothes Washers. |  | The incremental cost for this measure is $200 | MidA TRM Source: U.S. EPA. 2016. Savings Calculator for ENERGY STAR Qualified Appliances. Accessed March 7, 2016. | NA | NA | Clothes washer for Com uses RES equation n from Itron MCS. Results not be valid
Evaporator fan control on walk-in coolers/freezers (<1 hp) | Use current TRM values adjusted for inflation. |  |  |  | The incremental capital cost is $532 for multispeed controls . Value includes labor costs. The actual measure installation cost for ON/OFF controls should be used (including materials and labor) . | Sources Navigant. 2015. Incremental Cost Study Phase Four, Final Report. Burlington, MA. Navigant’s research revealed that ON/OFF controls are typically only found in refrigeration management systems. These systems have capabilities beyond evaporator fan control, including controls for the compressor cycle, defrost cycle, door heaters, outdoor air economizer, and more. The cost of these systems is highly variable depending on capability and falls in the approximate range of $500 - $1,700. | 669.0164 | NA | Itron Incremental Cost is the built up average from built-up estimate (n=4). Materials - $420.95, Labor - $199.55, Total- $620.50 - 2014 dollars; IMC source: Itron Measure Cost Study, 2014 Results Matrix VolumeII
Evaporator fan control on walk-in coolers/freezers (>1 hp) | Use current TRM values adjusted for inflation. | [5 empty] | 2128.6357 | NA | Itron Incremental Cost is the built up average from built-up estimate (n=6) Materials = $1212, Labor = $762, Total - $1974.26 - 2014 dollars; IMC source: Itron Measure Cost Study, 2014 Results Matrix VolumeII
Commercial/Food Service Convection Ovens - Electric - Full Size | Use current TRM values adjusted for inflation. |  |  |  | "The incremental cost is assumed to be $0 for electric commercial convection ovens and -$1,778 for gas ovens." | Electric MidA Source: US EPA. February 2015. Savings Calculator for ENERGY STAR Certified Commercial Kitchen Equipment. | -636.1342 | NA | RTF IMC is based on a 2006 prices that are converted to 2012 dollars and then to 2017 dollars; IMC source: Itron Measure Cost Study, 2014 Results Matrix VolumeII
Commercial/Food Service Convection Ovens - Gas - Full size | Use current TRM values adjusted for inflation. | [5 empty] | -225.8816 | NA | IMC source: Itron Measure Cost Study, 2014 Results Matrix VolumeII
Electric Fryer | Use current TRM values adjusted for inflation. |  |  |  | "$210 for standard sized equipment and $0 for large vat equipment" | Electric Fryer source midA TRM: US EPA. February 2015. Savings Calculator for ENERGY STAR Certified Commercial Kitchen Equipment. | 28.2981 | NA | Itron Incremental Cost is the Matched average in terms of per unit production capacity (lbs./hr.) IMC for unit w/70 lbs./hr. production capacity (roughly average for 14" vats) = $1,837. RTF IMC is based on a 2006 prices that are converted to 2012 dollars and then to 2017 dollars; IMC source: Itron Measure Cost Study, 2014 Results Matrix VolumeII
Gas Fryer | Use current TRM values adjusted for inflation. |  |  |  | "For gas fryers, the incremental cost is assumed to be $2,441" | Natural Gas: Navigant. 2015. Incremental Cost Study Phase Four Final Report. Burlington, MA. | 26.5337 | NA | Itron Incremental Cost is the Matched average in terms of per unit production capacity (lbs./hr.). IMC for unit w/70 lbs./hr. production capacity (roughly average for 14" vats) = $1,722; IMC source: Itron Measure Cost Study, 2014 Results Matrix VolumeII
Return To Master Summary

## Efficient_Fan_Motor
Recommended ($2017)
Time of Sale | Retrofit
97.7749 | 286.7974
Return To Master Summary
Costs | [5 empty] | Incremental Costs
Baseline (Labor Included) |  | Efficient Condition (Labor Included) |  | Labor Cost (same for all Res HVAC fan Motors) |  | Time of Sale |  | Lifecycle Retrofit/Early Replacement
Example: 0.5 HP Permanent Split Capacitor |  | Example: 0.5 HP Brushless Fan
Cost | Cost (2017 $) | Cost | Cost (2017 $) | Cost | Cost (2017 $) | IC | IC (2017 $) | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost ASHP
403.7575 | 435.3287 | 494.4415 | 533.1036 | 142.0218 | 153.127 | 90.684 | 97.7749 | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 189.0225 | 286.7974
Baseline (no Labor) |  | Efficient Condition (No Included)
Example: 0.5 HP Permanent Split Capacitor Motor |  | Example: 0.5 HP Brushless Fan Motor
Cost | Cost (2017 $) | Cost | Cost (2017 $)
261.7357 | 282.2017 | 352.4197 | 379.9766

## Residential_ASHP
Recommended Incremental Costs (assumes 3-Ton Units) | [10 empty] | For Reference Only
Empower Category | SEER | Components |  |  |  |  | Time of Sale |  | Early Replacement |  | Mid-Atlantic TRM Version 6.0
|  | Base Case Equipment Cost per Unit ($2017) | Base Case Equipment Cost per Ton ($2017) | Measure Equipment Cost per Unit ($2017) | Measure Equipment Cost per Ton ($2017) | Labor Cost | Incremental Cost per Unit ($2017) | Incremental Cost per Ton ($2017) | Incremental Cost per Unit ($2017) | Incremental Cost per Ton ($2017) | Time of Sale Cost per Ton ($2013) | Early Replacement Cost per Ton ($2013)
≥ 16 SEER and ≥ 13 EER and ≥ 9.0 HSPF | 16 | 2515.3257 | 838.4419 | 3697.6515 | 1232.5505 | 555.5718 | 1182.3258 | 394.1086 | 2830.0678 | 943.3559 | 340 | 3120
| 17 |  |  | 4288.8144 | 1429.6048 |  | 1773.4888 | 591.1629 | 3421.2308 | 1140.4103 | 529 | 3309
≥ 18 SEER and ≥ 13 EER and ≥ 9.5 HSPF | 18 |  |  | 4879.9773 | 1626.6591 |  | 2364.6517 | 788.2172 | 4012.3937 | 1337.4646 | 710 | 3614
| 19 |  |  | 5471.1403 | 1823.7134 |  | 2955.8146 | 985.2715 | 4603.5566 | 1534.5189 | NA | NA
| 20 |  |  | 6062.3032 | 2020.7677 |  | 3546.9775 | 1182.3258 | 5194.7195 | 1731.5732 | NA | NA
| 21 |  |  | 6653.4661 | 2217.822 |  | 4138.1404 | 1379.3801 | 5785.8824 | 1928.6275 | NA | NA
Return To Master Summary
ASHP IMC | [18 empty] | Baseline
Scenario |  |  |  | TOS |  |  |  | Lifecycle Retrofit/Early Replacement Incremental Cost Calculator
Empower Category | SEER | Cooling Capacity (Btuh) | Tons | TOS - ASHP Only | TOS/Ton | TOS (2017$) | TOS/Ton (2017$) | ASHP Labor (2017$) - from Itron Measure Cost study (Adjusted for Inflation and Location) | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost ASHP | Per Ton Lifecycle Retrofit/Early Replacement Incremental Cost ASHP |  | SEER | Cooling Capacity (But) | Tons | Baseline Cost | Baseline Cost/Ton | Baseline Cost (2017 $) | Baseline Cost/Ton (2017 $)
≥ 16 SEER and ≥ 13 EER and ≥ 9.0 HSPF | 16 | 24000 | 2 | 1096.5803 | 548.2902 | 1182.3258 | 591.1629 | 555.5718 | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 1055.054 | 2237.3798 | 1118.6899 |  | 14 | 24000 | 2 | 1738.3457 | 869.1729 | 1874.2732 | 937.1366
|  | 36000 | 3 | 1096.5803 | 365.5268 | 1182.3258 | 394.1086 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 1647.742 | 2830.0678 | 943.3559 |  |  | 36000 | 3 | 2332.9073 | 777.6358 | 2515.3257 | 838.4419
| 17 | 24000 | 2 | 1644.8705 | 822.4352 | 1773.4888 | 886.7444 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 1055.054 | 2828.5427 | 1414.2714
|  | 36000 | 3 | 1644.8705 | 548.2902 | 1773.4888 | 591.1629 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 1647.742 | 3421.2308 | 1140.4103 | Empower Incentive categories as the Efficient Condition
≥ 18 SEER and ≥ 13 EER and ≥ 9.5 HSPF | 18 | 24000 | 2 | 2193.1606 | 1096.5803 | 2364.6517 | 1182.3258 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 1055.054 | 3419.7056 | 1709.8528
|  | 36000 | 3 | 2193.1606 | 731.0535 | 2364.6517 | 788.2172 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 1647.742 | 4012.3937 | 1337.4646 | Empower Category | SEER | Cooling Capacity (Btuh) | Tons | Measure Cost | Measure Cost Cost/Ton | Measure Cost (2017 $) | Measure Cost/Ton (2017 $)
| 19 | 24000 | 2 | 2741.4508 | 1370.7254 | 2955.8146 | 1477.9073 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 1055.054 | 4010.8685 | 2005.4343 | ≥ 16 SEER and ≥ 13 EER and ≥ 9.0 HSPF | 16 | 24000 | 2 | 2834.926 | 1417.463 | 3056.599 | 1528.2995
|  | 36000 | 3 | 2741.4508 | 913.8169 | 2955.8146 | 985.2715 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 1647.742 | 4603.5566 | 1534.5189 |  |  | 36000 | 3 | 3429.4876 | 1143.1625 | 3697.6515 | 1232.5505
| 20 | 24000 | 2 | 3289.7409 | 1644.8705 | 3546.9775 | 1773.4888 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 1055.054 | 4602.0315 | 2301.0157 |  | 17 | 24000 | 2 | 3383.2162 | 1691.6081 | 3647.7619 | 1823.881
|  | 36000 | 3 | 3289.7409 | 1096.5803 | 3546.9775 | 1182.3258 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 1647.742 | 5194.7195 | 1731.5732 |  |  | 36000 | 3 | 3977.7778 | 1325.9259 | 4288.8144 | 1429.6048
| 21 | 24000 | 2 | 3838.0311 | 1919.0155 | 4138.1404 | 2069.0702 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 1055.054 | 5193.1944 | 2596.5972 | ≥ 18 SEER and ≥ 13 EER and ≥ 9.5 HSPF | 18 | 24000 | 2 | 3931.5064 | 1965.7532 | 4238.9249 | 2119.4624
|  | 36000 | 3 | 3838.0311 | 1279.3437 | 4138.1404 | 1379.3801 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 1647.742 | 5785.8824 | 1928.6275 |  |  | 36000 | 3 | 4526.068 | 1508.6893 | 4879.9773 | 1626.6591
NA | 15 | 24000 | 2 | 548.2902 | 274.1451 | 591.1629 | 295.5815 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 1055.054 | 1646.2169 | 823.1084 |  | 19 | 24000 | 2 | 4479.7965 | 2239.8983 | 4830.0878 | 2415.0439
|  | 36000 | 3 | 548.2902 | 182.7634 | 591.1629 | 197.0543 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 1647.742 | 2238.9049 | 746.3016 |  |  | 36000 | 3 | 5074.3581 | 1691.4527 | 5471.1403 | 1823.7134
[19 empty] | 20 | 24000 | 2 | 5028.0867 | 2514.0433 | 5421.2507 | 2710.6253
[20 empty] | 36000 | 3 | 5622.6483 | 1874.2161 | 6062.3032 | 2020.7677
[19 empty] | 21 | 24000 | 2 | 5576.3768 | 2788.1884 | 6012.4136 | 3006.2068
[20 empty] | 36000 | 3 | 6170.9384 | 2056.9795 | 6653.4661 | 2217.822
[18 empty] | NA | 15 | 24000 | 2 | 2286.6359 | 1143.3179 | 2465.4361 | 1232.7181
[20 empty] | 36000 | 3 | 2881.1975 | 960.3992 | 3106.4886 | 1035.4962

## Residential_CAC
Recommended Incremental Costs (assumes 3-Ton Units) | [18 empty] | For Reference Only
Category | SEER | Cost Components |  |  |  |  | Time of Sale | [5 empty] | Early Replacement | [5 empty] | Mid-Atlantic TRM Version 6.0
|  | Base Case Equipment Cost per Unit ($2017) | Base Case Equipment Cost per Ton ($2017) | CAC-Only Measure Equipment Cost per Unit ($2017) | CAC-Only Measure Equipment Cost per Ton ($2017) | Labor Cost | CAC-Only Incremental Cost per Unit ($2017) | CAC-Only Incremental Cost per Ton ($2017) | CAC plus Furnace Incremental Cost per Unit ($2017) | CAC plus Furnace Incremental Cost per Ton ($2017) | CAC plus Retrofit ECM Incremental Cost per Unit ($2017) | CAC plus Retrofit ECM Incremental Cost per Ton ($2017) | CAC-Only Incremental Cost per Unit ($2017) | CAC-Only Incremental Cost per Ton ($2017) | CAC plus Furnace Incremental Cost per Unit ($2017) | CAC plus Furnace Incremental Cost per Ton ($2017) | CAC plus Retrofit ECM Incremental Cost per Unit ($2017) | CAC plus Retrofit ECM Incremental Cost per Ton ($2017) | Time of Sale Cost per Ton ($2013) | Early Replacement Cost per Unit ($2013)
≥ 16 SEER and ≥ 13 EER and ≥ 9.0 HSPF | 16 | 1665.7349 | 555.245 | 2261.7179 | 753.906 | 586.0352 | 595.9831 | 198.661 | 2447.816 | 815.9387 | 1129.0867 | 376.3622 | 1521.262 | 507.0873 | 3373.095 | 2358.9203 | 2054.3657 | 1040.191 | 184 | 2495
| 17 |  |  | 2559.7095 | 853.2365 |  | 893.9746 | 297.9915 | 2745.8075 | 915.2692 | 1427.0782 | 475.6927 | 1819.2536 | 606.4179 | 3671.0865 | 2458.2508 | 2352.3572 | 1139.5215 | 276 | 2588
≥ 18 SEER and ≥ 13 EER and ≥ 9.5 HSPF | 18 |  |  | 2857.701 | 952.567 |  | 1191.9661 | 397.322 | 3043.799 | 1014.5997 | 1725.0697 | 575.0232 | 2117.2451 | 705.7484 | 3969.078 | 2557.5813 | 2650.3487 | 1238.852 | 369 | 2680
| 19 |  |  | 3155.6925 | 1051.8975 |  | 1489.9576 | 496.6525 | 3341.7905 | 1113.9302 | 2023.0613 | 674.3538 | 2415.2366 | 805.0789 | 4267.0695 | 2656.9118 | 2948.3403 | 1338.1825 | 461 | 2772
| 20 |  |  | 3453.684 | 1151.228 |  | 1787.9492 | 595.9831 | 3639.7821 | 1213.2607 | 2321.0528 | 773.6843 | 2713.2281 | 904.4094 | 4565.0611 | 2756.2423 | 3246.3318 | 1437.513 | 553 | 2864
| 21 |  |  | 3751.6756 | 1250.5585 |  | 2085.9407 | 695.3136 | 3937.7736 | 1312.5912 | 2619.0443 | 873.0148 | 3011.2197 | 1003.7399 | 4863.0526 | 2855.5728 | 3544.3233 | 1536.8435 | 645 | 2956
Return To Master Summary
Empower Incentive Category IMC
Scenario |  |  |  | Time of Sale | [5 empty] | Lifecycle Retrofit/Early Replacement Incremental Cost Calculator
Empower Category | SEER | Cooling Capacity (Btuh) | Tons | TOS Incremental Unit Cost - CAC Only | Per Ton Time of Sale Incremental Cost - CAC Only | TOS Incremental Unit Cost - CAC Only ($2017) | Per Ton Time of Sale Incremental Cost - CAC Only ($2017) | TOS Incremental Unit Cost w Central Furnace(2017$) | TOS w/Retrofit ECM (2017$) | CAC Labor (2017$) from Itron Measure Cost study (Adjusted for Inflation and Location) | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment ($2017) | Lifecycle Retrofit/Early Replacement Incremental Cost CAC- Only ($2017) | Lifecycle Retrofit/Early Replacement Incremental Cost w/ Central Furnace (2017$) | Lifecycle Retrofit/Early Replacement Incremental Cost w/ Retrofit ECM ($2017)
≥ 16 SEER and ≥ 13 EER and ≥ 9.0 HSPF | 16 | 24000 | 2 | 552.7607 | 276.3804 | 595.9831 | 297.9915 | 2447.816 | 1129.0867 | 586.0352 | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 781.4636 | 1377.4467 | 3229.2796 | 1910.5503
|  | 36000 | 3 | 552.7607 | 184.2536 | 595.9831 | 198.661 | 2447.816 | 1129.0867 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 925.279 | 1521.262 | 3373.095 | 2054.3657
| 17 | 24000 | 2 | 829.1411 | 414.5705 | 893.9746 | 446.9873 | 2745.8075 | 1427.0782 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 781.4636 | 1675.4382 | 3527.2711 | 2208.5418
|  | 36000 | 3 | 829.1411 | 276.3804 | 893.9746 | 297.9915 | 2745.8075 | 1427.0782 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 925.279 | 1819.2536 | 3671.0865 | 2352.3572
≥ 18 SEER and ≥ 13 EER and ≥ 9.5 HSPF | 18 | 24000 | 2 | 1105.5214 | 552.7607 | 1191.9661 | 595.9831 | 3043.799 | 1725.0697 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 781.4636 | 1973.4297 | 3825.2626 | 2506.5334
|  | 36000 | 3 | 1105.5214 | 368.5071 | 1191.9661 | 397.322 | 3043.799 | 1725.0697 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 925.279 | 2117.2451 | 3969.078 | 2650.3487
| 19 | 24000 | 2 | 1381.9018 | 690.9509 | 1489.9576 | 744.9788 | 3341.7905 | 2023.0613 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 781.4636 | 2271.4212 | 4123.2542 | 2804.5249
|  | 36000 | 3 | 1381.9018 | 460.6339 | 1489.9576 | 496.6525 | 3341.7905 | 2023.0613 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 925.279 | 2415.2366 | 4267.0695 | 2948.3403
| 20 | 24000 | 2 | 1658.2822 | 829.1411 | 1787.9492 | 893.9746 | 3639.7821 | 2321.0528 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 781.4636 | 2569.4128 | 4421.2457 | 3102.5164
|  | 36000 | 3 | 1658.2822 | 552.7607 | 1787.9492 | 595.9831 | 3639.7821 | 2321.0528 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 925.279 | 2713.2281 | 4565.0611 | 3246.3318
| 21 | 24000 | 2 | 1934.6625 | 967.3313 | 2085.9407 | 1042.9703 | 3937.7736 | 2619.0443 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 781.4636 | 2867.4043 | 4719.2372 | 3400.5079
|  | 36000 | 3 | 1934.6625 | 644.8875 | 2085.9407 | 695.3136 | 3937.7736 | 2619.0443 |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 925.279 | 3011.2197 | 4863.0526 | 3544.3233
NA | 15 | 24000 | 2 | 276.3804 | 138.1902 | 297.9915 | 148.9958 | NA | NA |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 781.4636 | 1079.4551 | 2931.2881 | 1612.5588
|  | 36000 | 3 | 276.3804 | 92.1268 | 297.9915 | 99.3305 | NA | NA |  | 5% | 18 | 6 | 5.0757 | 11.6896 | 0.43421 | 925.279 | 1223.2705 | 3075.1034 | 1756.3742
Empower Incentive Categories as the Efficient Condition
|  | CAC Baseline based on TRM description | [8 empty] | Empower Category | SEER | Cooling Capacity (Btuh) | Tons | EmPower Measure Cost | EmPower Cost Cost/Ton | EmPower Cost (2017 $) | EmPower Cost/Ton (2017 $)
|  | SEER | Btu | Tons | Baseline Cost | Baseline Cost/Ton | Baseline Cost (2017 $) | Baseline Cost/Ton (2017 $) |  |  | ≥ 16 SEER and ≥ 13 EER and ≥ 9.0 HSPF | 16 | 24000 | 2 | 1766.4775 | 883.2388 | 1904.6047 | 952.3024
|  | 14 | 24000 | 2 | 1213.7168 | 606.8584 | 1308.6217 | 654.3108 |  |  |  |  | 36000 | 3 | 2097.6919 | 699.2306 | 2261.7179 | 753.906
|  |  | 36000 | 3 | 1544.9312 | 514.9771 | 1665.7349 | 555.245 |  |  |  | 17 | 24000 | 2 | 2042.8579 | 1021.4289 | 2202.5962 | 1101.2981
[13 empty] | 36000 | 3 | 2374.0723 | 791.3574 | 2559.7095 | 853.2365
[11 empty] | ≥ 18 SEER and ≥ 13 EER and ≥ 9.5 HSPF | 18 | 24000 | 2 | 2319.2383 | 1159.6191 | 2500.5878 | 1250.2939
|  | Additional Costs to be applied based on Scenario | [10 empty] | 36000 | 3 | 2650.4527 | 883.4842 | 2857.701 | 952.567
|  | 80% AFUE Gas Furnace Cost w/OEM ECM (100,000 btuh unit) including labor - Source DOE | ECM Retrofit 0.5 HP Brushless Fan Motor (ECM) - From Itron MCS | ECM Retrofit Labor - From Itron MCS | [7 empty] | 19 | 24000 | 2 | 2595.6186 | 1297.8093 | 2798.5793 | 1399.2896
|  | 1851.8329 | 379.9766 | 153.127 | [8 empty] | 36000 | 3 | 2926.833 | 975.611 | 3155.6925 | 1051.8975
[12 empty] | 20 | 24000 | 2 | 2871.999 | 1435.9995 | 3096.5708 | 1548.2854
[13 empty] | 36000 | 3 | 3203.2134 | 1067.7378 | 3453.684 | 1151.228
[12 empty] | 21 | 24000 | 2 | 3148.3793 | 1574.1897 | 3394.5623 | 1697.2812
[13 empty] | 36000 | 3 | 3479.5937 | 1159.8646 | 3751.6756 | 1250.5585
[11 empty] | NA | 15 | 24000 | 2 | 1490.0972 | 745.0486 | 1606.6132 | 803.3066
[13 empty] | 36000 | 3 | 1821.3116 | 607.1039 | 1963.7264 | 654.5755
Note on U4: Loper, Joe: These TRM V6 ER values were reported as per ton values, which was incorrect.

## Res_CondensingFurnace_IMC
AFUE | Cost Components
| Base Case Equipment Cost ($2017) | Measure Cost | IMC
90% | 1851.8329 | 2244.0437 | 392.2108
92% |  | 2280.55 | 428.7171
95% |  | 2388.6723 | 536.8394
98% |  | 2511.3478 | 659.5149
Condensing Furnaces Time of Sale |  | Direct from Tables ($2015) |  | With Regional Adjustment ($2015) |  | With Regional Adjustment ($2017)
| AFUE | Total Cost | Incremental Cost | Total Cost | Incremental Cost | Total Cost | Incremental Cost
Avg Total Installed Cost | 80% (Baseline) | 2174.64 |  | 1783.4192 |  | 1851.8329
Table 8.2.16 | 90% | 2635.22 | 460.58 | 2161.1402 | 377.721 | 2244.0437 | 392.2108
| 92% | 2678.09 | 503.45 | 2196.2978 | 412.8786 | 2280.55 | 428.7171
| 95% | 2805.06 | 630.42 | 2300.4257 | 517.0065 | 2388.6723 | 536.8394
| 98% | 2949.12 | 774.48 | 2418.5691 | 635.1499 | 2511.3478 | 659.5149
| Avg Condensing | 2766.8725 | 592.2325 | 2269.1082 | 485.689 | 2356.1535 | 504.3205
Annualized Repair & Maintenance Cost | 80% (Baseline) | 61.1 |  | 50.108 |  | 52.0302
Tables 8.2.22 & 8.2.23 | 90% | 66.03 | 4.93 | 54.1511 | 4.0431 | 56.2284 | 4.1982
| 92% | 66.03 | 4.93 | 54.1511 | 4.0431 | 56.2284 | 4.1982
| 95% | 66.03 | 4.93 | 54.1511 | 4.0431 | 56.2284 | 4.1982
| 98% | 66.03 | 4.93 | 54.1511 | 4.0431 | 56.2284 | 4.1982
| Avg Condensing | 66.03 | 4.93 | 54.1511 | 4.0431 | 56.2284 | 4.1982
Highlighted values are average of the four condensing furnace categories.
Source: | Technical Support Document: Energy Efficiency Program for Consumer Products and Commercial and Industrial Equipment: Residential Furnaces
https://www.regulations.gov/document?D=EERE-2014-BT-STD-0031-0217
Return To Master Summary

## Residential_HPWH
Recommended Incremental Costs (assumes Averages for 40 and 60 Gallon Units)
Empower Category | Minimum Efficiency | Components |  |  |  |  | Time of Sale
| Efficiency Factor | Base Case Equipment Cost per Unit ($2017) - 40 Gallon Efficient Gas Water Heater without Labor | Base Case Equipment Cost per Unit ($2017) - 40 Gallon Efficient Gas Water Heater with Labor | Average Measure Equipment Cost per Unit ($2017) without Labor | Average Measure Equipment Cost per Unit ($2017) with Labor | Labor Cost - HPWH | Average Incremental Cost per Unit ($2017) -TOS | Average Incremental Cost per Ton ($2017) - with Labor
40 Gallon Heat Pump Water Heater | 2 | 763.4108 | 1035.7743 | 2101.2286 | 2492.0534 | 390.8247 | 1337.8178 | 1456.279
60 Gallon Heat Pump Water Heater | 2.2 |  |  | 3016.7546 | 3407.5794 |  | 2253.3438 | 2371.805
Return To Master Summary
IMC Calculations - TOS
Baseline -Efficient Water Heater |  |  | Cost Calculations | [5 empty] | EmPower - IMC Values -TOS
Baseline EF calculated from TRM equation | Assume 40 gal cost (Labor Not Included) | Assumed 40 gal cost (2017 $) (Labor NOT Included) | Minimum EmPOWER EF (2.0 under 55 gal, 2.2 if over 55 gal) | Assumed Storage Volume (Gallons) | Assumed Input Capacity (kw) | Volt 230 | Heat Pump Cost (Labor NOT Included) | Heat Pump Cost (2017 $ ) (Labor Not Included) | Calculated Incremental Cost | Calculated Incremental Cost (2017 $) | Average Incremental Cost ($2017) by input capacity | Average Incremental Cost ($2017) for 40 Gallon Units | Average Incremental Cost ($2017) for 60 Gallon Units | Labor Costs - Region Adjusted
0.948 | 708.0462 | 763.4108 | 2 | 40 | 3 | No | 1873.5915 | 2020.0943 | 1165.5453 | 1256.6835 | 1703.4342 | 1337.8178 | 2253.3438 | Condition | Gal | Labor Costs | Labor Costs (2017 $)
|  |  | 2.2 | 60 | 3 | No | 2227.9732 | 2402.1864 | 1519.927 | 1638.7755 |  |  |  | Baseline Labor | 40 | 252.611 | 272.3635
|  |  | 2.2 | 80 | 3 | No | 2762.2632 | 2978.2544 | 2054.217 | 2214.8436 |  |  |  | Heat pump water heater | NA | 362.481 | 390.8247
|  |  | 2 | 40 | 4 | No | 1608.5395 | 1734.3169 | 900.4933 | 970.9061 | 2128.9021
|  |  | 2.2 | 60 | 4 | No | 3941.9125 | 4250.1447 | 3233.8663 | 3486.7339
|  |  | 2.2 | 80 | 4 | No | 2497.2112 | 2692.477 | 1789.165 | 1929.0662 |  | Return To Master Summary
|  |  | 2 | 40 | 3 | yes | 2289.144 | 2468.1403 | 1581.0978 | 1704.7295 | 2151.4802
|  |  | 2.2 | 60 | 3 | yes | 2643.5257 | 2850.2324 | 1935.4795 | 2086.8216
|  |  | 2.2 | 80 | 3 | yes | 3177.8157 | 3426.3004 | 2469.7695 | 2662.8896
|  |  | 2 | 40 | 4 | yes | 2024.092 | 2182.363 | 1316.0458 | 1418.9521 | 1865.7029
|  |  | 2.2 | 60 | 4 | yes | 2378.4737 | 2564.455 | 1670.4275 | 1801.0442
|  |  | 2.2 | 80 | 4 | yes | 2912.7637 | 3140.5231 | 2204.7175 | 2377.1123
EmPOWER Categories IMC with Labor
Baseline EF calculated from TRM equation |  |  | Cost Calculations | [5 empty] | EmPower - IMC Values
Baseline EF calculated from TRM equation | Assume 40 gal cost (Labor Included) | Assumed 40 gal cost (2017 $) (Labor Included) | Minimum EmPOWER EF (2.0 under 55 gal, 2.2 if over 55 gal) | Assumed Storage Volume (Gallons) | Assumed Input Capacity (kw) | Volt 230 | Heat Pump Cost (Labor Included) | Heat Pump Cost (2017 $ ) (Labor Included) | Calculated Incremental Cost | Calculated Incremental Cost (2017 $) | Average Incremental Cost ($2017) by input capacity | Average Incremental Cost ($2017) for 40 Gallon Units | Average Incremental Cost ($2017) for 60 Gallon Units
0.948 | 960.6571 | 1035.7743 | 2 | 40 | 3 | No | 2236.0725 | 2410.919 | 1275.4154 | 1375.1447 | 1821.8954 | 1456.279 | 2371.805
|  |  | 2.2 | 60 | 3 | No | 2590.4542 | 2793.0111 | 1629.7971 | 1757.2368
|  |  | 2.2 | 80 | 3 | No | 3124.7442 | 3369.0791 | 2164.0871 | 2333.3048
|  |  | 2 | 40 | 4 | No | 1971.0205 | 2125.1417 | 1010.3634 | 1089.3673 | 2247.3633
|  |  | 2.2 | 60 | 4 | No | 4304.3935 | 4640.9694 | 3343.7364 | 3605.1951
|  |  | 2.2 | 80 | 4 | No | 2859.6922 | 3083.3018 | 1899.0351 | 2047.5274
|  |  | 2 | 40 | 3 | yes | 2651.625 | 2858.9651 | 1690.9679 | 1823.1907 | 2269.9415
|  |  | 2.2 | 60 | 3 | yes | 3006.0067 | 3241.0571 | 2045.3496 | 2205.2828
|  |  | 2.2 | 80 | 3 | yes | 3540.2967 | 3817.1252 | 2579.6396 | 2781.3508
|  |  | 2 | 40 | 4 | yes | 2386.573 | 2573.1877 | 1425.9159 | 1537.4134 | 1984.1641
|  |  | 2.2 | 60 | 4 | yes | 2740.9547 | 2955.2798 | 1780.2976 | 1919.5054
|  |  | 2.2 | 80 | 4 | yes | 3275.2447 | 3531.3478 | 2314.5876 | 2495.5735

## Refrigerator_IMC
Recommended Incremental Costs (Assumes Adjusted Volume of 25 ft. Cubed) | [11 empty] | For Reference Only
Product Category | Components |  |  |  |  | Time of Sale |  |  | Early Replacement |  |  | Mid-Atlantic TRM Version 6.0
| Calculated Baseline Cost ($2017) | Energy Star Calculated Cost ($2017) | CEER Tier 2 Calculated Cost ($2017) | CEER Tier 3 Calculated Cost ($2017) | Labor Cost | TOS - Energy Star ($2017) | TOS - Tier 2 ($2017) | TOS - Tier 3 ($2017) | ER - Energy Star ($2017) | ER - Tier 2 ($2017) | ER - Tier 3 ($2017) | Time of Sale - Energy Star ($2013) | Time of Sale - CEER Tier 2 ($2013) | Early Replacement Initial Cost - Energy Star | Early Replacement Initial Cost - CEER Tier 2 | avoided replacement cost (after 4 years) of a baseline replacement refrigerator
1. Refrigerators and Refrigerator-freezers with manual defrost | NA | NA | NA | NA | No Labor Associated with Residential Refrigerators | NA | NA |  | NA | NA | NA | 26 | 140 | 748 | 862 | 722
2. Refrigerator-Freezer--partial automatic defrost | NA | NA | NA | NA |  | NA | NA |  | NA | NA | NA
3. Refrigerator-Freezers--automatic defrost with top-mounted freezer without through-the-door ice service and all-refrigerators--automatic defrost | 720.6232 | 837.9466 | 861.5535 | 872.6102 |  | 9.5632 | 33.1701 | 44.2268 | 340.9773 | 364.5842 | 375.6409
4. Refrigerator-Freezers--automatic defrost with side-mounted freezer without through-the-door ice service | 514.1115 | 634.1315 | 659.6453 | 672.6089 |  | 13.377 | 38.8908 | 51.8544 | 261.7243 | 287.2381 | 300.2017
5. Refrigerator-Freezers--automatic defrost with bottom-mounted freezer without through-the-door ice service | 1092.0707 | 1212.6341 | 1238.8512 | 1252.5181 |  | 14.7837 | 41.0009 | 54.6678 | 494.0117 | 520.2288 | 533.8958
6. Refrigerator-Freezers--automatic defrost with top-mounted freezer with through-the-door ice service | 1202.5117 | 1327.12 | 1354.7883 | 1369.9063 |  | 17.686 | 45.3542 | 60.4723 | 541.5556 | 569.2238 | 584.3419
7. Refrigerator-Freezers--automatic defrost with side-mounted freezer with through-the-door ice service | 1007.5278 | 1134.3654 | 1163.3261 | 1179.7366 |  | 20.2708 | 49.2315 | 65.642 | 465.9903 | 494.951 | 511.3615
Return To Master Summary
Product Category | Annual Energy usage Calculations -From TRM | [13 empty] | Component Calculations Based on Itron MCS | [11 empty] | IMC - TOS
| Federal Baseline - Maximum Energy Usage in kWh/year Equation | Measure -ENERGY STAR Maximum Energy Usage in kWh/year Equation | Baseline - Maximum Energy Usage in kWh/year Calculated using Equation to the left |  |  | Efficient Condition - ENERGY STAR Maximum Energy Usage in kWh/year |  |  | Efficient Condition - Tier 2 Maximum Energy Usage in kWh/year - Calculation Based on definition of CEER tier 2 (15% less energy than required by the federal standard) provided in TRM |  |  | Efficient Condition - Tier 3 Maximum Energy Usage in kWh/year - Calculation Based on definition of CEER tier 3 (20% less energy than required by the federal standard) provided in TRM |  |  | Calculated Baseline Cost |  |  | Calculated Energy Star Cost |  |  | Calculated Tier 2 Cost |  |  | Calculated Tier 3 Cost |  |  | TOS - Energy Star as Measure |  |  | TOS - CEER 2 |  |  | TOS - CEER 3
|  |  | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30
1. Refrigerators and Refrigerator-freezers with manual defrost | 6.79AV + 193.6 | 6.11 * AV + 174.2 | 363.35 | 329.4 | 397.3 | 327.015 | 296.46 | 357.57 | 308.8475 | 279.99 | 337.705 | 290.68 | 263.52 | 317.84 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
2. Refrigerator-Freezer--partial automatic defrost | 7.99AV + 225.0 | 7.19 * AV + 202.5 | 424.75 | 384.8 | 464.7 | 382.275 | 346.32 | 418.23 | 361.0375 | 327.08 | 394.995 | 339.8 | 307.84 | 371.76 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
3. Refrigerator-Freezers--automatic defrost with top-mounted freezer without through-the-door ice service and all-refrigerators--automatic defrost | 8.07AV + 233.7 | 7.26 * AV + 210.3 | 435.45 | 395.1 | 475.8 | 391.905 | 355.59 | 428.22 | 370.1325 | 335.835 | 404.43 | 348.36 | 316.08 | 380.64 | 768.3067 | 668.3616 | 868.2519 | 777.1764 | 675.3308 | 879.0221 | 799.0713 | 696.2754 | 901.8671 | 809.3261 | 705.58 | 913.0722 | 8.8697 | 6.9692 | 10.7702 | 30.7645 | 27.9138 | 33.6153 | 41.0194 | 37.2184 | 44.8204
4. Refrigerator-Freezers--automatic defrost with side-mounted freezer without through-the-door ice service | 8.51AV + 297.8 | 7.66 * AV + 268.0 | 510.55 | 468 | 553.1 | 459.495 | 421.2 | 497.79 | 433.9675 | 397.8 | 470.135 | 408.44 | 374.4 | 442.48 | 575.7356 | 476.8267 | 674.6446 | 588.1425 | 487.2295 | 689.0556 | 611.806 | 509.8909 | 713.7211 | 623.8294 | 520.9123 | 726.7466 | 12.4069 | 10.4028 | 14.411 | 36.0704 | 33.0642 | 39.0765 | 48.0938 | 44.0856 | 52.102
5. Refrigerator-Freezers--automatic defrost with bottom-mounted freezer without through-the-door ice service | 8.85AV + 317.0 | 7.97 * AV + 285.3 | 538.25 | 494 | 582.5 | 484.425 | 444.6 | 524.25 | 457.5125 | 419.9 | 495.125 | 430.6 | 395.2 | 466 | 1110.9789 | 1012.8707 | 1209.0872 | 1124.6905 | 1024.4981 | 1224.8829 | 1149.0063 | 1047.7718 | 1250.2408 | 1161.6821 | 1059.4055 | 1263.9587 | 13.7116 | 11.6274 | 15.7958 | 38.0274 | 34.9011 | 41.1536 | 50.7031 | 46.5348 | 54.8715
6. Refrigerator-Freezers--automatic defrost with top-mounted freezer with through-the-door ice service | 8.40AV + 385.4 | 7.56 * AV + 355.3 | 595.4 | 553.4 | 637.4 | 535.86 | 498.06 | 573.66 | 506.09 | 470.39 | 541.79 | 476.32 | 442.72 | 509.92 | 1214.4703 | 1115.3023 | 1313.6383 | 1230.8736 | 1129.7274 | 1332.0198 | 1256.5353 | 1154.4 | 1358.6706 | 1270.557 | 1167.4326 | 1373.6814 | 16.4033 | 14.4251 | 18.3815 | 42.065 | 39.0977 | 45.0323 | 56.0867 | 52.1303 | 60.0431
7. Refrigerator-Freezers--automatic defrost with side-mounted freezer with through-the-door ice service | 8.54AV + 432.8 | 7.69 * AV + 397.9 | 646.3 | 603.6 | 689 | 581.67 | 543.24 | 620.1 | 549.355 | 513.06 | 585.65 | 517.04 | 482.88 | 551.2 | 1033.2974 | 934.4591 | 1132.1357 | 1052.0981 | 951.2486 | 1152.9476 | 1078.9585 | 977.1034 | 1180.8135 | 1094.1788 | 991.3182 | 1197.0395 | 18.8007 | 16.7896 | 20.8119 | 45.6611 | 42.6443 | 48.6779 | 60.8815 | 56.8591 | 64.9038
Product Category | Component Calculations Based on Itron MCS ($ 2017) | [11 empty] | IMC - TOS ($ 2017)
| Calculated Baseline Cost |  |  | Calculated Energy Star Cost |  |  | Calculated Tier 2 Cost |  |  | Calculated Tier 3 Cost |  |  | TOS - Energy Star as Measure |  |  | TOS - CEE 2 |  |  | TOS - CEE 3
| AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30
1. Refrigerators and Refrigerator-freezers with manual defrost | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
2. Refrigerator-Freezer--partial automatic defrost | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
3. Refrigerator-Freezers--automatic defrost with top-mounted freezer without through-the-door ice service and all-refrigerators--automatic defrost | 828.3834 | 720.6232 | 936.1436 | 837.9466 | 728.1373 | 947.7559 | 861.5535 | 750.7197 | 972.3874 | 872.6102 | 760.7518 | 984.4686 | 9.5632 | 7.5142 | 11.6123 | 33.1701 | 30.0965 | 36.2438 | 44.2268 | 40.1287 | 48.325
4. Refrigerator-Freezers--automatic defrost with side-mounted freezer without through-the-door ice service | 620.7545 | 514.1115 | 727.3974 | 634.1315 | 525.3277 | 742.9353 | 659.6453 | 549.7611 | 769.5295 | 672.6089 | 561.6443 | 783.5735 | 13.377 | 11.2162 | 15.5379 | 38.8908 | 35.6496 | 42.132 | 51.8544 | 47.5328 | 56.1761
5. Refrigerator-Freezers--automatic defrost with bottom-mounted freezer without through-the-door ice service | 1197.8503 | 1092.0707 | 1303.63 | 1212.6341 | 1104.6072 | 1320.6609 | 1238.8512 | 1129.7008 | 1348.0016 | 1252.5181 | 1142.2442 | 1362.7921 | 14.7837 | 12.5366 | 17.0309 | 41.0009 | 37.6301 | 44.3716 | 54.6678 | 50.1735 | 59.1621
6. Refrigerator-Freezers--automatic defrost with top-mounted freezer with through-the-door ice service | 1309.434 | 1202.5117 | 1416.3563 | 1327.12 | 1218.0648 | 1436.1752 | 1354.7883 | 1244.6666 | 1464.9099 | 1369.9063 | 1258.7183 | 1481.0944 | 17.686 | 15.5531 | 19.8189 | 45.3542 | 42.1549 | 48.5535 | 60.4723 | 56.2065 | 64.7381
7. Refrigerator-Freezers--automatic defrost with side-mounted freezer with through-the-door ice service | 1114.0946 | 1007.5278 | 1220.6614 | 1134.3654 | 1025.6302 | 1243.1007 | 1163.3261 | 1053.5066 | 1273.1456 | 1179.7366 | 1068.8329 | 1290.6403 | 20.2708 | 18.1024 | 22.4393 | 49.2315 | 45.9789 | 52.4841 | 65.642 | 61.3051 | 69.9789
IMC Early Replacement (2017$)
Product Category | Labor | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Refrigerator | PV Real Levelized Carrying Charge for New Refrigerator | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment |  |  | Lifecycle Retrofit/Early Replacement Incremental Cost (Energy Star) |  |  | Lifecycle Retrofit/Early Replacement Incremental Cost (CEE Tier 2) |  |  | Lifecycle Retrofit/Early Replacement Incremental Cost (CEE Tier 2)
[8 empty] | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30 | AV (volume ft3) = 25 | AV (volume ft3) = 20 | AV (volume ft3) = 30
1. Refrigerators and Refrigerator-freezers with manual defrost | Itron MCS does not consider cost for Refrigerators Washers | 5% | 12 | 4 | 3.546 | 8.8633 | 0.40007 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
2. Refrigerator-Freezer--partial automatic defrost |  | 5% | 12 | 4 | 3.546 | 8.8633 | 0.40007 | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
3. Refrigerator-Freezers--automatic defrost with top-mounted freezer without through-the-door ice service and all-refrigerators--automatic defrost |  | 5% | 12 | 4 | 3.546 | 8.8633 | 0.40007 | 331.4141 | 288.3021 | 374.5261 | 340.9773 | 295.8163 | 386.1384 | 364.5842 | 318.3986 | 410.7698 | 375.6409 | 328.4308 | 422.8511
4. Refrigerator-Freezers--automatic defrost with side-mounted freezer without through-the-door ice service |  | 5% | 12 | 4 | 3.546 | 8.8633 | 0.40007 | 248.3473 | 205.6823 | 291.0123 | 261.7243 | 216.8985 | 306.5502 | 287.2381 | 241.3319 | 333.1444 | 300.2017 | 253.2151 | 347.1884
5. Refrigerator-Freezers--automatic defrost with bottom-mounted freezer without through-the-door ice service |  | 5% | 12 | 4 | 3.546 | 8.8633 | 0.40007 | 479.228 | 436.9083 | 521.5476 | 494.0117 | 449.4449 | 538.5785 | 520.2288 | 474.5385 | 565.9192 | 533.8958 | 487.0819 | 580.7097
6. Refrigerator-Freezers--automatic defrost with top-mounted freezer with through-the-door ice service |  | 5% | 12 | 4 | 3.546 | 8.8633 | 0.40007 | 523.8696 | 481.0929 | 566.6464 | 541.5556 | 496.646 | 586.4652 | 569.2238 | 523.2478 | 615.1999 | 584.3419 | 537.2994 | 631.3844
7. Refrigerator-Freezers--automatic defrost with side-mounted freezer with through-the-door ice service |  | 5% | 12 | 4 | 3.546 | 8.8633 | 0.40007 | 445.7195 | 403.085 | 488.3541 | 465.9903 | 421.1874 | 510.7933 | 494.951 | 449.0638 | 540.8382 | 511.3615 | 464.3901 | 558.3329
Return To Master Summary

## Commercial_AC
Recommended Incremental Costs
| Size Category | Sub Category | Components |  |  |  |  | Labor Cost | Time of Sale |  |  | Early Replacement | Full Cost of Efficient Equipment
|  |  | Base Case Equipment Cost per Ton - IECC 2012 ($2017) | Base Case Equipment Cost per Ton - IECC 2015 ($2017) | Base Case Equipment Cost per Ton - If Federal Standards change on Jan 1, 2018 ($2017) - Calculated with IEER | Measure Equipment Cost per Ton CEE Tier 2 - ($2017) | Equipment Cost per Ton - If federal Standards change on Jan 1, 2018 ($2017) - ($2017) - Calculated with IEER |  | TOS per Ton - IECC 2012 ($2017) | TOS per Ton - IECC 2015 ($2017) | TOS per Ton - If Federal Standards change on Jan 1, 2018 ($2017) | ER per Ton - If Federal Standards change on Jan 1, 2018 ($2017) | Federal Standards change on Jan 1, 2018 ($2017) ($/ton)
| <65,000 Btu/h | Split System | 416.9323 | 416.9323 | NA | 595.7272 | NA | 6225.0025 | 178.7949 | 178.7949 | NA | 872.0065 | 1840.7278
| <65,000 Btu/h | Packaged | 789.6465 | 864.537 | NA | 1014.3182 | NA | 2756.4075 | 224.6717 | 149.7811 | NA | 740.3356 | 1565.5997
| ≥65,000 Btu/h and <135,000 Btu/h | Packaged | 980.2332 | 980.2332 | 1518.7271 | 1267.4299 | 1913.6226 | 2935.4851 | 287.1968 | 287.1968 | 394.8955 | 1175.3054 | 1913.6226
| ≥135,000 Btu/h and <240,000 Btu/h | Packaged | 1063.2655 | 1063.2655 | 1292.3281 | 1254.73 | 1443.4843 | 3327.2175 | 191.4645 | 191.4645 | 151.1562 | 1585.6199 | 1443.4843
| ≥240,000 Btu/h and <760,000 Btu/h | Packaged | 1102.0603 | 1102.0603 | 1202.5792 | 1145.1398 | 1252.8386 | 4726.2615 | 43.0795 | 43.0795 | 50.2594 | 1595.6902 | 1252.8386
| ≥760,000 Btu/h | Packaged | 1140.4063 | 1140.4063 | NA | 1180.7933 | NA | 6069.3438 | 40.387 | 40.387 | NA | 554.0378 | 1271.8335
Unitary AC
Incremental Cost |  |  |  | Early Replacement Calculator | [6 empty] | Early Replacement Costs |  |  |  | Calculated Measure Costs
Size Category (Cooling Capacity) | Sub Category | Incremental Cost ($/Ton) | Incremental Cost ($/Ton) ($2017) | Labor (assumed roof mount) based on closest capacity available | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost ASHP | Lifecycle Retrofit/Early Replacement Incremental Cost/ Per Ton | Full Cost of Efficient Equipment ($/ton) | Size Category (Cooling Capacity) |  | capacity used for calculation (BTUH) | Tons | Minimum SEER/EER Eligibility | Measure Cost(Labor Not Included) | Measure (2017 $) | Measure Cost/Ton (2017 $) (Labor Not Included)
Current CEE Tier 2 Measure Costs - No Electric Resistance
CEE Tier 2 IMC with IECC 2015 as Baseline | [14 empty] | <65,000 Btu/h | Split System | 60000 | 5 | 16 | 2762.6173 | 2978.6362 | 595.7272
<65,000 Btu/h | Split System | 165.8282 | 178.7949 | 6225.0025 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 3466.058 | 4360.0326 | 872.0065 | 1840.7278
[15 empty] | <65,000 Btu/h | Packaged System | 60000 | 5 | 16 | 4703.7851 | 5071.5908 | 1014.3182
| Packaged System | 138.9186 | 149.7811 | 2756.4075 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 2952.7723 | 3701.678 | 740.3356 | 1565.5997
[15 empty] | ≥65,000 Btu/h and <135,000 Btu/h | Single- Packaged | 100000 | 8.3333 | 12 | 9795.937 | 10561.9162 | 1267.4299
≥65,000 Btu/h and <135,000 Btu/h | Single- Packaged | 266.3685 | 287.1968 | 2935.4851 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 4631.6478 | 7024.9541 | 842.9945 | 1619.6882
[15 empty] | ≥135,000 Btu/h and <240,000 Btu/h | Single- Packaged | 187500 | 15.625 | 12 | 18183.337 | 19605.1569 | 1254.73
≥135,000 Btu/h and <240,000 Btu/h | Single- Packaged | 177.579 | 191.4645 | 3327.2175 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 8317.5163 | 11309.1492 | 723.7855 | 1467.672
[15 empty] | ≥240,000 Btu/h and <760,000 Btu/h | Single- Packaged | 500000 | 41.6667 | 10.6 | 44253.797 | 47714.1592 | 1145.1398
≥240,000 Btu/h and <760,000 Btu/h | Single- Packaged | 39.9553 | 43.0795 | 4726.2615 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 21124.8053 | 22919.785 | 550.0748 | 1258.5701
[15 empty] | ≥760,000 Btu/h | Single- Packaged | 800000 | 66.6667 | 10.6 | 73010.597 | 78719.556 | 1180.7933
≥760,000 Btu/h | Single- Packaged | 37.4581 | 40.387 | 6069.3438 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 34243.3805 | 36935.85 | 554.0378 | 1271.8335
CEE Tier 2 IMC with IECC 2012 as Baseline
<65,000 Btu/h | Split System | This Measure the same as the IECC 2015 baseline. | [11 empty] | 1840.7278 | Calculated Baseline Costs
[15 empty] | Size Category (Cooling Capacity) |  | capacity used for calculation (BTUH) | Tons | Baseline Condition (IECC 2015) | Baseline SEER/EER used for calculation | Baseline Cost | Baseline Cost (2017 $) (Labor Not Included) | Baseline Cost/Ton (2017 $) (Labor Not Included)
| Packaged System | 208.3779 | 224.6717 | 2756.4075 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 2796.5836 | 3919.9422 | 783.9884 | 1565.5997 | Baseline - (IECC 2015)
[15 empty] | <65,000 Btu/h | Split System | 60000 | 5 | 13.0 SEER | 13 | 1933.4763 | 2084.6617 | 416.9323
≥65,000 Btu/h and <135,000 Btu/h | Single- Packaged | 266.3685 | 287.1968 | 2935.4851 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 4631.6478 | 7024.9541 | 842.9945 | 1619.6882
[15 empty] | <65,000 Btu/h | Packaged System | 60000 | 5 | 14.0 SEER | 14 | 4009.1921 | 4322.6851 | 864.537
≥135,000 Btu/h and <240,000 Btu/h | Single- Packaged | 177.579 | 191.4645 | 3327.2175 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 8317.5163 | 11309.1492 | 723.7855 | 1467.672
[15 empty] | ≥65,000 Btu/h and <135,000 Btu/h | Single- Packaged | 100000 | 8.3333 | 11.2 EER/12.8 IEER | 11.2 | 7576.1998 | 8168.6099 | 980.2332
≥240,000 Btu/h and <760,000 Btu/h | Single- Packaged | 39.9553 | 43.0795 | 4726.2615 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 21124.8053 | 22919.785 | 550.0748 | 1258.5701
[15 empty] | ≥135,000 Btu/h and <240,000 Btu/h | Single- Packaged | 187500 | 15.625 | 11.0 EER/12.4 IEER | 11 | 15408.6656 | 16613.5241 | 1063.2655
≥760,000 Btu/h | Single- Packaged | 37.4581 | 40.387 | 6069.3438 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 34243.3805 | 36935.85 | 554.0378 | 1271.8335
[15 empty] | ≥240,000 Btu/h and <760,000 Btu/h | Single- Packaged | 500000 | 41.6667 | 11.6 IEER/10.0 EER | 10 | 42588.9942 | 45919.1795 | 1102.0603
Relevant Categories with Federal Standard Changes. Baseline is Federal Standard Change Jan 1, 2018 or Later.
Size Category (Cooling Capacity) |  | Incremental Cost ($/Ton) | Incremental Cost ($/Ton) (2017 $) | Labor | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost ASHP | Lifecycle Retrofit/Early Replacement Incremental Cost/ Per Ton | Full Measure Costs | ≥760,000 Btu/h | Single- Packaged | 800000 | 66.6667 | 9.7 EER/11.2 IEER | 9.7 | 70513.3928 | 76027.0864 | 1140.4063
≥65,000 Btu/h and <135,000 Btu/h | Single- Packaged | 366.2566 | 394.8955 | 2935.4851 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 6503.4153 | 9794.2115 | 1175.3054 | 1913.6226
Baseline - (IECC 2012)
≥135,000 Btu/h and <240,000 Btu/h | Single- Packaged | 140.1939 | 151.1562 | 3327.2175 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 9922.703 | 13213.4991 | 1585.6199 | 1443.4843 | <65,000 Btu/h | Split System | 60000 | 5 | 13.0 SEER | 13 | 1933.4763 | 2084.6617 | 416.9323
≥240,000 Btu/h and <760,000 Btu/h | Single- Packaged | 46.6145 | 50.2594 | 4726.2615 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 22871.7884 | 25265.0946 | 1595.6902 | 1252.8386 | <65,000 Btu/h | Packaged System | 60000 | 5 | 13.0 SEER | 13 | 3661.8956 | 3948.2323 | 789.6465
[15 empty] | ≥65,000 Btu/h and <135,000 Btu/h | Single- Packaged | 100000 | 8.3333 | 11.2 EER/11.4 IEER | 11.2 | 7576.1998 | 8168.6099 | 980.2332
[15 empty] | ≥135,000 Btu/h and <240,000 Btu/h | Single- Packaged | 187500 | 15.625 | 11.0 EER/11.2 IEER | 11 | 15408.6656 | 16613.5241 | 1063.2655
[15 empty] | ≥240,000 Btu/h and <760,000 Btu/h | Single- Packaged | 500000 | 41.6667 | 10.0 EER/10.1 IEER | 10 | 42588.9942 | 45919.1795 | 1102.0603
Commercial AC Labor
[10 empty] | type | Tons | Labor Cost ($2017) |  |  | ≥760,000 Btu/h | Single- Packaged | 800000 | 66.6667 | 9.7 EER/9.8 IEER | 9.7 | 70513.3928 | 76027.0864 | 1140.4063
[10 empty] | split system | NA | 6225.0025
[10 empty] | packaged system | 5 | 2756.4075
[11 empty] | 8.3333 | 2935.4851
[11 empty] | 15.625 | 3327.2175 |  |  | Measure Calculations Based Federal Standards - On or After Jan 1 , 2017
[11 empty] | 41.6667 | 4726.2615 | [8 empty] | IEER used in place of EER | IEER used in place of EER
[11 empty] | 66.6667 | 6069.3438 |  |  | Size Category (Cooling Capacity) |  | capacity used for calculation (BTUH) | Tons | Subcategory | Federal Baseline - 2018 Standards | Baseline IEER | Increased Efficiency - Higher IEER than base | Baseline Cost (Labor Not Included) | Baseline Cost (2017 $) (Labor Not Included) | Efficient Cost (Labor Not Included) | Efficient Cost (2017 $) (Labor Not Included)
[15 empty] | ≥65,000 Btu/h and <135,000 Btu/h | Single- Packaged | 100000 | 8.3333 | Single- Packaged | 12.7 IEER | 12.7 | 13.8 | 11738.2069 | 12656.0592 | 14790.3455 | 15946.8553
[15 empty] | ≥135,000 Btu/h and <240,000 Btu/h | Single- Packaged | 190000 | 15.8333 | Single- Packaged | 12.2 IEER | 12.2 | 13 | 18977.9112 | 20461.8618 | 21197.6483 | 22855.1681
[15 empty] | ≥240,000 Btu/h and <760,000 Btu/h | Single- Packaged | 500000 | 41.6667 | Single- Packaged | 11.4 IEER | 11.4 | 12.1 | 46473.5341 | 50107.4655 | 48415.8041 | 52201.6085
Return To Master Summary

## Commercial_HP
Recommended Incremental Costs
| Size Category | Sub Category | Components |  |  |  |  | Labor Cost | Time of Sale |  |  | Early Replacement | Full Cost of Efficient Equipment
|  |  | Base Case Equipment Cost per Ton - IECC 2012 ($2017) | Base Case Equipment Cost per Ton - IECC 2015 ($2017) | Base Case Equipment Cost per Ton - If Federal Standards change on Jan 1, 2018 ($2017) - Calculated with IEER | Measure Equipment Cost per Ton CEE Tier 1 - ($2017) | Equipment Cost per Ton - If federal Standards change on Jan 1, 2018 ($2017) - ($2017) - Calculated with IEER |  | TOS per Ton - IECC 2012 ($2017) | TOS per Ton - IECC 2015 ($2017) | TOS per Ton - If Federal Standards change on Jan 1, 2018 ($2017) | ER per Ton - If Federal Standards change on Jan 1, 2018 ($2017) | If Federal Standards change on Jan 1, 2018 ($2017) ($/ton)
| <65,000 Btu/h | Split System | 503.3173 | 621.5499 | NA | 739.7824 | NA | 3919.0703 | 236.4652 | 118.2326 | NA | 704.4263 | 1523.5965
| <65,000 Btu/h | Packaged | 872.0432 | 963.8814 | NA | 1055.7196 | NA | 761.8233 | 183.6765 | 91.8382 | NA | 557.4375 | 1208.0843
| ≥65,000 Btu/h and <135,000 Btu/h | Packaged | 1301.3406 | 1301.3406 | 1553.4455 | 1326.5511 | 1553.4455 | 621.412 | 25.2105 | 25.2105 | 0 | 584.4238 | 1628.015
| ≥135,000 Btu/h and <240,000 Btu/h | Packaged | 1284.4381 | 1284.4381 | 1392.0029 | 1297.8837 | 1392.0029 | 621.412 | 13.4456 | 13.4456 | 0 | 557.9512 | 1431.7733
| ≥240,000 Btu/h and <760,000 Btu/h | Packaged | 1288.9318 | 1288.9318 | 1334.3107 | 1319.1844 | 1334.3107 | 621.412 | 30.2526 | 30.2526 | 0 | 556.468 | 1349.2246
Commercial Unitary ASHP Systems - For Federal Standards See Unitary Heat Pump Air Cooled Sheet
Incremental Costs | [14 empty] | Calculated Measure Cost
Size Category (Cooling Capacity) | SubCatagory | Incremental Cost ($2017) | Incremental Cost ($/Ton) ($2017) | Labor (assumed roof mount) based on closest capacity available | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost ASHP | Lifecycle Retrofit/Early Replacement Incremental Cost/ Per Ton | Full Cost of Efficient Equipment ($/ton) | Size Category (Cooling Capacity) |  | Midpoint - capacity used for calculation (BTUH) | Tons | SEER/EER | SEER/EER used | Measure (Labor Not Included) | Measure Cost (2017 $) | Measure Cost/Ton (2017 $) (Labor Not Included)
CEE Tier 1 IMC (IECC 2015 as Baseline) | [14 empty] | Current CEE Tier 1 Measure Costs - No Electric Resistance
<65,000 Btu/h | Split System | 591.1629 | 118.2326 | 3919.0703 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 2930.9686 | 3522.1315 | 704.4263 | 1523.5965 | <65,000 Btu/h | Split System | 60000 | 5 | 15 | SEER | 3430.6569 | 3698.9122 | 739.7824
| Single-Packaged | 459.1912 | 91.8382 | 761.8233 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 2327.9964 | 2787.1876 | 557.4375 | 1208.0843 | <65,000 Btu/h | Single-Packaged | 60000 | 5 | 15 | SEER | 4895.7798 | 5278.5982 | 1055.7196
≥65,000 Btu/h and <135,000 Btu/h | Single-Packaged | 210.0874 | 25.2105 | 621.412 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 4782.568 | 4992.6555 | 599.1187 | 1401.1205 | ≥65,000 Btu/h and <135,000 Btu/h | Single-Packaged | 100000 | 8.3333 | 11.1 | EER | 10252.883 | 11054.5925 | 1326.5511
≥135,000 Btu/h and <240,000 Btu/h | Single-Packaged | 210.0874 | 13.4456 | 621.412 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 8630.3568 | 8840.4443 | 565.7884 | 1337.6541 | ≥135,000 Btu/h and <240,000 Btu/h | Single-Packaged | 187500 | 15.625 | 10.7 | EER | 18808.7127 | 20279.4331 | 1297.8837
≥240,000 Btu/h and <760,000 Btu/h | Single-Packaged | 1260.5247 | 30.2526 | 621.412 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 22660.3866 | 23920.9112 | 574.1019 | 1334.0983 | ≥240,000 Btu/h and <760,000 Btu/h | Single-Packaged | 500000 | 41.6667 | 10.1 | EER | 50979.7298 | 54966.0167 | 1319.1844
CEE Tier 1 IMC (IECC 2012 as Baseline) - ROB, NC | [14 empty] | Calculated cost with IIER in place of EER for Comparrison with on or After Jan 1, 2018 Standard Changes
<65,000 Btu/h | Split System | 1182.3258 | 236.4652 | 3919.0703 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 2684.3876 | 3866.7134 | 773.3427 | 1523.5965 | ≥65,000 Btu/h and <135,000 Btu/h | Single-Packaged | 100000 | 8.3333 | 12 | 12.0 IEER | 12006.5449 | 12945.3795 | 1553.4455
| Single-Packaged | 918.3824 | 183.6765 | 761.8233 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 2136.4624 | 3054.8448 | 610.969 | 1208.0843 | ≥135,000 Btu/h and <240,000 Btu/h | Single-Packaged | 187500 | 15.625 | 11.4 | 11.4IEER | 20172.672 | 21750.0452 | 1392.0029
≥65,000 Btu/h and <135,000 Btu/h | Single-Packaged | 210.0874 | 25.2105 | 621.412 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 4782.568 | 4992.6555 | 599.1187 | 1401.1205 | ≥240,000 Btu/h and <760,000 Btu/h | Single-Packaged | 500000 | 41.6667 | 10.4 | 10.4 IEER | 51564.2838 | 55596.279 | 1334.3107
≥135,000 Btu/h and <240,000 Btu/h | Single-Packaged | 210.0874 | 13.4456 | 621.412 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 8630.3568 | 8840.4443 | 565.7884 | 1337.6541
Calculated Baseline Cost
≥240,000 Btu/h and <760,000 Btu/h | Single-Packaged | 1260.5247 | 30.2526 | 621.412 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 22660.3866 | 23920.9112 | 574.1019 | 1334.0983 | Size Category (Cooling Capacity) |  | Midpoint - capacity used for calculation (BTUH) | Tons | Baseline Efficiency | Baseline SEER/EER used for calculation | Baseline Cost | Baseline Cost (2017 $) (Labor Not Included) | Baseline Cost/Ton (2017 $) (Labor Not Included)
Baseline - (IECC 2015)
Revelvant Catagories with Fedral Standard Changes. Baseline is Fedral Standard Change Jan 1, 2018 or Later. | [14 empty] | <65,000 Btu/h | Split System | 60000 | 5 | 14.0 SEER/8.0 HSPF | 14 | 2882.3667 | 3107.7493 | 621.5499
≥65,000 Btu/h and <135,000 Btu/h | Single- Packaged | 0 | 0 | 621.412 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 4870.198 | 4870.198 | 584.4238 | 1628.015
[15 empty] | <65,000 Btu/h | Single-Packaged | 60000 | 5 | 14.0 SEER/8.0 HSPF | 14 | 4469.8904 | 4819.407 | 963.8814
≥135,000 Btu/h and <240,000 Btu/h |  | 0 | 0 | 621.412 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 8717.9868 | 8717.9868 | 557.9512 | 1431.7733
[15 empty] | ≥65,000 Btu/h and <135,000 Btu/h | Single-Packaged | 100000 | 8.3333 | 11.0 EER/12.0 IEER | 11 | 10058.0317 | 10844.5051 | 1301.3406
≥240,000 Btu/h and <760,000 Btu/h |  | 0 | 0 | 621.412 | 5% | 15 | 5 | 4.3295 | 10.3797 | 0.41711 | 23186.1662 | 23186.1662 | 556.468 | 1349.2246
[15 empty] | ≥135,000 Btu/h and <240,000 Btu/h | Single-Packaged | 187500 | 15.625 | 10.6 EER/11.6 IEER | 10.6 | 18613.8614 | 20069.3456 | 1284.4381
[15 empty] | ≥240,000 Btu/h and <760,000 Btu/h | Single-Packaged | 500000 | 41.6667 | 9.5 EER/10.6 IEER | 9.5 | 49810.6219 | 53705.492 | 1288.9318
Baseline - (IECC 2012)
[15 empty] | <65,000 Btu/h | Split System | 60000 | 5 | 13.0 SEER/7.7 HSPF | 13 | 2334.0766 | 2516.5863 | 503.3173
Commercial HP Labor
Return To Master Summary | [9 empty] | type | mount | Tons | Labor Cost (2017$) |  | <65,000 Btu/h | Single-Packaged | 60000 | 5 | 13.0 SEER/7.7 HSPF | 13 | 4044.001 | 4360.2158 | 872.0432
[10 empty] | Split system | NA | NA | 3919.0703
[10 empty] | Packaged <65000 BTUH | NA | NA | 761.8233 |  | ≥65,000 Btu/h and <135,000 Btu/h | Single-Packaged | 100000 | 8.3333 | 11.0 EER/11.2 IEER | 11 | 10058.0317 | 10844.5051 | 1301.3406
[10 empty] | Packaged 65,000 to 240,000 BTUH | Ground | NA | 621.412
[10 empty] | Packaged 65,000 to 240,000 BTUH | Roof | NA | 607.834 |  | ≥135,000 Btu/h and <240,000 Btu/h | Single-Packaged | 187500 | 15.625 | 10.6 EER/10.7 IEER | 10.6 | 18613.8614 | 20069.3456 | 1284.4381
[15 empty] | ≥240,000 Btu/h and <760,000 Btu/h | Single-Packaged | 500000 | 41.6667 | 9.5 EER/9.6 IEER | 9.5 | 49810.6219 | 53705.492 | 1288.9318
2018 Federal Standard Changes - On or After 2018
[15 empty] | ≥65,000 Btu/h and <135,000 Btu/h | Single-Packaged | 100000 | 8.3333 | 12.0 IEER | 12 | 12006.5449 | 12945.3795 | 1553.4455
[15 empty] | ≥135,000 Btu/h and <240,000 Btu/h | Single-Packaged | 187500 | 15.625 | 11.4IEER | 11.4 | 20172.672 | 21750.0452 | 1392.0029
[15 empty] | ≥240,000 Btu/h and <760,000 Btu/h | Single-Packaged | 500000 | 41.6667 | 10.4 IEER | 10.4 | 51564.2838 | 55596.279 | 1334.3107
Note on L37: Barquest, Ethan: Beacuese model was deigned for EER inputs and on or after Jan, 1, federal changes are are the same as Tier 1 efrficenencies. Tier 1 measure costs calculated with EER are used for ER IMC to create a more accurate value

## VFD
EmPOWER Categories - VFD drives (>10HP) - Assumed Bypass | [6 empty] | EmPOWER Categories - VFD drives (>10HP) - NO Bypass | [7 empty] | Labor Costs
EmPower Incentive Levels Rated Motor Horsepower (HP) | Total Installed Costs (Labor Included) | [5 empty] | EmPower Incentive Levels Rated Motor Horsepower (HP) | Total Installed Costs (Incremental Cost) | [6 empty] | HP Equation Range | HP | Labor Costs | Labor Costs (2017 $)
| Assumed Bypass - yes, NEMA enclosure type =3 | Assumed Bypass - yes, NEMA enclosure type = 12 | Assumed Bypass - yes, NEMA enclosure type = 1 | Average IMC of EmPOWER Categories | Average IMC of EmPOWER Categories (2017$) |  |  | Assumed Bypass - No, NEMA enclosure type =3 | Assumed Bypass - No, NEMA enclosure type = 12 | Assumed Bypass - No,, NEMA enclosure type = 1 | Average IMC of EmPOWER Categories | Average IMC of EmPOWER Categories (2017$) |  |  | 3 to 10 HP | 2 | 545.6129 | 588.2764
15 | 4285.6955 | 3754.6595 | 3172.3955 | 3737.5835 | 4029.8385 |  | 15 | 3338.0075 | 2806.9715 | 2224.7075 | 2789.8955 | 3008.0474 |  |  |  | 3 | 564.6987 | 608.8545
20 | 4658.2522 | 4127.2162 | 3544.9522 | 4110.1402 | 4431.5267 |  | 20 | 3710.5642 | 3179.5282 | 2597.2642 | 3162.4522 | 3409.7356 |  |  |  | 4 | 583.7845 | 629.4326
25 | 5030.809 | 4499.773 | 3917.509 | 4482.697 | 4833.215 |  | 25 | 4083.121 | 3552.085 | 2969.821 | 3535.009 | 3811.4239 |  |  |  | 5 | 602.8702 | 650.0108
30 | 5403.3657 | 4872.3297 | 4290.0657 | 4855.2537 | 5234.9033 |  | 30 | 4455.6777 | 3924.6417 | 3342.3777 | 3907.5657 | 4213.1122 |  |  |  | 7.5 | 650.5846 | 701.4561
40 | 6148.4791 | 5617.4431 | 5035.1791 | 5600.3671 | 6038.2798 |  | 40 | 5200.7911 | 4669.7551 | 4087.4911 | 4652.6791 | 5016.4887 |  |  |  | 10 | 698.299 | 752.9015
50 | 6893.5926 | 6362.5566 | 5780.2926 | 6345.4806 | 6841.6563 |  | 50 | 5945.9046 | 5414.8686 | 4832.6046 | 5397.7926 | 5819.8652 |  |  | 15 to 50HP | 15 | 994.0021 | 1071.7266
60 | 8033.4047 | 7502.3687 | 6920.1047 | 7485.2927 | 8070.5944 |  | 60 | 7085.7167 | 6554.6807 | 5972.4167 | 6537.6047 | 7048.8033 |  |  |  | 20 | 1091.6388 | 1176.9979
75 | 8934.9113 | 8403.8753 | 7821.6113 | 8386.7993 | 9042.593 |  | 75 | 7987.2233 | 7456.1873 | 6873.9233 | 7439.1113 | 8020.8019 |  |  |  | 25 | 1189.2755 | 1282.2692
100 | 10437.4223 | 9906.3863 | 9324.1223 | 9889.3103 | 10662.5907 |  | 100 | 9489.7343 | 8958.6983 | 8376.4343 | 8941.6223 | 9640.7996 |  |  |  | 30 | 1286.9122 | 1387.5405
200 | 16447.4662 | 15916.4302 | 15334.1662 | 15899.3542 | 17142.5815 |  | 200 | 15499.7782 | 14968.7422 | 14386.4782 | 14951.6662 | 16120.7904 |  |  |  | 40 | 1482.1857 | 1598.0831
Note: Itron Calculations designed for 1- 100 HP. Itron Model looses robustness after 100 HP | [6 empty] | Note: Itron Calculations designed for 1- 100 HP. Itron Model looses robustness after 100 HP | [8 empty] | 50 | 1677.4591 | 1808.6257
[15 empty] | >50HP | 60 | 2267.4313 | 2444.7298
Return To Master Summary | [15 empty] | 75 | 2344.1779 | 2527.4775
[16 empty] | 100 | 2472.0888 | 2665.3903
[16 empty] | 200 | 2983.7328 | 3217.0415
EmPOWER Categories - VFD drives (<= 10HP) - Assumed Bypass | [9 empty] | EmPOWER Categories - VFD drives (<= 10HP) - No Bypass
Rated Motor Horsepower (HP) | Total Installed Costs (Incremental Cost) (Labor Included) | [8 empty] | Rated Motor Horsepower (HP) | Calculated Total Installed Costs (Labor Included)
| Assumed Bypass - yes, NEMA enclosure type =3, 500 volt = no | Assumed Bypass - yes, NEMA enclosure type = 12, 500 volt = no | Assumed Bypass - yes, NEMA enclosure type = 1, 500 volt = no | Assumed Bypass - yes, NEMA enclosure type =3, 500 volt = yes | Assumed Bypass - yes, NEMA enclosure type = 12, 500 volt = yes | Assumed Bypass - yes, NEMA enclosure type = 1, 500 volt = yes | Average IMC of EmPOWER Categories | Average IMC of EmPOWER Categories (2017$) |  |  | Assumed Bypass - No, NEMA enclosure type =3, 500 volt = no | Assumed Bypass - No, NEMA enclosure type = 12, 500 volt = no | Assumed Bypass - No,, NEMA enclosure type = 1, 500 volt = no | Assumed Bypass - No, NEMA enclosure type =3, 500 volt = yes | Assumed Bypass - No, NEMA enclosure type = 12, 500 volt = yes | Assumed Bypass - No,, NEMA enclosure type = 1, 500 volt = yes | Average IMC of EmPOWER Categories | Average IMC of EmPOWER Categories (2017$)
2 | 2668.4654 | 1742.3534 | 1444.0454 | 2805.8174 | 1879.7054 | 1581.3974 | 2020.2974 | 2178.2717 |  | 2 | 1782.6045 | 856.4925 | 558.1845 | 1919.9565 | 993.8445 | 695.5365 | 1134.4365 | 1223.1421
3 | 2745.1152 | 1819.0032 | 1520.6952 | 2882.4672 | 1956.3552 | 1658.0472 | 2096.9472 | 2260.9149 |  | 3 | 1840.1685 | 914.0565 | 615.7485 | 1977.5205 | 1051.4085 | 753.1005 | 1192.0005 | 1285.2072
4 | 2821.7649 | 1895.6529 | 1597.3449 | 2959.1169 | 2033.0049 | 1734.6969 | 2173.5969 | 2343.5582 |  | 4 | 1897.7325 | 971.6205 | 673.3125 | 2035.0845 | 1108.9725 | 810.6645 | 1249.5645 | 1347.2724
5 | 2898.4147 | 1972.3027 | 1673.9947 | 3035.7667 | 2109.6547 | 1811.3467 | 2250.2467 | 2426.2015 |  | 5 | 1955.2965 | 1029.1845 | 730.8765 | 2092.6485 | 1166.5365 | 868.2285 | 1307.1285 | 1409.3375
7.5 | 3042.3247 | 2116.2127 | 1817.9047 | 3179.6767 | 2253.5647 | 1955.2567 | 2394.1567 | 2581.3643 |  | 7.5 | 2099.2065 | 1173.0945 | 874.7865 | 2236.5585 | 1310.4465 | 1012.1385 | 1451.0385 | 1564.5003
10 | 3186.2347 | 2260.1227 | 1961.8147 | 3323.5867 | 2397.4747 | 2099.1667 | 2538.0667 | 2736.5272 |  | 10 | 2243.1165 | 1317.0045 | 1018.6965 | 2380.4685 | 1454.3565 | 1156.0485 | 1594.9485 | 1719.6632
Return To Master Summary

## VFD_Calculator
EmPOWER Categories - VFD drives (>10HP) - Assumed Bypass | [6 empty] | EmPOWER Categories - VFD drives (>10HP) - NO Bypass | [5 empty] | Fan VFDs (>10hp) | Mid-A TRM IC | Calculated Cost Itron | [6 empty] | Labor Costs
EmPower Incentive Levels Rated Motor Horsepower (HP) | Total Installed Costs (Incremental Cost) | [5 empty] | EmPower Incentive Levels Rated Motor Horsepower (HP) | Total Installed Costs (Incremental Cost) |  |  |  |  | Rated Motor Horsepower (HP) | Total Installed Costs (Incremental Cost) | Total Installed Costs (Incremental Cost) (Labor Included) | [6 empty] | HP | HP | Labor Costs | Labor Costs (2017 $)
| Assumed Bypass - yes, NEMA enclosure type =3 | Assumed Bypass - yes, NEMA enclosure type = 12 | Assumed Bypass - yes, NEMA enclosure type = 1 | Average IMC of EmPOWER Categories | Average IMC of EmPOWER Categories (2017$) |  |  | Assumed Bypass - No, NEMA enclosure type =3 | Assumed Bypass - No, NEMA enclosure type = 12 | Assumed Bypass - No,, NEMA enclosure type = 1 | Average IMC of EmPOWER Categories (2017$) | Average IMC of EmPOWER Categories (2017$) |  |  | Assumed Bypass - yes, NEMA enclosure type =3 | Assumed Bypass - yes, NEMA enclosure type = 12 | Assumed Bypass - yes, NEMA enclosure type = 1 | Assumed Bypass - No, NEMA enclosure type =3 | Assumed Bypass - No, NEMA enclosure type = 12 | Assumed Bypass - No,, NEMA enclosure type = 1 |  | 3 to 10 HP | 2 | 545.6129 | 588.2764
15 | 4285.6955 | 3754.6595 | 3172.3955 | 3737.5835 | 4029.8385 |  | 15 | 3338.0075 | 2806.9715 | 2224.7075 | 2789.8955 | 3008.0474 | 15 | 3193 | 4285.6955 | 3754.6595 | 3172.3955 | 3338.0075 | 2806.9715 | 2224.7075 |  |  | 3 | 564.6987 | 608.8545
20 | 4658.2522 | 4127.2162 | 3544.9522 | 4110.1402 | 4431.5267 |  | 20 | 3710.5642 | 3179.5282 | 2597.2642 | 3162.4522 | 3409.7356 | 25 | 4260 | 5030.809 | 4499.773 | 3917.509 | 4083.121 | 3552.085 | 2969.821 |  |  | 4 | 583.7845 | 629.4326
25 | 5030.809 | 4499.773 | 3917.509 | 4482.697 | 4833.215 |  | 25 | 4083.121 | 3552.085 | 2969.821 | 3535.009 | 3811.4239 | 50 | 6448 | 6503.0457 | 5972.0097 | 5389.7457 | 5555.3577 | 5024.3217 | 4442.0577 |  |  | 5 | 602.8702 | 650.0108
30 | 5403.3657 | 4872.3297 | 4290.0657 | 4855.2537 | 5234.9033 |  | 30 | 4455.6777 | 3924.6417 | 3342.3777 | 3907.5657 | 4213.1122 | 75 | 8407 | 8934.9113 | 8403.8753 | 7821.6113 | 7987.2233 | 7456.1873 | 6873.9233 |  |  | 7.5 | 650.5846 | 701.4561
40 | 6148.4791 | 5617.4431 | 5035.1791 | 5600.3671 | 6038.2798 |  | 40 | 5200.7911 | 4669.7551 | 4087.4911 | 4652.6791 | 5016.4887 | 100 | 10493 | 10437.4223 | 9906.3863 | 9324.1223 | 9489.7343 | 8958.6983 | 8376.4343 |  |  | 10 | 698.299 | 752.9015
50 | 6893.5926 | 6362.5566 | 5780.2926 | 6345.4806 | 6841.6563 |  | 50 | 5945.9046 | 5414.8686 | 4832.6046 | 5397.7926 | 5819.8652 | 200 | 17266 | 16447.4662 | 15916.4302 | 15334.1662 | 15499.7782 | 14968.7422 | 14386.4782 |  | 15 to 50HP | 15 | 994.0021 | 1071.7266
60 | 8033.4047 | 7502.3687 | 6920.1047 | 7485.2927 | 8070.5944 |  | 60 | 7085.7167 | 6554.6807 | 5972.4167 | 6537.6047 | 7048.8033 | Note: Itron Calculations designed for 1- 100 HP. Itron Model looses robustness after 200 HP | [9 empty] | 20 | 1091.6388 | 1176.9979
75 | 8934.9113 | 8403.8753 | 7821.6113 | 8386.7993 | 9042.593 |  | 75 | 7987.2233 | 7456.1873 | 6873.9233 | 7439.1113 | 8020.8019 | [10 empty] | 25 | 1189.2755 | 1282.2692
100 | 10437.4223 | 9906.3863 | 9324.1223 | 9889.3103 | 10662.5907 |  | 100 | 9489.7343 | 8958.6983 | 8376.4343 | 8941.6223 | 9640.7996 | Fan VFDs (>10hp) | Mid-A TRM IC | Calculated Cost Itron (2017 $) | [7 empty] | 30 | 1286.9122 | 1387.5405
200 | 16447.4662 | 15916.4302 | 15334.1662 | 15899.3542 | 17142.5815 |  | 200 | 15499.7782 | 14968.7422 | 14386.4782 | 14951.6662 | 16120.7904 | Rated Motor Horsepower (HP) | Total Installed Costs (Incremental Cost) (2017 $) | Total Installed Costs (Incremental Cost) (Labor Included) | [7 empty] | 40 | 1482.1857 | 1598.0831
[15 empty] | Assumed Bypass - yes, NEMA enclosure type =3 | Assumed Bypass - yes, NEMA enclosure type = 12 | Assumed Bypass - yes, NEMA enclosure type = 1 | Assumed Bypass - No, NEMA enclosure type =3 | Assumed Bypass - No, NEMA enclosure type = 12 | Assumed Bypass - No,, NEMA enclosure type = 1 |  |  | 50 | 1677.4591 | 1808.6257
EmPOWER Categories - VFD drives (<= 10HP) - Assumed Bypass | [12 empty] | 15 | 3442.6721 | 4620.8093 | 4048.2497 | 3420.4564 | 3599.0182 | 3026.4586 | 2398.6653 |  | >50HP | 60 | 2267.4313 | 2444.7298
Rated Motor Horsepower (HP) | Total Installed Costs (Incremental Cost) (Labor Included) | [9 empty] | Return To Master Summary |  | 25 | 4593.1046 | 5424.1858 | 4851.6262 | 4223.8329 | 4402.3947 | 3829.8351 | 3202.0418 |  |  | 75 | 2344.1779 | 2527.4775
| Assumed Bypass - yes, NEMA enclosure type =3, 500 volt = no | Assumed Bypass - yes, NEMA enclosure type = 12, 500 volt = no | Assumed Bypass - yes, NEMA enclosure type = 1, 500 volt = no | Assumed Bypass - yes, NEMA enclosure type =3, 500 volt = yes | Assumed Bypass - yes, NEMA enclosure type = 12, 500 volt = yes | Assumed Bypass - yes, NEMA enclosure type = 1, 500 volt = yes | Average IMC of EmPOWER Categories | Average IMC of EmPOWER Categories (2017$) |  |  |  |  | 50 | 6952.1921 | 7011.542 | 6438.9824 | 5811.1891 | 5989.7509 | 5417.1913 | 4789.398 |  |  | 100 | 2472.0888 | 2665.3903
2 | 2668.4654 | 1742.3534 | 1444.0454 | 2805.8174 | 1879.7054 | 1581.3974 | 2020.2974 | 2178.2717 |  |  |  |  | 75 | 9064.3733 | 9633.5639 | 9061.0043 | 8433.211 | 8611.7728 | 8039.2132 | 7411.4199 |  |  | 200 | 2983.7328 | 3217.0415
3 | 2745.1152 | 1819.0032 | 1520.6952 | 2882.4672 | 1956.3552 | 1658.0472 | 2096.9472 | 2260.9149 |  |  |  |  | 100 | 11313.4851 | 11253.5615 | 10681.0019 | 10053.2086 | 10231.7704 | 9659.2108 | 9031.4175
4 | 2821.7649 | 1895.6529 | 1597.3449 | 2959.1169 | 2033.0049 | 1734.6969 | 2173.5969 | 2343.5582 |  |  |  |  | 200 | 18616.0901 | 17733.5523 | 17160.9927 | 16533.1994 | 16711.7612 | 16139.2016 | 15511.4083
5 | 2898.4147 | 1972.3027 | 1673.9947 | 3035.7667 | 2109.6547 | 1811.3467 | 2250.2467 | 2426.2015
7.5 | 3042.3247 | 2116.2127 | 1817.9047 | 3179.6767 | 2253.5647 | 1955.2567 | 2394.1567 | 2581.3643 |  |  |  |  | Fan VFDs (<=10hp) | Mid-A TRM Incremental Cost | Calculated Cost Itron (Labor Included)
10 | 3186.2347 | 2260.1227 | 1961.8147 | 3323.5867 | 2397.4747 | 2099.1667 | 2538.0667 | 2736.5272 |  |  |  |  | Rated Motor Horsepower (HP) |  | Total Installed Costs (Incremental Cost)
[15 empty] | Assumed Bypass - yes, NEMA enclosure type =3, 500 volt = no | Assumed Bypass - yes, NEMA enclosure type = 12, 500 volt = no | Assumed Bypass - yes, NEMA enclosure type = 1, 500 volt = no | Assumed Bypass - No, NEMA enclosure type =3, 500 volt = no | Assumed Bypass - No, NEMA enclosure type = 12, 500 volt = no | Assumed Bypass - No,, NEMA enclosure type = 1, 500 volt = no | Assumed Bypass - yes, NEMA enclosure type =3, 500 volt = yes | Assumed Bypass - yes, NEMA enclosure type = 12, 500 volt = yes | Assumed Bypass - yes, NEMA enclosure type = 1, 500 volt = yes | Assumed Bypass - No, NEMA enclosure type =3, 500 volt = yes | Assumed Bypass - No, NEMA enclosure type = 12, 500 volt = yes | Assumed Bypass - No,, NEMA enclosure type = 1, 500 volt = yes
EmPOWER Categories - VFD drives (<= 10HP) - No Bypass | [12 empty] | 5 | 2125 | 2841.1574 | 1915.0454 | 1616.7374 | 2500.9094 | 1574.7974 | 1276.4894 | 2978.5094 | 2052.3974 | 1754.0894 | 2638.2614 | 1712.1494 | 1413.8414
Rated Motor Horsepower (HP) | Total Installed Costs (Incremental Cost) (Labor Included)
| Assumed Bypass - No, NEMA enclosure type =3, 500 volt = no | Assumed Bypass - No, NEMA enclosure type = 12, 500 volt = no | Assumed Bypass - No,, NEMA enclosure type = 1, 500 volt = no | Assumed Bypass - No, NEMA enclosure type =3, 500 volt = yes | Assumed Bypass - No, NEMA enclosure type = 12, 500 volt = yes | Assumed Bypass - No,, NEMA enclosure type = 1, 500 volt = yes | Average IMC of EmPOWER Categories | Average IMC of EmPOWER Categories (2017$) |  |  |  |  | Fan VFDs (<=10hp) | Mid-A TRM Incremental Cost (2017 $) | Calculated Cost Itron (2017 $) (Labor Included)
2 | 2328.2174 | 1402.1054 | 1103.7974 | 2465.5694 | 1539.4574 | 1241.1494 | 1680.0494 | 1811.4185 |  |  |  |  | Rated Motor Horsepower (HP) |  | Total Installed Costs (Incremental Cost)
3 | 2404.8672 | 1478.7552 | 1180.4472 | 2542.2192 | 1616.1072 | 1317.7992 | 1756.6992 | 1894.0617 | [6 empty] | Assumed Bypass - yes, NEMA enclosure type =3, 500 volt = no | Assumed Bypass - yes, NEMA enclosure type = 12, 500 volt = no | Assumed Bypass - yes, NEMA enclosure type = 1, 500 volt = no | Assumed Bypass - No, NEMA enclosure type =3, 500 volt = no | Assumed Bypass - No, NEMA enclosure type = 12, 500 volt = no | Assumed Bypass - No,, NEMA enclosure type = 1, 500 volt = no | Assumed Bypass - yes, NEMA enclosure type =3, 500 volt = yes | Assumed Bypass - yes, NEMA enclosure type = 12, 500 volt = yes | Assumed Bypass - yes, NEMA enclosure type = 1, 500 volt = yes | Assumed Bypass - No, NEMA enclosure type =3, 500 volt = yes | Assumed Bypass - No, NEMA enclosure type = 12, 500 volt = yes | Assumed Bypass - No,, NEMA enclosure type = 1, 500 volt = yes
4 | 2481.5169 | 1555.4049 | 1257.0969 | 2618.8689 | 1692.7569 | 1394.4489 | 1833.3489 | 1976.705 |  |  |  |  | 5 | 2291.1613 | 3267.6421 | 2226.8048 | 1911.1681 | 2846.7015 | 1866.7918 | 1551.1552 | 3352.0453 | 2372.1355 | 2056.4989 | 2992.0323 | 2012.1226 | 1696.4859
5 | 2558.1667 | 1632.0547 | 1333.7467 | 2695.5187 | 1769.4067 | 1471.0987 | 1909.9987 | 2059.3483
7.5 | 2702.0767 | 1775.9647 | 1477.6567 | 2839.4287 | 1913.3167 | 1615.0087 | 2053.9087 | 2214.5111
10 | 2845.9867 | 1919.8747 | 1621.5667 | 2983.3387 | 2057.2267 | 1758.9187 | 2197.8187 | 2369.674 |  |  |  |  | Return To Master Summary

## Residential Clothes Washer
Time of Sale |  | Front Loading | Top Loading |  | Early Replacement |  | Front Loading | Top Loading
Before Jan 1, 2018 | ENERGY STAR, CEE Tier 1 | 16.8256 | 16.8256 |  | Before Jan 1, 2018 | ENERGY STAR, CEE Tier 1 | 443.8051 | 348.4843
| ENERGY STAR Most Efficient, CEE TIER 2 | 28.0426 | 28.0426 |  |  | ENERGY STAR Most Efficient, CEE TIER 2 | 455.0222 | 377.8498
| CEE TIER 3 | 33.6512 | 33.6512 |  |  | CEE TIER 3 | 460.6307 | NA
After Jan 1, 2018 | ENERGY STAR, CEE Tier 1 | 16.8256 | 20.5558 |  | After Jan 1, 2018 | ENERGY STAR, CEE Tier 1 | 443.8051 | 353.6219
| ENERGY STAR Most Efficient, CEE TIER 2 | 28.0426 | 49.9213 |  |  | ENERGY STAR Most Efficient, CEE TIER 2 | 455.0222 | 455.0222
| CEE TIER 3 | 33.6512 | NA |  |  | CEE TIER 3 | 427.2245 | NA
Recommended Incremental Costs - Front Loading Clothes Washers | [8 empty] | Recommended Incremental Costs - Top Loading Clothes Washers | [9 empty] | Recommended Incremental Costs - Front Loading Clothes Washers | [8 empty] | Recommended Incremental Costs - Top Loading Clothes Washers
Time Period | Efficiency Level | IMEF | Compartment Capacity | Components |  | Time of Sale | Early Replacement |  | Time Period | Efficiency Level | IMEF | Compartment Capacity | Components |  | Time of Sale | Early Replacement |  |  | Time Period | Efficiency Level | IMEF | Compartment Capacity | Components |  | Time of Sale | Early Replacement |  | Time Period | Efficiency Level | IMEF | Compartment Capacity | Components |  | Time of Sale | Early Replacement
|  |  |  | Base Case Equipment Cost ($2017) | Measure Equipment Cost per Unit ($2017) | Incremental Cost per Unit ($2017) | Incremental Cost per Unit ($2017) | [5 empty] | Base Case Equipment Cost ($2017) | Measure Equipment Cost per Unit ($2017) | Incremental Cost per Unit ($2017) | Incremental Cost per Unit ($2017) | [6 empty] | Base Case Equipment Cost ($2017) | Measure Equipment Cost per Unit ($2017) | Incremental Cost per Unit ($2017) | Incremental Cost per Unit ($2017) | [5 empty] | Base Case Equipment Cost ($2017) | Measure Equipment Cost per Unit ($2017) | Incremental Cost per Unit ($2017) | Incremental Cost per Unit ($2017)
Before Jan 1, 2018 | ENERGY STAR, CEE Tier 1 | 2.38 | 3.5 | 724.4077 | 741.2333 | 16.8256 | 333.6677 |  | Before Jan, 1, 2018 | ENERGY STAR, CEE Tier 1 | 2.38 | 3.5 | 504.0998 | 536.4018 | 32.302 | 252.7857 |  |  | After Jan, 1, 2018 | ENERGY STAR, CEE Tier 1 | 2.38 | 3.5 | 724.4077 | 741.2333 | 16.8256 | 333.6677 |  | After Jan, 1, 2018 | ENERGY STAR, CEE Tier 1 | 2.38 | 3.5 | 515.846 | 536.4018 | 20.5558 | 257.9232
| ENERGY STAR Most Efficient, CEE TIER 2 | 2.74 |  |  | 752.4503 | 28.0426 | 344.8847 |  |  | ENERGY STAR Most Efficient, CEE TIER 2 | 2.74 |  |  | 565.7673 | 61.6675 | 282.1511 |  |  |  | ENERGY STAR Most Efficient, CEE TIER 2 | 2.74 |  |  | 752.4503 | 28.0426 | 344.8847 |  |  | ENERGY STAR Most Efficient, CEE TIER 2 | 2.74 |  |  | 565.7673 | 49.9213 | 287.2887
| CEE TIER 3 | 2.92 |  |  | 758.0588 | 33.6512 | 350.4933 |  |  | CEE TIER 3 | 2.92 |  |  | NA | NA | NA |  |  |  | CEE TIER 3 | 2.92 |  |  | 758.0588 | 33.6512 | 350.4933 |  |  | CEE TIER 3 | 2.92 |  |  | NA | NA | NA
| ENERGY STAR, CEE Tier 1 | 2.38 | 4.5 | 976.2189 | 993.0445 | 16.8256 | 443.8051 |  |  | ENERGY STAR, CEE Tier 1 | 2.38 | 4.5 | 722.8991 | 755.2012 | 32.302 | 348.4843 |  |  |  | ENERGY STAR, CEE Tier 1 | 2.38 | 4.5 | 976.2189 | 993.0445 | 16.8256 | 443.8051 |  |  | ENERGY STAR, CEE Tier 1 | 2.38 | 4.5 | 734.6453 | 755.2012 | 20.5558 | 353.6219
| ENERGY STAR Most Efficient, CEE TIER 2 | 2.74 |  |  | 1004.2616 | 28.0426 | 455.0222 |  |  | ENERGY STAR Most Efficient, CEE TIER 2 | 2.74 |  |  | 784.5666 | 61.6675 | 377.8498 |  |  |  | ENERGY STAR Most Efficient, CEE TIER 2 | 2.74 |  |  | 1004.2616 | 28.0426 | 455.0222 |  |  | ENERGY STAR Most Efficient, CEE TIER 2 | 2.74 |  |  | 784.5666 | 49.9213 | 455.0222
| CEE TIER 3 | 2.92 |  |  | 1009.8701 | 33.6512 | 460.6307 |  |  | CEE TIER 3 | 2.92 |  |  | NA | NA | NA |  |  |  | CEE TIER 3 | 2.92 |  |  | 1009.8701 | 33.6512 | 427.2245 |  |  | CEE TIER 3 | 2.92 |  |  | NA | NA | NA
Return To Master Summary
Calculations with Clothes Washers Federal Standards (Before Jan 1, 2018) as baseline
Efficiency Level | Federal Baseline from TRM |  | Efficient Criteria Based on TRM |  | Baseline Cost |  |  |  | Efficient Condition Cost |  |  |  | Incremental Costs - Time of Sale |  |  |  | Lifecycle Retrofit/Early Replacement Incremental Cost Calculator
| Front Loading (IMEF) | Top Loading (IMEF) | Integrated Modified Energy Factor (IMEF) |  | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Labor | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment |  |  |  | Lifecycle Retrofit/Early Replacement Incremental Cost
[5 empty] | 4.5 | 3.5 | 4.5 | 3.5 | 4.5 | 3.5 | 4.5 | 3.5 | 4.5 | 3.5 | 4.5 | 3.5 | [7 empty] | Capacity 4.5 | Capacity 3.5 | Capacity 4.5 | Capacity 3.5 | Capacity 4.5 | Capacity 3.5 | Capacity 4.5 | Capacity 3.5
|  |  | Front Loading | Top Loading | Front Loading |  | Top Loading |  | Front Loading |  | Top Loading |  | Front Loading |  | Top Loading | [8 empty] | Front Loading | Front Loading | Top Loading | Top Loading | Front Loading | Front Loading | Top Loading | Top Loading
ENERGY STAR, CEE Tier 1 | 1.84 | 1.29 | 2.38 | 2.06 | 905.4209 | 671.8716 | 670.4725 | 467.5411 | 921.0262 | 687.477 | 700.4319 | 497.5005 | 15.6053 | 15.6053 | 29.9594 | 29.9594 | Itron MCS does not consider cost for Residential Clothes Washers | 5% | 14 | 5 | 4.3295 | 9.8986 | 0.43738 | 396.0138 | 293.8638 | 293.2519 | 204.4936 | 411.6192 | 309.4692 | 323.2113 | 234.4529
ENERGY STAR Most Efficient, CEE TIER 2 |  |  | 2.74 | 2.76 |  |  |  |  | 931.4298 | 697.8805 | 727.6677 | 524.7363 | 26.0089 | 26.0089 | 57.1952 | 57.1952 |  | 5% | 14 | 5 | 4.3295 | 9.8986 | 0.43738 |  |  |  |  | 422.0227 | 319.8727 | 350.4471 | 261.6888
CEE TIER 3 |  |  | 2.92 | n/a |  |  |  |  | 936.6316 | 703.0823 | NA | NA | 31.2107 | 31.2107 | NA | NA |  | 5% | 14 | 5 | 4.3295 | 9.8986 | 0.43738 |  |  |  |  | 427.2245 | 325.0745 | NA | NA
2017 $ Adjusted
ENERGY STAR, CEE Tier 1 | 1.84 | 1.29 | 2.38 | 2.06 | 976.2189 | 724.4077 | 722.8991 | 504.0998 | 993.0445 | 741.2333 | 755.2012 | 536.4018 | 16.8256 | 16.8256 | 32.302 | 32.302 | Itron MCS does not consider cost for Residential Clothes Washers | 5% | 14 | 5 | 4.3295 | 9.8986 | 0.43738 | 426.9795 | 316.8421 | 316.1823 | 220.4836 | 443.8051 | 333.6677 | 348.4843 | 252.7857
ENERGY STAR Most Efficient, CEE TIER 2 |  |  | 2.74 | 2.76 |  |  |  |  | 1004.2616 | 752.4503 | 784.5666 | 565.7673 | 28.0426 | 28.0426 | 61.6675 | 61.6675 |  | 5% | 14 | 5 | 4.3295 | 9.8986 | 0.43738 |  |  |  |  | 455.0222 | 344.8847 | 377.8498 | 282.1511
CEE TIER 3 |  |  | 2.92 | n/a |  |  |  |  | 1009.8701 | 758.0588 | NA | NA | 33.6512 | 33.6512 | NA | NA |  | 5% | 14 | 5 | 4.3295 | 9.8986 | 0.43738 |  |  |  |  | 460.6307 | 350.4933 | NA | NA
Calculations with Clothes Washers Federal Standards (Jan 1, 2018 or after) as baseline | [16 empty] | Lifecycle Retrofit/Early Replacement Incremental Cost Calculator
Efficiency Level | Federal Baseline from TRM |  | Efficient Criteria Based on TRM |  | Baseline Cost |  |  |  | Efficient Condition Cost |  |  |  | Incremental Costs - Time of Sale
| Front Loading (IMEF) | Top Loading (IMEF) | Integrated Modified Energy Factor (IMEF) |  | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Assumed Compartment Capacity | Labor | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment |  |  |  | Lifecycle Retrofit/Early Replacement Incremental Cost
[5 empty] | 4.5 | 3.5 | 4.5 | 3.5 | 4.5 | 3.5 | 4.5 | 3.5 | 4.5 | 3.5 | 4.5 | 3.5 | [7 empty] | Capacity 4.5 | Capacity 3.5 | Capacity 4.5 | Capacity 3.5 | Capacity 4.5 | Capacity 3.5 | Capacity 4.5 | Capacity 3.5
|  |  | Front Loading | Top Loading | Front Loading |  | Top Loading |  | Front Loading |  | Top Loading |  | Front Loading |  | Top Loading | [8 empty] | Front Loading | Front Loading | Top Loading | Top Loading | Front Loading | Front Loading | Top Loading | Top Loading
ENERGY STAR, CEE Tier 1 | 1.84 | 1.57 | 2.38 | 2.06 | 905.4209 | 671.8716 | 681.3668 | 478.4354 | 921.0262 | 687.477 | 700.4319 | 497.5005 | 15.6053 | 15.6053 | 29.9594 | 29.9594 | Itron MCS does not consider cost for Residential Clothes Washers | 5% | 14 | 5 | 4.3295 | 9.8986 | 0.43738 | 396.0138 | 293.8638 | 298.0168 | 209.2585 | 411.6192 | 309.4692 | 327.9762 | 239.2179
ENERGY STAR Most Efficient, CEE TIER 2 |  |  | 2.74 | 2.76 |  |  |  |  | 931.4298 | 697.8805 | 727.6677 | 524.7363 | 26.0089 | 26.0089 | 57.1952 | 57.1952 |  | 5% | 14 | 5 | 4.3295 | 9.8986 | 0.43738 |  |  |  |  | 422.0227 | 319.8727 | 355.212 | 266.4537
CEE TIER 3 |  |  | 2.92 | n/a |  |  |  |  | 936.6316 | 703.0823 | NA | NA | 31.2107 | 31.2107 | NA | NA |  | 5% | 14 | 5 | 4.3295 | 9.8986 | 0.43738 |  |  |  |  | 427.2245 | 325.0745 | NA | NA
2017 $ Adjusted
ENERGY STAR, CEE Tier 1 | 1.84 | 1.57 | 2.38 | 2.06 | 976.2189 | 724.4077 | 734.6453 | 515.846 | 993.0445 | 741.2333 | 755.2012 | 536.4018 | 16.8256 | 16.8256 | 32.302 | 32.302 | Itron MCS does not consider cost for Residential Clothes Washers | 5% | 14 | 5 | 4.3295 | 9.8986 | 0.43738 | 426.9795 | 316.8421 | 321.3198 | 225.6212 | 443.8051 | 333.6677 | 353.6219 | 257.9232
ENERGY STAR Most Efficient, CEE TIER 2 |  |  | 2.74 | 2.76 |  |  |  |  | 1004.2616 | 752.4503 | 784.5666 | 565.7673 | 28.0426 | 28.0426 | 61.6675 | 61.6675 |  | 5% | 14 | 5 | 4.3295 | 9.8986 | 0.43738 |  |  |  |  | 455.0222 | 344.8847 | 382.9873 | 287.2887
CEE TIER 3 |  |  | 2.92 | n/a |  |  |  |  | 1009.8701 | 758.0588 | NA | NA | 33.6512 | 33.6512 | NA | NA |  | 5% | 14 | 5 | 4.3295 | 9.8986 | 0.43738 |  |  |  |  | 460.6307 | 350.4933 | NA | NA

## Comm_MidATRM_Mini Ductless HP
The full installed cost of the ductless mini-split system is shown below[1]. |  |  |  |  | The full installed cost of the baseline equipment is shown below. |  | [1] Navigant, Inc. Incremental Cost Study Phase 2. January 16, 2013. Table 16.
Capacity (kBtu/h) | Efficiency |  |  |  | Unit | Cost | [2] Energy Star Calculator. http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/CalculatorConsumerRoomAC.xls)
| 13 SEER | 18 SEER | 21 SEER | 26 SEER | Window AC[2] | $170/unit | [3] Energy Star Calculator. 46% added to value to reflect labor, based on ratio of equipment to labor cost for measure EffFurn-cond-90AFUE in DEER database. http://www.energystar.gov/buildings/sites/default/uploads/files/Furnace_Calculator.xls?8178-e52c
9 | 2733 | 3078 | 3236 | 3460 | Gas furnace[3] | $1,606/unit | [4] If existing case is electric resistance heat, assume project replaces existing functional baseboard.
12 | 2803 | 3138 | 3407 | 3363 | Electric Baseboard[4] | 0
18 | 3016 | 3374 | 3640 | N/A
24 | 3273 | 3874 | N/A | N/A
Return To Master Summary
Incremental Cost - Baseline Widow AC
Capacity (kBtu/h) | Efficiency
| 13 SEER | 18 SEER | 21 SEER | 26 SEER
9 | 2563 | 2908 | 3066 | 3290
12 | 2633 | 2968 | 3237 | 3193
18 | 2846 | 3204 | 3470 | N/A
24 | 3103 | 3704 | N/A | N/A
Incremental Cost - Baseline Gas Furnace
Capacity (kBtu/h) | Efficiency
| 13 SEER | 18 SEER | 21 SEER | 26 SEER
9 | 1127 | 1472 | 1630 | 1854
12 | 1197 | 1532 | 1801 | 1757
18 | 1410 | 1768 | 2034 | N/A
24 | 1667 | 2268 | N/A | N/A
Incremental Cost- Baseline Electric Baseboard
Capacity (kBtu/h) | Efficiency
| 13 SEER | 18 SEER | 21 SEER | 26 SEER
9 | 2733 | 3078 | 3236 | 3460
12 | 2803 | 3138 | 3407 | 3363
18 | 3016 | 3374 | 3640 | N/A
24 | 3273 | 3874 | N/A | N/A
Return To Master Summary

## Res Mini Ductless HP
Incremental Cost Calculations ($2017) | [11 empty] | For Reference Only
Capacity (tons) | ASHP Labor Adjusted for Maryland Labor Rates | Real Discount Rate | EUL | RUL | Baseline Cost (assumes ASHP) |  | PV Real Levelized Carrying Charge for Existing DSHP | PV Real Levelized Carrying Charge for New DSHP | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost | From TRM V6
[6 empty] | Time of Sale Incremental Cost (1) | [5 empty] | Unit Size | Time of Sale | Initial Measure Cost
1 | 555.5718 | 5% | 18 | 6 | 937.1366 | 266.6667 | 5.0757 | 11.6896 | 0.43421 | 648.1434 | 914.81 | 1-Ton | 603 | 3000
1.5 |  | 5% | 18 | 6 | 1405.7049 | 400 | 5.0757 | 11.6896 | 0.43421 | 851.5987 | 1251.5987 | 1.5-Ton | 624 | 3750
2 |  | 5% | 18 | 6 | 1874.2732 | 533.3333 | 5.0757 | 11.6896 | 0.43421 | 1055.054 | 1588.3873 | 2-Ton | 601 | 4500
2.5 |  | 5% | 18 | 6 | 2342.8415 | 666.6667 | 5.0757 | 11.6896 | 0.43421 | 1258.5093 | 1925.1759 | 2.5-Ton | 600 | 5250
3 |  | 5% | 18 | 6 | 2811.4098 | 800 | 5.0757 | 11.6896 | 0.43421 | 1461.9646 | 2261.9646 | 3-Ton | 600 | 6000
Homewyse.com calculator gives ~$400 difference between SEER 15 and SEER 20 units, with total installed cost for SEER 15 about $6k and SEER 20 at $6.4k, assuming 18kBTU (1.5 ton) capacity units. These values assume increemntal costs are proportinal to capacity. Homewyse values are based on four distributor web sites, which are listed on Homewyse webpage (see https://www.homewyse.com/costs/cost_of_ductless_heat_pump_systems.html).
Return To Master Summary

## TRM Res HP Air Source IC
Time of Sale
Efficiency (SEER) | Incremental Cost per Ton of Capacity
| Mid - A TRM | IL TRM | CPUC Avg IMC (per Ton)
15 | 170 | 137 | 182.76
16 | 340 | 274 | 365.52
17 | 529 | 411 | 548.29
18 | 710 | 548 | 731.05
Early Replacement
Efficiency (SEER) | Full Retrofit Cost (including labor) per Ton of Capacity ($/ton)
| Mid - A TRM | IL TRM
15 | 2544 | 1518
16 | 3120 | 1655
17 | 3309 | 1792
18 | 3614 | 1929
The capital cost for this measure is the actual cost of removing the existing unit and installing the new one.
Return To Master Summary

## TRM V6 ResCAC
Res CAC
TOS
Efficiency Level | Cost per Ton
SEER 15 | 92
SEER 16 | 184
SEER 17 | 276
SEER 18 | 369
SEER 19 | 461
SEER 20 | 553
SEER 21 | 645
ER
Efficiency (SEER) | Full Retrofit Cost (including labor) per Ton of Capacity ($/ton)
15 | 2403
16 | 2495
17 | 2588
18 | 2680
19 | 2772
20 | 2864
21 | 2956

## TRM Comm Unitary HVAC IC
Incremental Costs
Air-Cooled Unitary Air Conditioners - Time of Sale and New Construction |  |  | Note: | "Incremental costs for water- and evaporatively-cooled ACs, PTACs, and PTHPs will be addressed in subsequent versions of the TRM. In the interim, incremental costs for these equipment types should be determined on a site-specific basis."
Size Category | Efficient Condition (CEE Tier 1) | Efficient Condition (CEE Tier 2)
>=65,000 Btu/h and <135,000 | $62.96/ton | $125.92/ton
>=135,000 Btu/h and <240,000 Btu/h | $62.96/ton | $125.92/ton
>=240,000 Btu/h and <760,000 Btu/h | $18.78/ton | $37.56/ton
Air-Source Unitary Heat Pumps - Time of Sale and New Construction
Size Category | Efficient Condition (CEE Tier 1) | Efficient Condition (CEE Tier 2)
<65,000 Btu/h | $443/unit | $886/ton
>=65,000 Btu/h and <135,000 | $62.96/ton | $125.92/ton
>=135,000 Btu/h and <240,000 Btu/h | $62.96/ton | $125.92/ton
>=240,000 Btu/h and <760,000 Btu/h | $18.78/ton | $37.56/ton
Early Replacement
"If the measure is an early replacement, the full installed cost of the efficient unit should be used as the incremental cost and determined on a site-specific basis."
Return To Master Summary

## RES_Small_Gas_WH_Calcs
Recommended Incremental Costs
Gas Storage | 159.067
Tankless Gas | 406.9594
Mid-A TRM Baseline Conditions |  | Calculated Baseline Cost |  | Mid-A TRM Efficiency Measure Conditions |  | Calculated Measure Cost |  |  | IMC - TOS |  | Lifecycle Retrofit/Early Replacement Incremental Cost Calculator - $2017
Size (gallons) | Efficiency Rating | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Water Heater Type | Energy Factor (Energy Star Minimum) | Rated Volume (gallons)or Capacity (MBTU) | Cost (min eff) | Cost (min eff) (2017 $) | Incremental Cost | Incremental Cost (2017 $) | Labor | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost ASHP
40 | 0.615 | 632.1083 | 681.5351 | Gas Storage | 0.67 | 40 | 779.6394 | 840.6021 | 147.531 | 159.067 | 290.6709 | 5% | 13 | 4.3333 | 3.8114 | 9.3936 | 0.40574 | 459.0071 | 618.0741
|  |  |  | Whole Home Gas Tankless | 0.82 | 180 | 1009.5539 | 1088.4945 | 377.4456 | 406.9594 | 387.4669 | 5% | 13 | 4.3333 | 3.8114 | 9.3936 | 0.40574 | 598.8623 | 1005.8217
Return To Master Summary
Labor Costs
WH Type | Gal | Labor Costs | Labor Costs (2017 $)
Gas Storage | 30 | 249.392 | 268.8929
| 40 | 269.5906 | 290.6709
| 65 | 320.0872 | 345.1159
Tankless Gas | NA | 294.7162 | 387.4669

## Elec_Chillers_TRM_IMC
Mid-A TRM Incremental Cost values
Air-Cooled Chiller Incremental Costs ($/Ton) for Washington, D.C. and Delaware
Capacity (Tons) | Baseline EER | Efficient EER
|  | 9.9 | 10.2 | 10.52 | 10.7
50 | 9.562 | 258 | 486 | 730 | 867
100 | 9.562 | 128 | 243 | 364 | 433
150 | 9.562 | 86 | 162 | 244 | 289
200 | 9.562 | 53 | 99 | 149 | 177
400 | 9.562 | 26 | 50 | 74 | 88
Air-Cooled Chiller Incremental Costs ($/Ton) for Maryland
Capacity (Tons) | Baseline EER | Efficient EER
|  | 9.9 | 10.2 | 10.52 | 10.7
50 | 10.1 | N/A | 76 | 320 | 457
100 | 10.1 | N/A | 38 | 159 | 228
150 | 10.1 | N/A | 25 | 107 | 152
200 | 10.1 | N/A | 15 | 65 | 93
400 | 10.1 | N/A | 8 | 32 | 46
Water-Cooled Scroll/Screw Chiller Incremental Costs ($/Ton) for Washington, D.C. and Delaware
Capacity (Tons) | Baseline kW/ton | Efficient kW/ton
|  | 0.72 | 0.68 | 0.64 | 0.6
50 | 0.78 | 114 | 164 | N/A | N/A
100 | 0.775 | 52 | 77 | N/A | N/A
150 | 0.68 | N/A | N/A | N/A | N/A
200 | 0.68 | N/A | N/A | 61 | 122
400 | 0.62 | N/A | N/A | N/A | 16
Water-Cooled Scroll/Screw Chiller Incremental Costs ($/Ton) for Maryland
Capacity (Tons) | Baseline kW/ton | Efficient kW/ton
|  | 0.72 | 0.68 | 0.64 | 0.6
50 | 0.75 | 57 | 107 | N/A | N/A
100 | 0.72 | 0 | 25 | N/A | N/A
150 | 0.66 | N/A | N/A | N/A | N/A
200 | 0.66 | N/A | N/A | 31 | 92
400 | 0.61 | N/A | N/A | N/A | 8
Water-Cooled Centrifugal Chiller Incremental Costs ($/Ton) for Washington, D.C. and Delaware
Capacity (Tons) | Baseline kW/ton | Efficient kW/ton
|  | 0.6 | 0.58 | 0.54
100 | 0.634 | 62 | 99 | 172
150 | 0.634 | 42 | 66 | 115
200 | 0.634 | 31 | 49 | 86
300 | 0.576 | N/A | N/A | 55
600 | 0.57 | N/A | N/A | 22
Water-Cooled Centrifugal Chiller Incremental Costs ($/Ton) for Maryland
Capacity (Tons) | Baseline kW/ton | Efficient kW/ton
|  | 0.6 | 0.58 | 0.54
100 | 0.61 | 18 | 55 | 128
150 | 0.61 | 12 | 36 | 85
200 | 0.61 | 9 | 27 | 64
300 | 0.56 | N/A | N/A | 31
600 | 0.56 | N/A | N/A | 15
Return To Master Summary

## Elct_Chillers_Water_Cooled_TOS
Recommended Incremental Costs
| Screw-Scroll | [11 empty] | Centrifugal
| Water-Cooled Scroll/Screw Chiller Incremental Costs ($/Ton) for Washington, D.C. and Delaware | [5 empty] | Water-Cooled Scroll/Screw Chiller Incremental Costs ($/Ton) for Maryland | [5 empty] | Water-Cooled Centrifugal Chiller Incremental Costs ($/Ton) for Washington, D.C. and Delaware | [5 empty] | Water-Cooled Centrifugal Chiller Incremental Costs ($/Ton) for Maryland
| Capacity (Tons) | Baseline kW/ton | Efficient kW/ton |  |  |  | Capacity (Tons) | Baseline kW/ton | Efficient kW/ton |  |  |  | Capacity (Tons) | Baseline kW/ton | Efficient kW/ton |  |  |  | Capacity (Tons) | Baseline kW/ton | Efficient kW/ton
|  |  | 0.72 | 0.68 | 0.64 | 0.6 |  |  | 0.72 | 0.68 | 0.64 | 0.6 |  |  | 0.72 | 0.68 | 0.64 | 0.6 |  |  | 0.72 | 0.68 | 0.64 | 0.6
| 50 | 0.78 | 311.032 | 518.3867 | N/A | N/A | 50 | 0.75 | 155.516 | 362.8707 | N/A | N/A | 50 | 0.78 | N/A | 88.1257 | 139.9644 | 243.6418 | 50 | 0.75 | N/A | 25.9193 | 77.758 | 181.4353
| 100 | 0.775 | 142.5563 | 246.2337 | N/A | N/A | 100 | 0.72 | 0 | 103.6773 | N/A | N/A | 100 | 0.775 | N/A | 58.7505 | 93.3096 | 162.4278 | 100 | 0.72 | N/A | 17.2796 | 51.8387 | 120.9569
| 150 | 0.68 | N/A | N/A | N/A | N/A | 150 | 0.66 | N/A | N/A | N/A | N/A | 150 | 0.68 | N/A | 44.0629 | 69.9822 | 121.8209 | 150 | 0.66 | N/A | 12.9597 | 38.879 | 90.7177
| 200 | 0.68 | N/A | N/A | 51.8387 | 103.6773 | 200 | 0.66 | N/A | N/A | 25.9193 | 77.758 | 200 | 0.68 | N/A | N/A | N/A | 31.1032 | 200 | 0.66 | N/A | N/A | N/A | 17.2796
| 400 | 0.62 | N/A | N/A | N/A | 12.9597 | 400 | 0.61 | N/A | N/A | N/A | 6.4798 | 400 | 0.62 | N/A | N/A | N/A | 12.9597 | 400 | 0.61 | N/A | N/A | N/A | 8.6398
Water-Cooled Screw Costs ($) for Washington, D.C. and Delaware | [23 empty] | Labor Costs for Chillers |  |  |  |  | Labor Costs Not included in calculation, but are provided as a reference
Water Cooled Screw Chiller | Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  |  | Capacity (Tons) | Calculated Incremental Cost/Ton |  |  |  | Calculated Incremental Cost/Ton -$2017 |  |  |  |  | Cooling Type | Mount | Size | Labor Cost | Labor Cost (2017$)
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton |  |  |  |  | Water Cooled | ground | 100 | 252.9614 | 272.7413
[5 empty] | 0.72 | 0.68 | 0.64 | 0.6 | 0.72 | 0.68 | 0.64 | 0.6 |  |  | 0.72 | 0.68 | 0.64 | 0.6 | 0.72 | 0.68 | 0.64 | 0.6 |  |  |  | 200 | 209.132 | 225.4848
| 50 | 0.78 | 24228.0959 | 26122.5772 | 38651.8524 | 48267.69 | N/A | N/A | 41674.1786 | 52041.9129 | N/A | N/A |  | 50 | 288.4751 | 480.7919 | N/A | N/A | 311.032 | 518.3867 | N/A | N/A |  |  |  | 300 | 175.5114 | 189.2352
| 100 | 0.775 | 40507.6256 | 43675.0614 | 53729.4024 | 63345.24 | N/A | N/A | 57930.696 | 68298.4303 | N/A | N/A |  | 100 | 132.2178 | 228.3761 | N/A | N/A | 142.5563 | 246.2337 | N/A | N/A |  |  | basement | 100 | 291.1966 | 313.9663
| 150 | 0.68 | 78422.79 | 84554.9477 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  |  | 200 | 231.1353 | 249.2086
| 200 | 0.68 | 93500.34 | 100811.4651 | N/A | N/A | 103116.1777 | 112732.0153 | N/A | N/A | 111179.1993 | 121546.9336 |  | 200 | N/A | N/A | 48.0792 | 96.1584 | N/A | N/A | 51.8387 | 103.6773 |  |  |  | 300 | 187.6847 | 202.3604
| 400 | 0.62 | 168234.2965 | 181389.1361 | N/A | N/A | N/A | 173042.2153 | N/A | N/A | N/A | 186573.0032 |  | 400 | N/A | N/A | N/A | 12.0198 | N/A | N/A | N/A | 12.9597 |  |  | roof | 100 | 274.295 | 295.7431
| Water-Cooled Screw Chiller Costs ($) for Maryland | [24 empty] | 200 | 216.1251 | 233.0247
| Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  |  | Capacity (Tons) | Calculated Incremental Cost/Ton |  |  |  | Calculated Incremental Cost/Ton -$2017
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton
[5 empty] | 0.72 | 0.68 | 0.64 | 0.6 | 0.72 | 0.68 | 0.64 | 0.6 |  |  | 0.72 | 0.68 | 0.64 | 0.6 | 0.72 | 0.68 | 0.64 | 0.6
| 50 | 0.75 | 31439.9742 | 33898.3779 | 38651.8524 | 48267.69 | N/A | N/A | 41674.1786 | 52041.9129 | N/A | N/A |  | 50 | 144.2376 | 336.5543 | N/A | N/A | 155.516 | 362.8707 | N/A | N/A
| 100 | 0.72 | 53729.4024 | 57930.696 | 53729.4024 | 63345.24 | N/A | N/A | 57930.696 | 68298.4303 | N/A | N/A |  | 100 | 0 | 96.1584 | N/A | N/A | 0 | 103.6773 | N/A | N/A
| 150 | 0.66 | 83230.7088 | 89738.8148 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| 200 | 0.66 | 98308.2588 | 105995.3322 | N/A | N/A | 103116.1777 | 112732.0153 | N/A | N/A | 111179.1993 | 121546.9336 |  | 200 | N/A | N/A | 24.0396 | 72.1188 | N/A | N/A | 25.9193 | 77.758
| 400 | 0.61 | 170638.2559 | 183981.0697 | N/A | N/A | N/A | 173042.2153 | N/A | N/A | N/A | 186573.0032 |  | 400 | N/A | N/A | N/A | 6.0099 | N/A | N/A | N/A | 6.4798
Water-Cooled Scroll Costs ($) for Washington, D.C. and Delaware
Water Cooled Scroll Chiller | Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  |  | Capacity (Tons) | Calculated Incremental Cost/Ton |  |  |  | Calculated Incremental Cost/Ton -$2017
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton
[5 empty] | 0.72 | 0.68 | 0.64 | 0.6 | 0.72 | 0.68 | 0.64 | 0.6 |  |  | 0.72 | 0.68 | 0.64 | 0.6 | 0.72 | 0.68 | 0.64 | 0.6
| 50 | 0.78 | 19049.2603 | 20538.7899 | 33473.0167 | 43088.8543 | N/A | N/A | 36090.3913 | 46458.1255 | N/A | N/A |  | 50 | 14423.7565 | 24039.5941 | N/A | N/A | 15551.6014 | 25919.3357 | N/A | N/A
| 100 | 0.775 | 35328.79 | 38091.2741 | 48550.5667 | 58166.4043 | N/A | N/A | 52346.9087 | 62714.6429 | N/A | N/A |  | 100 | 13221.7767 | 22837.6144 | N/A | N/A | 14255.6346 | 24623.3689 | N/A | N/A
| 150 | 0.68 | 73243.9543 | 78971.1604 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| 200 | 0.68 | 88321.5043 | 95227.6778 | N/A | N/A | 97937.342 | 107553.1796 | N/A | N/A | 105595.412 | 115963.1463 |  | 200 | N/A | N/A | 9615.8376 | 19231.6753 | N/A | N/A | 10367.7343 | 20735.4685
| 400 | 0.62 | 163055.4608 | 175805.3488 | N/A | N/A | N/A | 167863.3796 | N/A | N/A | N/A | 180989.2159 |  | 400 | N/A | N/A | N/A | 4807.9188 | N/A | N/A | N/A | 5183.8671
Water-Cooled Scroll Costs ($) for Maryland
| Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  |  | Capacity (Tons) | Calculated Incremental Cost/Ton |  |  |  | Calculated Incremental Cost/Ton -$2017
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton
[5 empty] | 0.72 | 0.68 | 0.64 | 0.6 | 0.72 | 0.68 | 0.64 | 0.6 |  |  | 0.72 | 0.68 | 0.64 | 0.6 | 0.72 | 0.68 | 0.64 | 0.6
| 50 | 0.75 | 26261.1385 | 28314.5906 | 33473.0167 | 43088.8543 | N/A | N/A | 36090.3913 | 46458.1255 | N/A | N/A |  | 50 | 7211.8782 | 16827.7159 | N/A | N/A | 7775.8007 | 18143.535 | N/A | N/A
| 100 | 0.72 | 48550.5667 | 52346.9087 | 48550.5667 | 58166.4043 | N/A | N/A | 52346.9087 | 62714.6429 | N/A | N/A |  | 100 | 0 | 9615.8376 | N/A | N/A | 0 | 10367.7343 | N/A | N/A
| 150 | 0.66 | 78051.8732 | 84155.0275 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 150 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| 200 | 0.66 | 93129.4232 | 100411.5449 | N/A | N/A | 97937.342 | 107553.1796 | N/A | N/A | 105595.412 | 115963.1463 |  | 200 | N/A | N/A | 4807.9188 | 14423.7565 | N/A | N/A | 5183.8671 | 15551.6014
| 400 | 0.61 | 165459.4202 | 178397.2824 | N/A | N/A | N/A | 167863.3796 | N/A | N/A | N/A | 180989.2159 |  | 400 | N/A | N/A | N/A | 2403.9594 | N/A | N/A | N/A | 2591.9336
Water-Cooled Centrifugal Chiller Costs ($) for Washington, D.C. and Delaware
Water Cooled Centrifugal Chiller* Assuming no centrifugal VSD | Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  |  | Capacity (Tons) | Calculated Incremental Cost/Ton |  |  |  | Calculated Incremental Cost/Ton -$2017
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton
[5 empty] | NA | 0.6 | 0.58 | 0.54 | NA | 0.6 | 0.58 | 0.54 |  |  | NA | 0.6 | 0.58 | 0.54 | NA | 0.6 | 0.58 | 0.54
| 100 | 0.634 | 52207.8892 | 56290.2103 | N/A | 60381.3512 | 65189.27 | 74805.1077 | N/A | 65102.7844 | 70286.6515 | 80654.3858 |  | 100 | N/A | 81.7346 | 129.8138 | 225.9722 | N/A | 88.1257 | 139.9644 | 243.6418
| 150 | 0.634 | 67285.4392 | 72546.7277 | N/A | 75458.9012 | 80266.82 | 89882.6577 | N/A | 81359.3018 | 86543.1689 | 96910.9032 |  | 150 | N/A | 54.4897 | 86.5425 | 150.6481 | N/A | 58.7505 | 93.3096 | 162.4278
| 200 | 0.634 | 82362.9892 | 88803.2451 | N/A | 90536.4512 | 95344.37 | 104960.2077 | N/A | 97615.8192 | 102799.6864 | 113167.4206 |  | 200 | N/A | 40.8673 | 64.9069 | 112.9861 | N/A | 44.0629 | 69.9822 | 121.8209
| 300 | 0.576 | 126461.0538 | 136349.4946 | N/A | N/A | N/A | 135115.3077 | N/A | N/A | N/A | 145680.4554 |  | 300 | N/A | N/A | N/A | 28.8475 | N/A | N/A | N/A | 31.1032
| 600 | 0.57 | 218368.7294 | 235443.7592 | N/A | N/A | N/A | 225580.6077 | N/A | N/A | N/A | 243219.5599 |  | 600 | N/A | N/A | N/A | 12.0198 | N/A | N/A | N/A | 12.9597
Water-Cooled Centrifugal Chiller Costs ($) for Maryland
| Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  |  | Capacity (Tons) | Calculated Incremental Cost/Ton |  |  |  | Calculated Incremental Cost/Ton -$2017
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton
[5 empty] | NA | 0.6 | 0.58 | 0.54 | NA | 0.6 | 0.58 | 0.54 |  |  | NA | 0.6 | 0.58 | 0.54 | NA | 0.6 | 0.58 | 0.54
| 100 | 0.61 | 57977.3918 | 62510.8508 | N/A | 60381.3512 | 65189.27 | 74805.1077 | N/A | 65102.7844 | 70286.6515 | 80654.3858 |  | 100 | N/A | 24.0396 | 72.1188 | 168.2772 | N/A | 25.9193 | 77.758 | 181.4353
| 150 | 0.61 | 73054.9418 | 78767.3682 | N/A | 75458.9012 | 80266.82 | 89882.6577 | N/A | 81359.3018 | 86543.1689 | 96910.9032 |  | 150 | N/A | 16.0264 | 48.0792 | 112.1848 | N/A | 17.2796 | 51.8387 | 120.9569
| 200 | 0.61 | 88132.4918 | 95023.8857 | N/A | 90536.4512 | 95344.37 | 104960.2077 | N/A | 97615.8192 | 102799.6864 | 113167.4206 |  | 200 | N/A | 12.0198 | 36.0594 | 84.1386 | N/A | 12.9597 | 38.879 | 90.7177
| 300 | 0.56 | 130307.3888 | 140496.5883 | N/A | N/A | N/A | 135115.3077 | N/A | N/A | N/A | 145680.4554 |  | 300 | N/A | N/A | N/A | 16.0264 | N/A | N/A | N/A | 17.2796
| 600 | 0.56 | 220772.6888 | 238035.6927 | N/A | N/A | N/A | 225580.6077 | N/A | N/A | N/A | 243219.5599 |  | 600 | N/A | N/A | N/A | 8.0132 | N/A | N/A | N/A | 8.6398
Return To Master Summary

## Elct_Chillers_Water_Cooled_ER
| Calculated Costs (Labor Not Included) | [11 empty] | ER IMC Cost Calculator | [11 empty] | Labor Costs for Chillers
Water-Cooled Screw Costs ($) for Washington, D.C. and Delaware | [24 empty] | Cooling Type | Mount | Size | Labor Cost | Labor Cost (2017$)
Water Cooled Screw Chiller | Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  | Labor (assumed roof mount) based on closest capacity available | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost (2017$) |  |  |  | Water Cooled | ground | 100 | 252.9614 | 272.7413
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [11 empty] | Efficiency kW/ton | [5 empty] | 200 | 209.132 | 225.4848
[5 empty] | 0.72 | 0.68 | 0.64 | 0.6 | 0.72 | 0.68 | 0.64 | 0.6 | [8 empty] | 0.72 | 0.68 | 0.64 | 0.6 |  |  | 300 | 175.5114 | 189.2352
| 50 | 0.78 | 24481.0573 | 26395.3185 | 38651.8524 | 48267.69 | N/A | N/A | 41674.1786 | 52041.9129 | N/A | N/A | 295.7431 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 12350.1434 | 54320.0651 | 64687.7994 | N/A | N/A |  | basement | 100 | 291.1966 | 313.9663
| 100 | 0.775 | 40507.6256 | 43675.0614 | 53729.4024 | 63345.24 | N/A | N/A | 57930.696 | 68298.4303 | N/A | N/A | 295.7431 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 20345.603 | 78572.0421 | 88939.7763 | N/A | N/A |  |  | 200 | 231.1353 | 249.2086
| 150 | 0.68 | 78422.79 | 84554.9477 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 233.0247 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 39231.9959 | N/A | N/A | N/A | N/A |  |  | 300 | 187.6847 | 202.3604
| 200 | 0.68 | 93500.34 | 100811.4651 | N/A | N/A | 103116.1777 | 112732.0153 | N/A | N/A | 111179.1993 | 121546.9336 | 233.0247 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 46754.0018 | N/A | N/A | 158166.2258 | 168533.96 |  | roof | 100 | 274.295 | 295.7431
| 400 | 0.62 | 168234.2965 | 181389.1361 | N/A | N/A | N/A | 173042.2153 | N/A | N/A | N/A | 186573.0032 | 196.2135 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 84020.8286 | N/A | N/A | N/A | 270790.0453 |  |  | 200 | 216.1251 | 233.0247
| Water-Cooled Screw Chiller Costs ($) for Maryland | [25 empty] | 300 | 181.9835 | 196.2135
| Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  | Labor (assumed roof mount) based on closest capacity available | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost |  |  |  | water cooled with Centrifugal VSD | gound | 300 | 175.4065 | 189.1222
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [11 empty] | Efficiency kW/ton |  |  |  |  | basement | 300 | 187.5565 | 202.2222
[5 empty] | 0.72 | 0.68 | 0.64 | 0.6 | 0.72 | 0.68 | 0.64 | 0.6 | [8 empty] | 0.72 | 0.68 | 0.64 | 0.6 |  | roof | 300 | 181.8669 | 196.0877
| 50 | 0.75 | 31439.9742 | 33898.3779 | 38651.8524 | 48267.69 | N/A | N/A | 41674.1786 | 52041.9129 | N/A | N/A | 295.7431 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 15821.8622 | 57791.7839 | 68159.5182 | N/A | N/A
| 100 | 0.72 | 53729.4024 | 57930.696 | 53729.4024 | 63345.24 | N/A | N/A | 57930.696 | 68298.4303 | N/A | N/A | 295.7431 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 26941.7862 | 85168.2253 | 95535.9595 | N/A | N/A
| 150 | 0.66 | 83230.7088 | 89738.8148 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 233.0247 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 41630.608 | N/A | N/A | N/A | N/A
| 200 | 0.66 | 98308.2588 | 105995.3322 | N/A | N/A | 103116.1777 | 112732.0153 | N/A | N/A | 111179.1993 | 121546.9336 | 233.0247 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 49152.6138 | N/A | N/A | 160564.8378 | 170932.5721
| 400 | 0.61 | 170638.2559 | 183981.0697 | N/A | N/A | N/A | 173042.2153 | N/A | N/A | N/A | 186573.0032 | 196.2135 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 85220.1347 | N/A | N/A | N/A | 271989.3514
Water-Cooled Scroll Costs ($) for Washington, D.C. and Delaware
Water Cooled Scroll Chiller | Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  | Labor (assumed roof mount) based on closest capacity available | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost (2017$)
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [11 empty] | Efficiency kW/ton
[5 empty] | 0.72 | 0.68 | 0.64 | 0.6 | 0.72 | 0.68 | 0.64 | 0.6 | [8 empty] | 0.72 | 0.68 | 0.64 | 0.6
| 50 | 0.78 | 19049.2603 | 20538.7899 | 33473.0167 | 43088.8543 | N/A | N/A | 36090.3913 | 46458.1255 | N/A | N/A | 295.7431 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 9640.2861 | 25191.8875 | 35559.6218 | N/A | N/A
| 100 | 0.775 | 35328.79 | 38091.2741 | 48550.5667 | 58166.4043 | N/A | N/A | 52346.9087 | 62714.6429 | N/A | N/A | 295.7431 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 17761.945 | 32017.5796 | 42385.3139 | N/A | N/A
| 150 | 0.68 | 73243.9543 | 78971.1604 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 233.0247 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 36648.3379 | N/A | N/A | N/A | N/A
| 200 | 0.68 | 88321.5043 | 95227.6778 | N/A | N/A | 97937.342 | 107553.1796 | N/A | N/A | 105595.412 | 115963.1463 | 233.0247 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 44170.3438 | N/A | N/A | 54538.0781 | 64905.8123
| 400 | 0.62 | 163055.4608 | 175805.3488 | N/A | N/A | N/A | 167863.3796 | N/A | N/A | N/A | 180989.2159 | 196.2135 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 81437.1707 | N/A | N/A | N/A | 86621.0378
Water-Cooled Scroll Costs ($) for Maryland
| Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  | Labor (assumed roof mount) based on closest capacity available | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost (2017$)
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [11 empty] | Efficiency kW/ton
[5 empty] | 0.72 | 0.68 | 0.64 | 0.6 | 0.72 | 0.68 | 0.64 | 0.6 | [8 empty] | 0.72 | 0.68 | 0.64 | 0.6
| 50 | 0.75 | 26261.1385 | 28314.5906 | 33473.0167 | 43088.8543 | N/A | N/A | 36090.3913 | 46458.1255 | N/A | N/A | 295.7431 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 13238.2042 | 21014.0049 | 31381.7392 | N/A | N/A
| 100 | 0.72 | 48550.5667 | 52346.9087 | 48550.5667 | 58166.4043 | N/A | N/A | 52346.9087 | 62714.6429 | N/A | N/A | 295.7431 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 24358.1282 | 24358.1282 | 34725.8625 | N/A | N/A
| 150 | 0.66 | 78051.8732 | 84155.0275 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 233.0247 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 39046.95 | N/A | N/A | N/A | N/A
| 200 | 0.66 | 93129.4232 | 100411.5449 | N/A | N/A | 97937.342 | 107553.1796 | N/A | N/A | 105595.412 | 115963.1463 | 233.0247 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 46568.9559 | N/A | N/A | 51752.823 | 62120.5573
| 400 | 0.61 | 165459.4202 | 178397.2824 | N/A | N/A | N/A | 167863.3796 | N/A | N/A | N/A | 180989.2159 | 196.2135 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 82636.4767 | N/A | N/A | N/A | 85228.4103
Water-Cooled Centrifugal Chiller Costs ($) for Washington, D.C. and Delaware
Water Cooled Centrifugal Chiller* Assuming no centrifugal VSD | Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  | Labor (assumed roof mount) based on closest capacity available | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost (2017$)
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [11 empty] | Efficiency kW/ton
[5 empty] | NA | 0.6 | 0.58 | 0.54 | NA | 0.6 | 0.58 | 0.54 | [8 empty] | NA | 0.6 | 0.58 | 0.54
| 100 | 0.634 | 52207.8892 | 56290.2103 | N/A | 60381.3512 | 65189.27 | 74805.1077 | N/A | 65102.7844 | 70286.6515 | 80654.3858 | 295.7431 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 26182.7218 | N/A | 34995.2959 | N/A | N/A
| 150 | 0.634 | 67285.4392 | 72546.7277 | N/A | 56227.2259 | 65843.0636 | 75458.9012 | N/A | 60623.8333 | 70991.5675 | 81359.3018 | 295.7431 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 33704.7277 | N/A | 21781.8333 | N/A | N/A
| 200 | 0.634 | 82362.9892 | 88803.2451 | N/A | 71304.7759 | 80920.6136 | 90536.4512 | N/A | 76880.3507 | 87248.0849 | 97615.8192 | 233.0247 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 41197.7132 | N/A | 29274.8188 | 39642.5531 | 50010.2874
| 300 | 0.576 | 126461.0538 | 136349.4946 | N/A | N/A | N/A | 120691.5512 | N/A | N/A | N/A | 130128.854 | 196.2135 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 63180.6672 | N/A | N/A | N/A | 56960.0266
| 600 | 0.57 | 218368.7294 | 235443.7592 | N/A | N/A | N/A | 211156.8512 | N/A | N/A | N/A | 227667.9585 | 196.2135 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 108941.4966 | N/A | N/A | N/A | 101165.6959
Water-Cooled Centrifugal Chiller Costs ($) for Maryland
| Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  | Labor (assumed roof mount) based on closest capacity available | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost (2017$)
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [11 empty] | Efficiency kW/ton
[5 empty] | NA | 0.6 | 0.58 | 0.54 | NA | 0.6 | 0.58 | 0.54 | [8 empty] | NA | 0.6 | 0.58 | 0.54
| 100 | 0.61 | 57977.3918 | 62510.8508 | N/A | 60381.3512 | 65189.27 | 74805.1077 | N/A | 65102.7844 | 70286.6515 | 80654.3858 | 295.7431 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 28924.2139 | N/A | 31516.1474 | N/A | N/A
| 150 | 0.61 | 90071.6702 | 97114.6953 | N/A | 56227.2259 | 65843.0636 | 75458.9012 | N/A | 60623.8333 | 70991.5675 | 81359.3018 | 295.7431 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 44935.658 | N/A | 8444.796 | N/A | N/A
| 200 | 0.61 | 105149.2202 | 113371.2127 | N/A | 71304.7759 | 80920.6136 | 90536.4512 | N/A | 76880.3507 | 87248.0849 | 97615.8192 | 233.0247 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 52457.6639 | N/A | 15966.8018 | 26334.5361 | 36702.2704
| 300 | 0.56 | 147324.1172 | 158843.9154 | N/A | N/A | N/A | 120691.5512 | N/A | N/A | N/A | 130128.854 | 196.2135 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 73498.2058 | N/A | N/A | N/A | 44783.1444
| 600 | 0.56 | 237789.4172 | 256383.0198 | N/A | N/A | N/A | 211156.8512 | N/A | N/A | N/A | 227667.9585 | 196.2135 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 118630.2409 | N/A | N/A | N/A | 89915.1796
Return To Master Summary

## Elct_Chillers_Air_Cooled_TOS
Recommended Incremental Costs
| Air-Cooled Chiller Incremental Costs ($/Ton) for Washington, D.C. and Delaware | [5 empty] | Air-Cooled Chiller Incremental Costs ($/Ton) for Maryland
| Capacity (Tons) | Baseline EER | Efficient EER |  |  |  | Capacity (Tons) | Baseline EER | Efficient EER
|  |  | 9.9 | 10.2 | 10.52 | 10.7 |  |  | 9.9 | 10.2 | 10.52 | 10.7
| 50 | 9.562 | 137.0677 | 258.9934 | 350.4378 | 411.4006 | 50 | 10.1 | N/A | 54.8666 | 146.3109 | 207.2738
| 100 | 9.562 | 68.5338 | 129.4967 | 175.2189 | 205.7003 | 100 | 10.1 | N/A | 27.4333 | 73.1555 | 103.6369
| 150 | 9.562 | 45.6892 | 86.3311 | 116.8126 | 137.1335 | 150 | 10.1 | N/A | 18.2889 | 48.7703 | 69.0913
| 200 | 9.562 | 34.2669 | 64.7484 | 87.6094 | 102.8502 | 200 | 10.1 | N/A | 13.7166 | 36.5777 | 51.8185
| 400 | 9.562 | 17.1335 | 32.3742 | 43.8047 | 51.4251 | 400 | 10.1 | N/A | 6.8583 | 18.2889 | 25.9092
| Air-Cooled Chiller for Washington, D.C. and Delaware | [19 empty] | Labor Costs for Chillers - Region Adjusted
Air Cooled Screw Chiller | Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  | Calculated Incremental Cost/ton - Time of Sale/New Construction | [7 empty] | Cooling Type | Mount | Size | Labor Cost | Labor Cost (2017$)
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton |  |  |  | Efficiency kW/ton |  |  |  | Efficiency kW/ton |  |  |  | Air Cooled | ground | 100 | 211.2269 | 227.7435
[5 empty] | 1.21 | 1.17 | 1.14 | 1.12 | 1.21 | 1.17 | 1.14 | 1.12 | 1.21 | 1.17 | 1.14 | 1.12 | 1.21 | 1.17 | 1.14 | 1.12 |  |  | 200 | 149.3979 | 161.0799
| 50 | 1.255 | 19328.4061 | 20839.7631 | 25684.7633 | 31338.932 | 35579.5586 | 38406.6429 | 27693.1465 | 33789.4349 | 38361.6511 | 41409.7953 | 127.1271 | 240.2105 | 325.023 | 381.5647 | 137.0677 | 258.9934 | 350.4378 | 411.4006 |  |  | 300 | 142.5143 | 153.658
| 100 | 1.255 | 50883.9436 | 54862.7407 | 57240.3008 | 62894.4695 | 67135.0961 | 69962.1804 | 61716.124 | 67812.4124 | 72384.6286 | 75432.7728 | 63.5636 | 120.1053 | 162.5115 | 190.7824 | 68.5338 | 129.4967 | 175.2189 | 205.7003 |  | roof | 100 | 213.2253 | 229.8982
| 150 | 1.255 | 82439.4811 | 88885.7182 | 88795.8383 | 94450.007 | 98690.6336 | 101517.7179 | 95739.1015 | 101835.3899 | 106407.6062 | 109455.7503 | 42.3757 | 80.0702 | 108.341 | 127.1882 | 45.6892 | 86.3311 | 116.8126 | 137.1335 |  |  | 200 | 154.9505 | 167.0666
| 200 | 1.255 | 113995.0186 | 122908.6957 | 120351.3758 | 126005.5445 | 130246.1711 | 133073.2554 | 129762.079 | 135858.3674 | 140430.5837 | 143478.7278 | 31.7818 | 60.0526 | 81.2558 | 95.3912 | 34.2669 | 64.7484 | 87.6094 | 102.8502 |  |  | 300 | 147.1989 | 158.7089
| 400 | 1.255 | 240217.1686 | 259000.6057 | 246573.5258 | 252227.6945 | 256468.3211 | 259295.4054 | 265853.9891 | 271950.2775 | 276522.4937 | 279570.6379 | 15.8909 | 30.0263 | 40.6279 | 47.6956 | 17.1335 | 32.3742 | 43.8047 | 51.4251
Air-Cooled Chiller for Maryland
| Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  | Calculated Incremental Cost/ton - Time of Sale/New Construction
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton |  |  |  | Efficiency kW/ton |  |  |  | Efficiency kW/ton
[5 empty] | 1.21 | 1.17 | 1.14 | 1.12 | 1.21 | 1.17 | 1.14 | 1.12 | 1.21 | 1.17 | 1.14 | 1.12 | 1.21 | 1.17 | 1.14 | 1.12
| 50 | 1.188 | 28794.5561 | 31046.1051 | N/A | 31338.932 | 35579.5586 | 38406.6429 | N/A | 33789.4349 | 38361.6511 | 41409.7953 | N/A | 50.8875 | 135.7 | 192.2417 | N/A | 54.8666 | 146.3109 | 207.2738
| 100 | 1.188 | 60350.0936 | 65069.0826 | N/A | 62894.4695 | 67135.0961 | 69962.1804 | N/A | 67812.4124 | 72384.6286 | 75432.7728 | N/A | 25.4438 | 67.85 | 96.1209 | N/A | 27.4333 | 73.1555 | 103.6369
| 150 | 1.188 | 91905.6311 | 99092.0601 | N/A | 94450.007 | 98690.6336 | 101517.7179 | N/A | 101835.3899 | 106407.6062 | 109455.7503 | N/A | 16.9625 | 45.2333 | 64.0806 | N/A | 18.2889 | 48.7703 | 69.0913
| 200 | 1.188 | 123461.1686 | 133115.0376 | N/A | 126005.5445 | 130246.1711 | 133073.2554 | N/A | 135858.3674 | 140430.5837 | 143478.7278 | N/A | 12.7219 | 33.925 | 48.0604 | N/A | 13.7166 | 36.5777 | 51.8185
| 400 | 1.188 | 249683.3186 | 269206.9477 | N/A | 252227.6945 | 256468.3211 | 259295.4054 | N/A | 271950.2775 | 276522.4937 | 279570.6379 | N/A | 6.3609 | 16.9625 | 24.0302 | N/A | 6.8583 | 18.2889 | 25.9092
Air-Cooled Chiller for Washington, D.C. and Delaware
Air Cooled Scroll Chiller | Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  | Calculated Incremental Cost/ton - Time of Sale/New Construction
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton |  |  |  | Efficiency kW/ton |  |  |  | Efficiency kW/ton
[5 empty] | 1.21 | 1.17 | 1.14 | 1.12 | 1.21 | 1.17 | 1.14 | 1.12 | 0.72 | 0.68 | 0.64 | 0.6 | 0.72 | 0.68 | 0.64 | 0.6
| 50 | 1.255 | 21975.906 | 23694.2805 | N/A | 33986.4319 | 38227.0584 | 41054.1428 | N/A | 36643.9522 | 41216.1685 | 44264.3126 | N/A | 240.2105 | 325.023 | 381.5647 | N/A | 258.9934 | 350.4378 | 411.4006
| 100 | 1.255 | 53531.4435 | 57717.258 | N/A | 65541.9694 | 69782.5959 | 72609.6803 | N/A | 70666.9297 | 75239.146 | 78287.2902 | N/A | 120.1053 | 162.5115 | 190.7824 | N/A | 129.4967 | 175.2189 | 205.7003
| 150 | 1.255 | 85086.981 | 91740.2355 | N/A | 97097.5069 | 101338.1334 | 104165.2178 | N/A | 104689.9072 | 109262.1235 | 112310.2677 | N/A | 80.0702 | 108.341 | 127.1882 | N/A | 86.3311 | 116.8126 | 137.1335
| 200 | 1.255 | 116642.5185 | 125763.213 | N/A | 128653.0444 | 132893.6709 | 135720.7553 | N/A | 138712.8847 | 143285.101 | 146333.2452 | N/A | 60.0526 | 81.2558 | 95.3912 | N/A | 64.7484 | 87.6094 | 102.8502
| 400 | 1.255 | 242864.6685 | 261855.1231 | N/A | 254875.1944 | 259115.8209 | 261942.9053 | N/A | 274804.7948 | 279377.0111 | 282425.1552 | N/A | 30.0263 | 40.6279 | 47.6956 | N/A | 32.3742 | 43.8047 | 51.4251
Air-Cooled Chiller for Maryland
| Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  | Calculated Incremental Cost/ton - Time of Sale/New Construction
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton |  |  |  | Efficiency kW/ton |  |  |  | Efficiency kW/ton
[5 empty] | 1.21 | 1.17 | 1.14 | 1.12 | 1.21 | 1.17 | 1.14 | 1.12 | 0.72 | 0.68 | 0.64 | 0.6 | 0.72 | 0.68 | 0.64 | 0.6
| 50 | 1.188 | 31442.0559 | 33900.6224 | N/A | 33986.4319 | 38227.0584 | 41054.1428 | N/A | 36643.9522 | 41216.1685 | 44264.3126 | N/A | 50.8875 | 135.7 | 192.2417 | N/A | 54.8666 | 146.3109 | 207.2738
| 100 | 1.188 | 62997.5934 | 67923.5999 | N/A | 65541.9694 | 69782.5959 | 72609.6803 | N/A | 70666.9297 | 75239.146 | 78287.2902 | N/A | 25.4438 | 67.85 | 96.1209 | N/A | 27.4333 | 73.1555 | 103.6369
| 150 | 1.188 | 94553.1309 | 101946.5775 | N/A | 97097.5069 | 101338.1334 | 104165.2178 | N/A | 104689.9072 | 109262.1235 | 112310.2677 | N/A | 16.9625 | 45.2333 | 64.0806 | N/A | 18.2889 | 48.7703 | 69.0913
| 200 | 1.188 | 126108.6684 | 135969.555 | N/A | 128653.0444 | 132893.6709 | 135720.7553 | N/A | 138712.8847 | 143285.101 | 146333.2452 | N/A | 12.7219 | 33.925 | 48.0604 | N/A | 13.7166 | 36.5777 | 51.8185
| 400 | 1.188 | 252330.8184 | 272061.465 | N/A | 254875.1944 | 259115.8209 | 261942.9053 | N/A | 274804.7948 | 279377.0111 | 282425.1552 | N/A | 6.3609 | 16.9625 | 24.0302 | N/A | 6.8583 | 18.2889 | 25.9092
Return To Master Summary
Note on O15: Barquest, Ethan: Kw/ton used for Hedonic Modeling, but will be rported as the equivilent EER in the TRM

## Elct_Chillers_Air_Cooled_ER
Labor Costs for Chillers - Region Adjusted
Air-Cooled Chiller for Washington, D.C. and Delaware | [24 empty] | Cooling Type | Mount | Size | Labor Cost | Labor Cost (2017$)
Air Cooled Screw Chiller | Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  | Labor (assumed roof mount) based on closest capacity available | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost/Ton (2017$) |  |  |  | Air Cooled | ground | 100 | 211.2269 | 227.7435
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [11 empty] | Efficiency kW/ton | [5 empty] | 200 | 149.3979 | 161.0799
[5 empty] | 1.21 | 1.17 | 1.14 | 1.12 | 1.21 | 1.17 | 1.14 | 1.12 | [8 empty] | 1.21 | 1.17 | 1.14 | 1.12 |  |  | 300 | 142.5143 | 153.658
| 100 | 1.255 | 50883.9436 | 54862.7407 | 57240.3008 | 62894.4695 | 67135.0961 | 69962.1804 | 61716.124 | 67812.4124 | 72384.6286 | 75432.7728 | 229.8982 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 25491.7546 | 323.4514 | 384.4143 | 430.1364 | 460.6179 |  | roof | 100 | 213.2253 | 229.8982
| 150 | 1.255 | 82439.4811 | 88885.7182 | 88795.8383 | 94450.007 | 98690.6336 | 101517.7179 | 95739.1015 | 101835.3899 | 106407.6062 | 109455.7503 | 167.0666 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 41205.3549 | 320.3916 | 361.0335 | 391.515 | 411.8359 |  |  | 200 | 154.9505 | 167.0666
| 200 | 1.255 | 113995.0186 | 122908.6957 | 120351.3758 | 126005.5445 | 130246.1711 | 133073.2554 | 129762.079 | 135858.3674 | 140430.5837 | 143478.7278 | 167.0666 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 56948.0278 | 319.0071 | 349.4885 | 372.3496 | 387.5903 |  |  | 300 | 147.1989 | 158.7089
| 300 | 1.255 | 177106.0936 | 190954.6507 | 183462.4508 | 189116.6195 | 193357.2461 | 196184.3304 | 197808.0341 | 203904.3224 | 208476.5387 | 211524.6829 | 158.7089 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 88429.5064 | 317.6096 | 337.9306 | 353.1713 | 363.3318
| 400 | 1.255 | 240217.1686 | 259000.6057 | 246573.5258 | 252227.6945 | 256468.3211 | 259295.4054 | 265853.9891 | 271950.2775 | 276522.4937 | 279570.6379 | 158.7089 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 119914.8522 | 316.9206 | 332.1613 | 343.5919 | 351.2122
Air-Cooled Chiller for Maryland
| Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  | Labor (assumed roof mount) based on closest capacity available | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost/Ton (2017$)
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [11 empty] | Efficiency kW/ton
[5 empty] | 1.21 | 1.17 | 1.14 | 1.12 | 1.21 | 1.17 | 1.14 | 1.12 | [8 empty] | 1.21 | 1.17 | 1.14 | 1.12
| 100 | 1.188 | 60350.0936 | 65069.0826 | N/A | 62894.4695 | 67135.0961 | 69962.1804 | N/A | 67812.4124 | 72384.6286 | 75432.7728 | 229.8982 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 30214.3014 | NA | 329.5763 | 375.2985 | 405.7799
| 150 | 1.188 | 91905.6311 | 99092.0601 | N/A | 94450.007 | 98690.6336 | 101517.7179 | N/A | 101835.3899 | 106407.6062 | 109455.7503 | 167.0666 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 45927.9016 | NA | 324.4749 | 354.9563 | 375.2773
| 200 | 1.188 | 123461.1686 | 133115.0376 | N/A | 126005.5445 | 130246.1711 | 133073.2554 | N/A | 135858.3674 | 140430.5837 | 143478.7278 | 167.0666 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 61670.5745 | NA | 322.0695 | 344.9306 | 360.1713
| 300 | 1.188 | 186572.2436 | 201160.9927 | N/A | 189116.6195 | 193357.2461 | 196184.3304 | N/A | 203904.3224 | 208476.5387 | 211524.6829 | 158.7089 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 93152.0532 | NA | 319.6513 | 334.892 | 345.0525
| 400 | 1.188 | 249683.3186 | 269206.9477 | N/A | 252227.6945 | 256468.3211 | 259295.4054 | N/A | 271950.2775 | 276522.4937 | 279570.6379 | 158.7089 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 124637.399 | NA | 318.4518 | 329.8824 | 337.5027
Air-Cooled Chiller for Washington, D.C. and Delaware
Air Cooled Scroll Chiller | Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  | Labor (assumed roof mount) based on closest capacity available | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost/Ton (2017$)
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [11 empty] | Efficiency kW/ton
[5 empty] | 1.21 | 1.17 | 1.14 | 1.12 | 1.21 | 1.17 | 1.14 | 1.12 | [8 empty] | 1.21 | 1.17 | 1.14 | 1.12
| 100 | 1.255 | 53531.4435 | 57717.258 | 59887.8006 | 65541.9694 | 69782.5959 | 72609.6803 | 64570.6413 | 70666.9297 | 75239.146 | 78287.2902 | 229.8982 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 26812.56 | 336.6594 | 397.6223 | 443.3445 | 473.8259
| 150 | 1.255 | 85086.981 | 91740.2355 | 91443.3381 | 97097.5069 | 101338.1334 | 104165.2178 | 98593.6189 | 104689.9072 | 109262.1235 | 112310.2677 | 167.0666 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 42526.1603 | 329.197 | 369.8389 | 400.3203 | 420.6413
| 200 | 1.255 | 116642.5185 | 125763.213 | 122998.8756 | 128653.0444 | 132893.6709 | 135720.7553 | 132616.5964 | 138712.8847 | 143285.101 | 146333.2452 | 167.0666 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 58268.8332 | 325.6111 | 356.0925 | 378.9536 | 394.1943
| 300 | 1.255 | 179753.5935 | 193809.168 | 186109.9506 | 191764.1194 | 196004.7459 | 198831.8303 | 200662.5514 | 206758.8398 | 211331.056 | 214379.2002 | 158.7089 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 89750.3118 | 322.0123 | 342.3333 | 357.574 | 367.7345
| 400 | 1.255 | 242864.6685 | 261855.1231 | 249221.0256 | 254875.1944 | 259115.8209 | 261942.9053 | 268708.5064 | 274804.7948 | 279377.0111 | 282425.1552 | 158.7089 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 121235.6576 | 320.2226 | 335.4633 | 346.8939 | 354.5142
Air-Cooled Chiller for Maryland
| Capacity (Tons) | Baseline kW/ton | Calculated Baseline Cost | Calculated Baseline Cost (2017 $) | Calculated Cost (Labor Not Included) |  |  |  | Calculated Cost (2017 $) (Labor Not Included) |  |  |  | Labor (assumed roof mount) based on closest capacity available | Real Discount Rate | EUL | RUL | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment | Lifecycle Retrofit/Early Replacement Incremental Cost/Ton (2017$)
[5 empty] | Efficiency kW/ton |  |  |  | Efficiency kW/ton | [11 empty] | Efficiency kW/ton
[5 empty] | 1.21 | 1.17 | 1.14 | 1.12 | 1.21 | 1.17 | 1.14 | 1.12 | [8 empty] | 1.21 | 1.17 | 1.14 | 1.12
| 100 | 1.188 | 60350.0936 | 65069.0826 | N/A | 65541.9694 | 69782.5959 | 72609.6803 | N/A | 70666.9297 | 75239.146 | 78287.2902 | 229.8982 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 30214.3014 | NA | 358.1215 | 403.8436 | 434.3251
| 150 | 1.188 | 91905.6311 | 99092.0601 | N/A | 97097.5069 | 101338.1334 | 104165.2178 | N/A | 104689.9072 | 109262.1235 | 112310.2677 | 167.0666 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 45927.9016 | NA | 343.505 | 373.9864 | 394.3074
| 200 | 1.188 | 123461.1686 | 133115.0376 | N/A | 128653.0444 | 132893.6709 | 135720.7553 | N/A | 138712.8847 | 143285.101 | 146333.2452 | 167.0666 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 61670.5745 | NA | 336.3421 | 359.2032 | 374.4439
| 300 | 1.188 | 186572.2436 | 201160.9927 | N/A | 191764.1194 | 196004.7459 | 198831.8303 | N/A | 206758.8398 | 211331.056 | 214379.2002 | 158.7089 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 93152.0532 | NA | 329.1663 | 344.4071 | 354.5675
| 400 | 1.188 | 249683.3186 | 269206.9477 | N/A | 254875.1944 | 259115.8209 | 261942.9053 | N/A | 274804.7948 | 279377.0111 | 282425.1552 | 158.7089 | 5% | 23 | 7.6667 | 6.2413 | 13.4886 | 0.46271 | 124637.399 | NA | 325.5881 | 337.0187 | 344.639
Return To Master Summary

## Occupancy_Sensor
Recommended Incremental Costs
Occupancy Sensor (w/o Ultrasonic) | 130.0098
Occupancy Sensor (with Ultrasonic) | 180.4248
Occupancy Sensor (w/o Ultrasonic) | [5 empty] | Average IMC with Labor (2017$)
Coverage (ft2) | Volts | Measure Cost (No Labor) | Measure Cost (No Labor) ( 2017$) | Average IMC (No Labor) | Average IMC (No Labor) (2017$) | Mount type | ultrasonic | Average IMC (with Labor)
500 | 24 | 109.7097 | 116.0827 | 122.8722 | 130.0098 | Wall | no | 200.2042
1000 | 24 | 113.4597 | 120.0505 |  |  | Ceiling | no | 224.9834
1500 | 24 | 117.2097 | 124.0184 |  |  | Wall | yes | 250.6192
500 | 120 | 128.5347 | 136.0012 |  |  | Ceiling | yes | 275.3984
1000 | 120 | 132.2847 | 139.9691
1500 | 120 | 136.0347 | 143.9369
Occupancy Sensor (with Ultrasonic) | [5 empty] | Labor Costs
Coverage (ft2) | Volts | Measure Cost (No Labor) | Measure Cost (No Labor) ( 2017$) | Average IMC (No Labor) | Average IMC (No Labor) (2017$) | Mount | Labor Costs | Labor Costs (2017 $)
500 | 24 | 156.3378 | 165.4195 | 170.5194 | 180.4248 | Wall Mounted | 66.3406 | 70.1944
1000 | 24 | 147.2366 | 155.7895 |  |  | Ceiling Mounted | 89.7594 | 94.9735
1500 | 24 | 163.8378 | 173.3551 |  |  | Fixture Integrated | 65.3827 | 69.1807
500 | 120 | 181.4847 | 192.0271
1000 | 120 | 185.2347 | 195.9949
1500 | 120 | 188.9847 | 199.9628
Return To Master Summary

## Room_AC_Calculations
Recommended Incremental Costs
Product Type and Class (Btu/hour) |  | Lifecycle Retrofit/Early Replacement Incremental Cost - Energy Star with Louvered Sides | Lifecycle Retrofit/Early Replacement Incremental Cost - Energy Star without Louvered Sides
Without Reverse Cycle | < 8,000 | 244.0598 | 205.304
| 8,000 to 10,999 | 360.7267 | 311.1705
| 11,000 to 13,999 | 450.9271 | 397.7707
| 14,000 to 19,999 | 579.0273 | 523.1169
| 20,000 to 24,999 | 692.0844 | 692.0844
| 25,000 to 27,999 | 808.9668 | 812.3515
| >=28,000 | 896.1178 | 910.5185
With Reverse Cycle | <14,000 | NA | 312.6494
| >= 14,000 | NA | 591.7162
| <20,000 | 333.4042 | NA
| >=20,000 | 763.6512 | NA
Calculated Component Costs | [6 empty] | IMC Calculations | [12 empty] | From Mid Atlantic TRM |  | Baseline Efficiency Used Specified in TRM |  | Efficient Conditions (TRM)
Product Type and Class (Btu/hour) Specified by Mid A TRM |  |  | Itron Baseline Cost* Midpoint of Btuh used |  | Itron Efficient Measure Cost * Midpoint of Btuh used |  | Incremental Cost - Time of Sale |  | Lifecycle Retrofit/Early Replacement Incremental Cost Calculator | [10 empty] | Product Type and Class (Btu/hour) |  | Federal Standard with louvered sides | Federal Standard without louvered sides | ENERGY STAR with louvered sides (CEER) | ENERGY STAR without louvered sides (CEER)
|  | Capacity used For calculation | Federal Standard with louvered sides | Federal Standard without louvered sides | ENERGY STAR with louvered sides | ENERGY STAR without louvered sides | With Louvered sides | without louvered sides | Labor | Real Discount Rate | EUL From TRM V6 | RUL - From TRM V6 | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment -with Louvered Sides | Incremental cost of early replace w/ standard equipment - Without Louvered Sides | Lifecycle Retrofit/Early Replacement Incremental Cost - Energy Star with Louvered Sides | Lifecycle Retrofit/Early Replacement Incremental Cost - Energy Star without Louvered Sides |  |  | (CEER) | (CEER)
Without Reverse Cycle | < 8,000 | 5500 | 171.3639 | 143.8239 | 191.4079 | 161.1139 | 20.044 | 17.29 | No Labor Value provided by Itron MCS. Therefore, No labor costs are included in Room AC numbers. | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 52.6518 | 44.1901 | 244.0598 | 205.304 | Without Reverse Cycle | < 8,000 | 11 | 10 | 12.1 | 11
| 8,000 to 10,999 | 9500 | 260.6099 | 224.8079 | 280.6539 | 242.0979 | 20.044 | 17.29 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 80.0728 | 69.0726 | 360.7267 | 311.1705 |  | 8,000 to 10,999 | 10.9 | 9.6 | 12 | 10.6
| 11,000 to 13,999 | 12500 | 329.6099 | 291.0539 | 349.6539 | 308.3439 | 20.044 | 17.29 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 101.2732 | 89.4268 | 450.9271 | 397.7707 |  | 11,000 to 13,999 | 10.9 | 9.5 | 12 | 10.5
| 14,000 to 19,999 | 17000 | 427.6019 | 389.0459 | 447.6459 | 403.5819 | 20.044 | 14.536 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 131.3814 | 119.535 | 579.0273 | 523.1169 |  | 14,000 to 19,999 | 10.7 | 9.3 | 11.8 | 10.2
| 20,000 to 24,999 | 22500 | 518.2999 | 518.2999 | 532.8359 | 532.8359 | 14.536 | 14.536 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 159.2485 | 159.2485 | 692.0844 | 692.0844 |  | 20,000 to 24,999 | 9.4 | 9.4 | 10.3 | 10.3
| 25,000 to 27,999 | 26500 | 599.2839 | 610.2999 | 624.8359 | 624.8359 | 25.552 | 14.536 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 184.1309 | 187.5156 | 808.9668 | 812.3515 |  | 25,000 to 27,999 | 9 | 9.4 | 10.3 | 10.3
| >=28,000 | 29000 | 656.7839 | 667.7999 | 694.3199 | 705.3359 | 37.536 | 37.536 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 201.7979 | 205.1826 | 896.1178 | 910.5185 |  | >=28,000 | 9 | 9.4 | 9.9 | 10.3
With Reverse Cycle | <14,000 | 10000 | NA | 228.0459 | NA | 242.5819 | NA | 14.536 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | NA | 70.0675 | NA | 312.6494 | With Reverse Cycle | <14,000 | NA | 9.3 | NA | 10.2
| >= 14,000 | 20000 | NA | 441.5219 | NA | 456.0579 | NA | 14.536 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | NA | 135.6583 | NA | 591.7162 |  | >= 14,000 | NA | 8.7 | NA | 9.6
| <20,000 | 10000 | 241.8159 | NA | 259.1059 | NA | 17.29 | NA |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 74.2983 | NA | 333.4042 | NA |  | <20,000 | 9.8 | NA | 10.8 | NA
| >=20,000 | 25000 | 573.0459 | NA | 587.5819 | NA | 14.536 | NA |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 176.0693 | NA | 763.6512 | NA |  | >=20,000 | 9.3 | NA | 10.2 | NA
Calculated Costs (2017 $) | [19 empty] | Return To Master Summary
Product Type and Class (Btu/hour) |  |  | Itron Baseline Cost* Midpoint of Btuh used |  | Itron Efficient Measure Cost * Midpoint of Btuh used |  | Incremental Cost - Time of Sale |  | Lifecycle Retrofit/Early Replacement Incremental Cost Calculator (2017$)
|  |  | Federal Standard with louvered sides | Federal Standard without louvered sides | ENERGY STAR with louvered sides | ENERGY STAR without louvered sides | With Louvered sides | without louvered sides | Labor | Real Discount Rate | EUL From TRM V6 | RUL - From TRM V6 | PV Real Levelized Carrying Charge for Existing Furnace | PV Real Levelized Carrying Charge for New Furnace | ER Cost factor (E/H) | Incremental cost of early replace w/ standard equipment -with Louvered Sides | Incremental cost of early replace w/ standard equipment - Without Louvered Sides | Lifecycle Retrofit/Early Replacement Incremental Cost - Energy Star with Louvered Sides | Lifecycle Retrofit/Early Replacement Incremental Cost - Energy Star without Louvered Sides
Without Reverse Cycle | < 8,000 |  | 184.7635 | 155.07 | 206.3748 | 173.712 | 21.6113 | 18.642 | No Labor Value provided by Itron MCS. Therefore, No labor costs are included in Room AC numbers. | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 56.7689 | 47.6455 | 263.1437 | 221.3575
| 8,000 to 10,999 |  | 280.9879 | 242.3865 | 302.5993 | 261.0284 | 21.6113 | 18.642 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 86.334 | 74.4736 | 388.9332 | 335.502
| 11,000 to 13,999 |  | 355.3833 | 313.8125 | 376.9946 | 332.4544 | 21.6113 | 18.642 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 109.1921 | 96.4194 | 486.1867 | 428.8738
| 14,000 to 19,999 |  | 461.0376 | 419.4668 | 482.649 | 435.1394 | 21.6113 | 15.6726 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 141.6545 | 128.8818 | 624.3035 | 564.0213
| 20,000 to 24,999 |  | 558.8276 | 558.8276 | 574.5003 | 574.5003 | 15.6726 | 15.6726 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 171.7007 | 171.7007 | 746.2009 | 746.2009
| 25,000 to 27,999 |  | 646.1441 | 658.0214 | 673.6941 | 673.6941 | 27.55 | 15.6726 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 198.5288 | 202.1781 | 872.2229 | 875.8722
| >=28,000 |  | 708.1402 | 720.0176 | 748.6113 | 760.4887 | 40.4711 | 40.4711 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 217.5772 | 221.2265 | 966.1885 | 981.7152
With Reverse Cycle | <14,000 |  | NA | 245.8776 | NA | 261.5503 | NA | 15.6726 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | NA | 75.5463 | NA | 337.0966
| >= 14,000 |  | NA | 476.0461 | NA | 491.7187 | NA | 15.6726 |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | NA | 146.2659 | NA | 637.9846
| <20,000 |  | 260.7244 | NA | 279.3663 | NA | 18.642 | NA |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 80.108 | NA | 359.4743 | NA
| >=20,000 |  | 617.8544 | NA | 633.527 | NA | 15.6726 | NA |  | 5% | 12 | 3 | 2.7232 | 8.8633 | 0.30725 | 189.8367 | NA | 823.3638 | NA

## Inflation
Inflation
Time Period | Average Inflation | Time (Years) | 2017 Adjustment factor
2013-2017 | 0.019 | 4 | 1.0782 | <- Used for Itron MCS Inflation Adjustment
2016-2017 | 0.019 | 1 | 1.019
2015-2017 | 0.019 | 2 | 1.0384
2014-2017 | 0.019 | 3 | 1.0581
Return To Master Summary

## Labor Adjustment
Table G-1: Statewide RSMeans Cost Indices Weighted by 2010-2012 HVAC Measure Claims
HVAC Labor Adjustment Factors |  | When used in doccument | Climate Zone | Reference City | Material1 | Installation1 | Weights2 | Weighted Material | Weighted Installation | RSMeans City Cost Indices for Maryland |  | Population
National to MD wieghted Avg | 0.8201 | When average RS means has been applied and results represent the national average | 1 | Eureka | 0.94 | 1.017 | 0.0032678 | 0.0030717 | 0.0033234 | ANNAPOLIS | 0.823 | ANNAPOLIS | 38394
CA to MD | 0.70818 | When labor represents the California average | 2 | Santa Rosa | 0.94 | 1.653 | 0.0096952 | 0.0091135 | 0.016026 | BALTIMORE | 0.824 | BALTIMORE | 620961
|  |  | 3 | San Francisco | 1.001 | 1.673 | 0.030274 | 0.030304 | 0.050648 | COLLEGE PARK | 0.87 | COLLEGE PARK | 30413
|  |  | 4 | San Jose | 1 | 1.448 | 0.015286 | 0.015286 | 0.022134 | CUMBERLAND | 0.728 | CUMBERLAND | 20859
Lighting Labor Adjustment Factors |  | When used in doccument | 5 | San Luis Obispo | 0.94 | 1.055 | 0.00043296 | 0.00040698 | 0.00045677 | EASTON | 0.693 | EASTON | 15945
National to MD wieghted Avg | 0.8201 | When average RS means has been applied and results represent the national average | 6 | Santa Barbara | 1 | 1.167 | 0.1391 | 0.1391 | 0.16233 | ELKTON | 0.819 | ELKTON | 15443
CA to MD | 0.73743 | When labor represents the california average | 7 | San Diego | 1 | 1.152 | 0.046714 | 0.046714 | 0.053815 | HAGERSTOWN | 0.834 | HAGERSTOWN | 39662
|  |  | 8 | Santa Ana | 0.94 | 1.055 | 0.16224 | 0.15251 | 0.17117 | SALISBURY | 0.632 | SALISBURY | 30343
Return To Master Summary | 42.4228 |  | 9 | Los Angeles | 1.001 | 1.167 | 0.2181 | 0.21832 | 0.25453 | SILVER SPRING | 0.857 | SILVER SPRING | 71452
|  |  | 10 | Riverside | 1 | 1.166 | 0.21278 | 0.21278 | 0.2481 | WALDORF | 0.856 | WALDORF | 67752
|  |  | 11 | Redding | 1 | 1.07 | 0.010239 | 0.010239 | 0.010956 | Unweighted average | 0.7936
|  |  | 12 | Sacramento | 1 | 1.198 | 0.036051 | 0.036051 | 0.04319 | Population wieghted average | 0.8201
|  |  | 13 | Fresno | 1.001 | 1.113 | 0.021693 | 0.021715 | 0.024144
|  |  | 14 | Mojave | 0.94 | 0.992 | 0.034946 | 0.032849 | 0.034666
|  |  | 15 | Palm Springs | 0.94 | 1.054 | 0.047199 | 0.044367 | 0.049748
|  |  | 16 | Susanville | 0.94 | 1.07 | 0.011973 | 0.011255 | 0.012811
|  |  |  | Average | 0.97394 | 1.1906 | 1 | 0.98408 | 1.158
1 - Table 21, 22, 23 (Fire Suppression, Plumbing, & HVAC) RSMeans MasterFormat City Cost Indexes, Year 2013 National Average Base
2 - 2010-2012 Standard Program Tracking Data (all in-scope deemed HVAC claims)
Table G-2: Statewide RSMeans Cost Indices Weighted by 2010-2012 Lighting Measure Claims
|  |  | Climate Zone | Reference City | Material1 | Installation1 | Weights2 | Weighted Material | Weighted Installation
|  |  | 1 | Eureka | 1.002 | 1.146 | 0.0054359 | 0.0054468 | 0.0062295
|  |  | 2 | Santa Rosa | 0.965 | 1.187 | 0.013086 | 0.012628 | 0.015533
|  |  | 3 | San Francisco | 1.061 | 1.571 | 0.04861 | 0.051575 | 0.076367
|  |  | 4 | San Jose | 1.025 | 1.532 | 0.019217 | 0.019697 | 0.02944
|  |  | 5 | San Luis Obispo | 0.904 | 0.962 | 0.0051419 | 0.0046483 | 0.0049465
|  |  | 6 | Santa Barbara | 0.894 | 1.097 | 0.13381 | 0.11963 | 0.14679
|  |  | 7 | San Diego | 0.992 | 0.991 | 0.033253 | 0.032987 | 0.032954
|  |  | 8 | Santa Ana | 0.962 | 1.03 | 0.19239 | 0.18508 | 0.19816
|  |  | 9 | Los Angeles | 0.998 | 1.208 | 0.16605 | 0.16572 | 0.20059
|  |  | 10 | Riverside | 0.925 | 1.065 | 0.19969 | 0.18471 | 0.21267
|  |  | 11 | Redding | 0.997 | 1.018 | 0.01062 | 0.010589 | 0.010812
|  |  | 12 | Sacramento | 1.012 | 1.133 | 0.038485 | 0.038947 | 0.043604
|  |  | 13 | Fresno | 0.918 | 1.015 | 0.05595 | 0.051362 | 0.056789
|  |  | 14 | Mojave | 0.904 | 0.964 | 0.048091 | 0.043474 | 0.04636
|  |  | 15 | Palm Springs | 0.962 | 1.024 | 0.025533 | 0.024563 | 0.026146
|  |  | 16 | Susanville | 1.001 | 1.018 | 0.0046397 | 0.0046444 | 0.0047232
|  |  |  | Average | 0.97012 | 1.1226 | 1 | 0.9557 | 1.1121
1 - Table 26, 27, 3370 (Electrical, Communications, & Utilities) RSMeans MasterFormat City Cost Indexes, Year 2013 National Average Base
2 - 2010-2012 Standard Program Tracking Data (all in-scope deemed nonresidential lighting claims)

## Equipment Results Matrix
| Itron MCS | [7 empty] | DEER |  | Workpapers |  | Model Results | [6 empty] | Incremental Costs | [5 empty] | Model Validation
Technology | Variable | Type | Values | Count | Mean | Std Dev | Mean Price | Std Dev Price | Type | Values | Type | Values | Model Coefficients | t-stat | s.e. | Weights for Roll-up to DEER/WP | DEER/WP-equivalent Coefficients | Data and Model Info |  | Measure Source | Match Pair | Description | Modeled price | Incremental Cost | Standard Error or MAE/mean | Large-Sample Validation Summary/Additional Documentation Narratives |  |  | Small-Sample Validation / Benchmarking Summary
[29 empty] | Matched Pair | Description | Modeled price | Actual price 1 | Actual price 2 | Actual price 3 | Actual price 4 | Actual price 5 | Actual price 6 | Actual price 7 | Actual price 8 | Actual price 9 | Actual price 10 | Actual price 11 | Actual price 12 | Actual price 13 | Actual price 14 | Actual price 15 | Actual price 16 | Actual price 17 | Actual price 18 | Actual price 19 | Actual price 20 | Actual price 21 | Actual price 22 | Actual price 23 | Actual price 24 | Actual price 25
Appliances and Electronics
Refrigerators (full size residential) | ENERGY STAR | Binary | Yes | 6014 | N/A | N/A | 1176.86 | 4373.61 | Binary | Yes | Binary | Yes | -11.64 | -1.03 | 11.34 | N/A | -11.64 | Data Source | Data Type | DEER Measures | Baseline | Bottom Mount Freezer, Large, 573 rated kWh/yr | 993.5042 | 28.866 | 7.74 | * Plot is of the actual purchase price of 56,608 full-size refrigerators bought through | Model Validation Summary Stats
|  |  | No | 1358 | N/A | N/A | 536.18 | 2939.16 |  | No |  | No | 0 | -- | -- | N/A | 0 | NPD | Point of sales |  | Measure | Energy Star Bottom Mount Freezer without through-the-door ice - large (16.5-25 ft3 TV) - 487 kWh/yr | 1022.3702 |  |  | the CA C4A program vs. Modeled price. Dotted line represents a perfect model fit (slope = 1). | Mean | 0.17497
| Capacity (Total volume ft3) | Continuous | 7.8 - 31 | 7372 | 22.9 | 3.55 | 1031.01 | 4669.44 | Discrete | 8 - 31 | Continuous | > 7.75 | 23.79 | 17.6 | 1.35 | N/A | 23.79 | Weighting | % CA market |  | Baseline | Refrigerator: Bottom Mount Freezer, Small; 518 rated kWh/yr | 817.1942 | 21.801 | 6.39 |  | Standard Error | 0.0049223
| Type | Categorical | Freezer on Bottom | 464 | N/A | N/A | 1019.69 | 1310.72 | Categorical | Freezer on Bottom | Categorical | Freezer on Bottom | 0 | -- | -- | N/A | 0 | CA unit sales | 79.2% |  | Measure | Energy Star(R) Refrigerator: Bottom Mount Freezer without through-the-door ice - small (8-16.5 ft3 TV) - 447 kWh/yr | 838.9952 |  |  |  | Median | 0.16584
|  |  | Freezer on Top | 1552 | N/A | N/A | 511.27 | 1282.78 |  | Freezer on Top |  | Freezer on Top | -391.091 | -24.9 | 15.74 | N/A | -391.091 | N observations | N unit sales |  | Baseline | Refrigerator: Side Mount Freezer, Large; 665 rated kWh/yr | 550.5697 | 35.46 | 9 |  | Mode | 0.28266
|  |  | French Doors | 3050 | N/A | N/A | 1779 | 2871.83 |  | N/A |  | French Doors | 308.33 | 18.4 | 16.78 | N/A | 308.33 | 7372 | 470718.8108 |  | Measure | Energy Star(R) Refrigerator: Side Mount Freezer without through-the-door ice - large (23-31ft3 TV) - 565 kWh/yr | 586.0297 |  |  |  | St. Dev. | 1.1711
|  |  | Side-by-Side | 2306 | N/A | N/A | 1042.9 | 2199.84 |  | Side-by-Side |  | Side-by-Side | -548.29 | -29.2 | 18.75 | N/A | -548.29 | R2 | Intercept |  | Baseline | Side Mount Freezer, Large, Ice Maker; 730 rated kWh/yr | 1041.4547 | 40.17 | 9.9 |  | Sample Variance | 1.3715
| Quarter | Categorical | 1 | 1672 | N/A | N/A | 1100.57 | 3575.98 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.12895 | -43.5779 | 0.86 | 726.7 |  | Measure | Energy Star Side Mount Freezer with through-the-door ice - large(23-31 ft3 TV) - 620 kWh/yr | 1081.6247 |  |  |  | Kurtosis | 10032.4584
|  |  | 2 | 1898 | N/A | N/A | 1041.52 | 4811.87 |  |  |  |  | -34.9 | -3.9 | 8.86 | 0.27071 |  | MAE | Contr. Markup |  | Baseline | Refrigerator: 620 rated kWh/yr | 381.4447 | 31.692 | 8.28 |  | Skewness | 95.486
|  |  | 3 | 1931 | N/A | N/A | 971.45 | 5386.66 |  |  |  |  | -42 | -4.9 | 8.53 | 0.36131 |  | 383.459 | N/A |  | Measure | Energy Star(R) Refrigerator: Side Mount Freezer without through-the-door ice - medium (15-23 ft3 TV) - 528 kWh/yr | 413.1367 |  |  |  | Range | 136.9224
|  |  | 4 | 1871 | N/A | N/A | 1071.6 | 4527.16 |  |  |  |  | -79.3 | -8.7 | 9.08 | 0.23903 |  |  |  |  | Baseline | Refrigerator: 639 rated kWh/yr | 893.9957 | 33.576 | 8.64 |  | Minimum | -0.87069
| Color | Categorical | White | 1980 | N/A | N/A | 676.08 | 3414.63 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.3953 | 86.6226 |  |  |  | Measure | Energy Star(R) Refrigerator: Side Mount Freezer with through-the-door ice - medium (15-23 ft3 TV) - 543 kWh/yr | 927.5717 |  |  |  | Maximum | 136.0517
|  |  | Bisque | 275 | N/A | N/A | 894.58 | 1292.82 |  |  |  |  | 71.514 | 2.51 | 28.51 | 0.0086532 |  |  |  |  | Baseline | Refrigerator: Top Mount Freezer, Large; 532 rated kWh/yr | 663.3567 | 26.04 | 7.2 |  | Sum | 9904.4391
|  |  | Black | 1648 | N/A | N/A | 921.55 | 3151.23 |  |  |  |  | 14.769 | 1.92 | 7.71 | 0.18481 |  |  |  |  | Measure | Energy Star(R) Refrigerator: Top Mount Freezer without through-the-door ice - large (20-25 ft3 TV) - 452 kWh/yr | 689.3967 |  |  |  | Count | 56608
|  |  | Other | 203 | N/A | N/A | 974.08 | 2102.31 |  |  |  |  | 169.169 | 6.17 | 27.42 | 0.0096071 |  |  |  |  | Baseline | Refrigerator: Top Mount Freezer, Medium; 469 rated kWh/yr | 574.0797 | 21.33 | 6.3
|  |  | Stainless | 2477 | N/A | N/A | 1557.92 | 4374.76 |  |  |  |  | 250.38 | 32.31 | 7.75 | 0.31174 |  |  |  |  | Measure | Energy Star(R) Refrigerator: Top Mount Freezer without through-the-door ice - medium (15-20 ft3 TV) - 399 kWh/yr | 595.4097
|  |  | Stainless Look | 789 | N/A | N/A | 1008.76 | 3025.57 |  |  |  |  | 40 | 3.96 | 10.1 | 0.089899 |  |  |  |  | Baseline | Top Mount Freezer, Small; 420 rated kWh/yr | 478.2087 | 18.033 | 5.67
| Dispenser | Binary | Yes | 4072 | N/A | N/A | 1392.81 | 4147.99 | Binary | Yes | Binary | Yes | 521.5 | 42.9 | 12.15 | N/A | 521.5 |  |  |  | Measure | Energy Star Top Mount Freezer without through-the-door ice - small (10-15 ft3 TV) - 357 kWh/yr | 496.2417
|  |  | No | 3300 | N/A | N/A | 698.46 | 3211.98 |  | No |  | No | 0 | -- | -- | N/A | 0
| kWh/yr | Continuous | 253 - 728 | 7372 | 511.8 | 77.4 | 1031.01 | 4669.44 | Discrete | 357 - 730 | N/A | N/A | -0.471 | -5.2 | 0.09 | N/A | -0.471
| CEE Tier 3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Binary | Yes | N/A | N/A |  | N/A | N/A
|  |  |  | N/A | N/A | N/A | N/A | N/A |  |  |  | No | N/A | N/A |  | N/A | N/A
Clothes Washers (side by side, top loading) | Modified Energy Factor | Continuous | 1.26-3.61 | 512 | 2.078 | 0.45387 | 563.1657 | 160.2986 | N/A | N/A | Continuous | >=1.26 | 38.9083 | 4.89 | 7.9595 | N/A | 38.9083 | Data Source | Data Type | Workpaper measures | Baseline | Top-loading, Title 20 code minimum, MEF=1.26, assumed 3.5 ft3 capacity | 466.3738 | - | - | * Plot is of the actual purchase price of 17,662 top-loading clothes washers bought through | Model Validation Summary Stats
| Compartment Capacity | Continuous | 2.5-4.7 | 512 | 3.8201 | 0.41341 | 563.1657 | 160.2986 | N/A | N/A | Continuous | 1.6-4.0 | 202.9314 | 14.74 | 13.7644 | N/A | 202.9314 | NPD | Point of sales |  | Measure | Top-loading, CEE Tier 1, MEF = 2.0, assumed 3.5 ft3 capacity | 495.166 | 28.7921 | 5.89 | the CA C4A program vs. Modeled price. Dotted line represents a perfect model fit (slope = 1). | Mean | 0.0059471
| Soil Sensor | Categorical | Yes | 154 | N/A | N/A | 688.5288 | 142.322 | N/A | N/A | N/A | N/A | 58.601 | 6.55 | 8.9475 | 0.13085 | 8.4809 | Weighting | % CA market |  | Measure | Top-loading, CEE Tier 2, MEF = 2.2, assumed 3.5 ft3 capacity | 502.9476 | 36.5738 | 7.4819 |  | Standard Error | 0.0016041
|  |  | No | 334 | N/A | N/A | 540.9404 | 150.5206 | N/A | N/A | N/A | N/A | 0 | . | . | 0.85982 |  | CA unit sales |  |  | Measure | Top-loading, CEE Tier 3, MEF = 2.4, assumed 3.5 ft3 capacity | 510.7293 | 44.3555 | 9.0738 |  | Median | -0.021305
|  |  | Not Specified | 24 | N/A | N/A | 853.2899 | 178.8368 | N/A | N/A | N/A | N/A | 87.1516 | 3.54 |  | 0.0093293 |  | N observations | N unit sales |  | Baseline | Top-loading, Title 20 code minimum, MEF=1.26, assumed 4.0 ft3 capacity | 567.8395 | - | - |  | Mode | -0.26769
| Quarter | Categorical | 1 | 137 | N/A | N/A | 533.9918 | 161.2261 | N/A | N/A | N/A | N/A | -17.0743 | -2.37 | 7.2064 | 0.18574 | 7.2902 | 512 | 112589 |  | Measure | Top-loading, CEE Tier 1, MEF = 2.0, assumed 4.0 ft3 capacity | 596.6317 | 28.7921 | 5.89 |  | Standard Deviation | 0.21318
|  |  | 2 | 134 | N/A | N/A | 563.7511 | 154.7554 | N/A | N/A | N/A | N/A | 10.5611 | 1.6 | 6.6019 | 0.2589 |  | R2 | Intercept |  | Measure | Top-loading, CEE Tier 2, MEF = 2.2, assumed 4.0 ft3 capacity | 604.4133 | 36.5738 | 7.4819 |  | Sample Variance | 0.045445
|  |  | 3 | 127 | N/A | N/A | 581.4066 | 164.5461 | N/A | N/A | N/A | N/A | 23.7111 | 3.83 | 6.183 | 0.32589 |  | 0.90349 | -400.4466 |  | Measure | Top-loading, CEE Tier 3, MEF = 2.4, assumed 4.0 ft3 capacity | 612.195 | 44.3555 | 9.0738 |  | Kurtosis | 7.4943
|  |  | 4 | 114 | N/A | N/A | 560.2129 | 155.8672 | N/A | N/A | N/A | N/A | 0 | . | . | 0.22947 |  | MAE | Contr. Markup | [7 empty] | Skewness | 1.5302
| Electronic Controls | Binary | Yes | 255 | N/A | N/A | 701.4457 | 148.3251 | N/A | N/A | N/A | N/A | 44.5263 | 6.2 | 7.1767 | 0.42103 | 18.7468 | 111.074 | N/A | [7 empty] | Range | 4.1013
|  |  | No | 257 | N/A | N/A | 462.6095 | 66.0787 | N/A | N/A | N/A | N/A | 0 | . | . | 0.57897 | [10 empty] | Minimum | -0.94781
| Brand | Categorical | Amana | 18 | N/A | N/A | 410.0197 | 21.6077 | N/A | N/A | N/A | N/A | -12.4412 | -0.31 | 40.2242 | 0.0035439 | -5.0419 | [9 empty] | Maximum | 3.1535
|  |  | Estate | 6 | N/A | N/A | 296.6754 | 33.8604 | N/A | N/A | N/A | N/A | -12.6048 | -0.01 | 1105.3718 | 0 | [10 empty] | Sum | 105.0378
|  |  | Fisher & Paykel | 32 | N/A | N/A | 535.443 | 84.398 | N/A | N/A | N/A | N/A | -125.2186 | -4.17 | 30.0339 | 0.0059686 | [10 empty] | Count | 17662
|  |  | GE | 179 | N/A | N/A | 469.3151 | 89.1097 | N/A | N/A | N/A | N/A | -55.4873 | -8.53 | 6.5079 | 0.21745 | [10 empty] | Confidence Level(95.0%) | 0.0031441
|  |  | Hotpoint | 8 | N/A | N/A | 349.9063 | 7.8538 | N/A | N/A | N/A | N/A | -52.843 | -3.39 | 15.5907 | 0.025686
|  |  | LG Electronics | 12 | N/A | N/A | 838.3334 | 79.3368 | N/A | N/A | N/A | N/A | 69.567 | 5.06 | 13.7523 | 0.085239
|  |  | Maytag | 93 | N/A | N/A | 557.1971 | 94.4384 | N/A | N/A | N/A | N/A | 9.1364 | 1.35 | 6.7472 | 0.19462
|  |  | Samsung | 10 | N/A | N/A | 836.3601 | 60.964 | N/A | N/A | N/A | N/A | 26.18 | 1.59 | 16.414 | 0.055938
|  |  | Whirlpool | 154 | N/A | N/A | 536.4817 | 133.5718 | N/A | N/A | N/A | N/A | 0 | . | . | 0.41157
| Color | Categorical | Bisque | 8 | N/A | N/A | 400.0833 | 17.5094 | N/A | N/A | N/A | N/A | 122.9339 | 0.36 | 342.5549 | 0.00080825 | 78.0601
|  |  | Black | 22 | N/A | N/A | 896.6081 | 120.6282 | N/A | N/A | N/A | N/A | 213.1542 | 0.59 | 363.8079 | 0.00023981
|  |  | Red | 12 | N/A | N/A | 863.9421 | 167.8457 | N/A | N/A | N/A | N/A | 223.1556 | 0.64 | 350.452 | 0.00043521
|  |  | Stainless | 4 | N/A | N/A | 483.0624 | 9.8932 | N/A | N/A | N/A | N/A | 146.6592 | 0.42 | 351.6748 | 0.00040857
|  |  | Stainless Look | 53 | N/A | N/A | 924.8587 | 98.5298 | N/A | N/A | N/A | N/A | 211.9382 | 0.64 | 333.5939 | 0.03606
|  |  | White | 409 | N/A | N/A | 549.5659 | 145.4192 | N/A | N/A | N/A | N/A | 72.8785 | 0.22 | 333.3549 | 0.96201
|  |  | Other | 4 | N/A | N/A | 445.2153 | 88.1713 | N/A | N/A | N/A | N/A | 0 | . | . | 4.4409e-05
Clothes Washers (stackable, front loading) | Modified Energy Factor | Continuous | 1.8-3.88 | 754 | 2.8224 | 0.37052 | 725.9896 | 191.3133 | N/A | N/A | Continuous | >=1.26 | 28.8988 | 2.24 | 12.8778 | N/A | 28.8988 | Data Source | Data Type | Workpaper measures | Baseline | Top-loading, Title 20 code minimum, MEF=1.26, assumed 3.5 ft3 capacity | 466.3738 | - | - | * Plot is of the actual purchase price of 18,688 front loading clothes washers bought through | Model Validation Summary Stats
| Compartment Capacity | Continuous | 2-4.4 | 754 | 3.7057 | 0.35331 | 725.9896 | 191.3133 | N/A | N/A | Continuous | 1.6-4.0 | 233.5492 | 14.97 | 15.601 | N/A | 233.5492 | NPD | Point of sales |  | Measure | Front-loading, CEE Tier 1, MEF = 2.0, assumed 3.5 ft3 capacity | 676.4954 | 210.1216 | 9.5296 | the CA C4A program vs. Modeled price. Dotted line represents a perfect model fit (slope = 1). | Mean | 0.0005086
| Steam Feature | Binary | Yes | 318 | N/A | N/A | 881.8909 | 170.5873 | N/A | N/A | N/A | N/A | 58.7582 | 4.3 | 13.6659 | 0.2916 | 17.1337 | Weighting | % CA market |  | Measure | Front-loading, CEE Tier 2, MEF = 2.2, assumed 3.5 ft3 capacity | 682.2752 | 215.9013 | 12.1051 |  | Standard Error | 0.00165
|  |  | No | 436 | N/A | N/A | 661.8139 | 159.8901 | N/A | N/A | N/A | N/A | 0 | . | . | 0.7084 |  | CA unit sales |  |  | Measure | Front-loading, CEE Tier 3, MEF = 2.4, assumed 3.5 ft3 capacity | 688.0549 | 221.6811 | 14.6807 |  | Median | -0.021984
| Sensor Type | Categorical | Both Load and Soil | 219 | N/A | N/A | 886.0311 | 241.1419 | N/A | N/A | N/A | N/A | 93.1278 | 4.45 | 20.9426 | 0.061282 | 10.6165 | N observations | N unit sales |  | Baseline | Top-loading, Title 20 code minimum, MEF=1.26, assumed 4.0 ft3 capacity | 567.8395 | - | - |  | Mode | 0.1972
|  |  | Soil Only | 150 | N/A | N/A | 787.4402 | 211.4986 | N/A | N/A | N/A | N/A | 80.8542 | 6.32 | 12.7919 | 0.22526 |  | 754 | 89778 |  | Measure | Front-loading, CEE Tier 1, MEF = 2.0, assumed 4.0 ft3 capacity | 676.4954 | 108.6559 | 9.5296 |  | Standard Deviation | 0.22557
|  |  | Load Only | 238 | N/A | N/A | 732.9806 | 173.8455 | N/A | N/A | N/A | N/A | -44.853 | -3.06 | 14.6537 | 0.31943 |  | R2 | Intercept |  | Measure | Front-loading, CEE Tier 2, MEF = 2.2, assumed 4.0 ft3 capacity | 682.2752 | 114.4356 | 12.1051 |  | Sample Variance | 0.05088
|  |  | Not Specified | 30 | N/A | N/A | 932.8451 | 253.1696 | N/A | N/A | N/A | N/A | 134.5629 | 2.83 | 47.5121 | 0.0076059 |  | 0.74016 | -342.0664 |  | Measure | Front-loading, CEE Tier 3, MEF = 2.4, assumed 4.0 ft3 capacity | 688.0549 | 120.2154 | 14.6807 |  | Kurtosis | 17.1041
|  |  | No Sensor | 117 | N/A | N/A | 654.9369 | 144.848 | N/A | N/A | N/A | N/A | 0 | . | . | 0.38642 |  | MAE | Contr. Markup | [7 empty] | Skewness | 1.3924
| Quarter | Categorical | 1 | 186 | N/A | N/A | 686.393 | 181.6703 | N/A | N/A | N/A | N/A | 1.2358 | 0.11 | 11.6822 | 0.2279 | 16.2231 | 142.312 | N/A | [7 empty] | Range | 5.2652
|  |  | 2 | 193 | N/A | N/A | 736.1254 | 195.7014 | N/A | N/A | N/A | N/A | 26.364 | 2.41 | 10.9318 | 0.28682 | [10 empty] | Minimum | -0.92901
|  |  | 3 | 194 | N/A | N/A | 739.3104 | 192.9578 | N/A | N/A | N/A | N/A | 28.4528 | 2.63 | 10.8217 | 0.29452 | [10 empty] | Maximum | 4.3361
|  |  | 4 | 181 | N/A | N/A | 737.4881 | 186.9083 | N/A | N/A | N/A | N/A | 0 | . | . | 0.19077 | [10 empty] | Sum | 9.5047
| Brand | Categorical | Amana | 4 | N/A | N/A | 424.082 | 20.1162 | N/A | N/A | N/A | N/A | -112.2256 | -0.39 | 287.0978 | 0.00016127 | 22.5961 | [9 empty] | Count | 18688
|  |  | Bosch | 20 | N/A | N/A | 704.0895 | 185.3423 | N/A | N/A | N/A | N/A | 185.6453 | 5.03 | 36.8895 | 0.01363 | [10 empty] | Confidence Level(95.0%) | 0.0032342
|  |  | Electro Brand | 2 | N/A | N/A | 1089.521 | 235.929 | N/A | N/A | N/A | N/A | 178.953 | 0.38 | 470.9248 | 5.9744e-05
|  |  | Electrolux | 51 | N/A | N/A | 911.5115 | 206.1602 | N/A | N/A | N/A | N/A | 29.0435 | 1 | 29.1612 | 0.025923
|  |  | Frigidaire | 71 | N/A | N/A | 517.7988 | 66.5272 | N/A | N/A | N/A | N/A | -122.1372 | -6.54 | 18.6779 | 0.073343
|  |  | GE | 79 | N/A | N/A | 738.4054 | 130.8527 | N/A | N/A | N/A | N/A | 58.4379 | 1.96 | 29.7961 | 0.021921
|  |  | LG Electronics | 146 | N/A | N/A | 758.6744 | 198.5775 | N/A | N/A | N/A | N/A | 88.5463 | 6.23 | 14.2086 | 0.20006
|  |  | Maytag | 100 | N/A | N/A | 786.7184 | 168.7491 | N/A | N/A | N/A | N/A | 44.5138 | 2.39 | 18.6473 | 0.067439
|  |  | Samsung | 122 | N/A | N/A | 713.3541 | 146.8121 | N/A | N/A | N/A | N/A | 17.7196 | 1.47 | 12.085 | 0.35446
|  |  | Whirlpool | 159 | N/A | N/A | 743.9223 | 223.8546 | N/A | N/A | N/A | N/A | 0 | . | . | 0.24301
| RPMs | Categorical | 720-1100 | 162 | N/A | N/A | 564.4132 | 70.1144 | N/A | N/A | N/A | N/A | -8.3065 | -0.15 | 54.8266 | 0.28651 | 28.9235
|  |  | >1100 | 573 | N/A | N/A | 791.2952 | 186.7894 | N/A | N/A | N/A | N/A | 44.2534 | 0.82 | 53.9431 | 0.70737
|  |  | Unspecified | 19 | N/A | N/A | 741.8033 | 47.6279 | N/A | N/A | N/A | N/A | 0 | . | . | 0.0061271
| Color | Categorical | Bisque | 3 | N/A | N/A | 594.5292 | 131.3164 | N/A | N/A | N/A | N/A | 2.6549 | 0 | 1274.6462 | 8.1663e-06 | 98.6
|  |  | Black | 28 | N/A | N/A | 774.646 | 39.4161 | N/A | N/A | N/A | N/A | 104.3302 | 1.25 | 83.7849 | 0.021697
|  |  | Blue | 53 | N/A | N/A | 827.1903 | 198.266 | N/A | N/A | N/A | N/A | 41.1242 | 0.46 | 89.2055 | 0.011853
|  |  | Green | 7 | N/A | N/A | 608.6697 | 105.0088 | N/A | N/A | N/A | N/A | -62.5017 | -0.19 | 330.6556 | 0.00013268
|  |  | Red | 138 | N/A | N/A | 815.2734 | 144.4103 | N/A | N/A | N/A | N/A | 93.2776 | 1.16 | 80.5547 | 0.046728
|  |  | Stainless | 4 | N/A | N/A | 582.3143 | 138.7422 | N/A | N/A | N/A | N/A | 63.6955 | 0.04 | 1513.555 | 5.782e-06
|  |  | Stainless Look | 105 | N/A | N/A | 1007.526 | 153.8306 | N/A | N/A | N/A | N/A | 223.3164 | 2.82 | 79.2504 | 0.097183
|  |  | White | 378 | N/A | N/A | 684.6501 | 167.8351 | N/A | N/A | N/A | N/A | 85.1488 | 1.08 | 78.7779 | 0.81969
|  |  | Other | 38 | N/A | N/A | 768.4798 | 171.7432 | N/A | N/A | N/A | N/A | 0 | . | . | 0.0027115
| Number of Wash Cycles | Categorical | 3 to 11 cycles | 383 | N/A | N/A | 678.2326 | 162.123 | N/A | N/A | N/A | N/A | -61.0911 | -1.56 | 39.1191 | 0.73736 | -50.7509
|  |  | 12 to 19 cycles | 283 | N/A | N/A | 852.3861 | 196.1165 | N/A | N/A | N/A | N/A | -27.0597 | -0.68 | 39.6098 | 0.23927
|  |  | 20 or more cycles | 60 | N/A | N/A | 872.8659 | 313.9839 | N/A | N/A | N/A | N/A | 59.0743 | 1.07 | 55.4557 | 0.013031
|  |  | Not Specified | 28 | N/A | N/A | 1021.462 | 65.39 | N/A | N/A | N/A | N/A | 0 | . | . | 0.010336
Residential HVAC
Room AC (cooling only, window units only) | Energy Star | Binary | Yes | 398 | N/A | N/A | 220.53 | 1272.79 | N/A | N/A | Binary | Yes | -10.25 | -1.1 | 9.29 | N/A | -10.25 | Data Source | Data Type | Workpaper measures | Baseline | Non-Energy Star with louvered sides 6,000 btuh 9.7 EER | 147.0619 | 17.29 | 10.08 | * Plot is of the actual purchase price of 399 RAC bought through the CA C4A program vs. | Model Validation Summary Stats
|  |  | No | 240 | N/A | N/A | 146.72 | 1406.07 |  |  |  | No | 0 | -- | -- | N/A | 0 | NPD | Point of sales |  | Measure | Energy Star with louvered sides 6,000 btuh 10.7 EER | 164.3519 |  |  | Modeled price. Dotted line represents a perfect model fit (slope = 1). | Mean | 0.041112
| Capacity (btuh) | Continuous | 5,500 - 29,000 | 638 | 11086 | 5382 | 183.34 | 1447.97 | N/A | N/A | Continuous | Not specified | 0.023 | 32.22 | 0.0007 | N/A | 0.023 | Weighting | % CA market |  | Baseline | Non-Energy Star without louvered sides 6,000 btuh 9.0 EER | 127.7839 | 14.536 | 9.072 |  | Standard Error | 0.010711
| Chassis type | Categorical | Not Specified | 143 | N/A | N/A | 276.15 | 655.59 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.042896 | 1.3878 | CA unit sales | 63.6% |  | Measure | Energy Star without louvered sides 6,000 btuh 9.9 EER | 142.3199 |  |  |  | Median | 0.020338
|  |  | Fixed | 333 | N/A | N/A | 174.4 | 1704.49 |  | N/A |  | N/A | 0.812 | 0.11 | 7.59 | 0.92908 |  | N observations | N unit sales |  | Baseline | Non-Energy Star with louvered sides 8,000 btuh 9.8 EER | 195.8159 | 17.29 | 10.08 |  | Mode | 0.020338
|  |  | Slide-out | 162 | N/A | N/A | 337.92 | 899.3 |  | N/A |  | N/A | 22.6 | 2.1 | 10.77 | 0.028025 |  | 638 | 161423.66 |  | Measure | Energy Star with louvered sides 8,000 btuh 10.8 EER | 213.1059 |  |  |  | St. Dev. | 0.21395
| Quarter | Categorical | 1 | 111 | N/A | N/A | 204.4 | 621.18 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.021331 | -6.2793 | R2 | Intercept |  | Baseline | Non-Energy Star with louvered sides 14,000 btuh 9.7 EER | 331.0619 | 17.29 | 10.08 |  | Sample Variance | 0.045774
|  |  | 2 | 194 | N/A | N/A | 179.15 | 1931.5 |  | N/A |  | N/A | -3.04 | -0.34 | 9.03 | 0.55162 |  | 0.88 | -269.4 |  | Measure | Energy Star with louvered sides 14,000 btuh 10.7 EER | 348.3519 |  |  |  | Kurtosis | 63.1483
|  |  | 3 | 203 | N/A | N/A | 186.74 | 1649.07 |  | N/A |  | N/A | -10.93 | -1.2 | 9.1 | 0.42039 |  |  |  |  | Baseline | Non-Energy Star with louvered sides 20,000 btuh 8.5 EER | 436.0139 | 14.536 | 9.072 |  | Skewness | 4.9112
|  |  | 4 | 130 | N/A | N/A | 249.1 | 343.54 |  | N/A |  | N/A | -1.12 | -0.06 | 18.76 | 0.0066579 |  |  |  |  | Measure | Energy Star with louvered sides 20,000 btuh 9.4 EER | 450.5499 |  |  |  | Range | 3.3661
| Air direction control | Categorical | 2-way | 101 | N/A | N/A | 119.5 | 431.1 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.48517 | 16.2154 | [9 empty] | Minimum | -0.62982
|  |  | 4-way | 246 | N/A | N/A | 254.42 | 1019.93 |  | N/A |  | N/A | 26.1 | 4.67 | 5.59 | 0.13681 | [10 empty] | Maximum | 2.7363
|  |  | 8-way | 291 | N/A | N/A | 239.57 | 1229.46 |  | N/A |  | N/A | 33.45 | 7.26 | 4.61 | 0.37802 | [10 empty] | Sum | 16.4036
| EER | Continuous | 8.7 - 11 | 638 | 10.2 | 0.6 | 183.34 | 1447.97 | N/A | N/A | Continuous | Not specified | 27.54 | 2.73 | 10.08 | N/A | 27.54 | [9 empty] | Count | 399
| Louvered sides | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Binary | Yes | N/A | N/A |  | N/A | N/A
|  |  |  | N/A | N/A | N/A | N/A | N/A |  |  |  | No | N/A | N/A |  | N/A | N/A
Whole House Fans | CFM | Continuous | 600-6418 | 25 | 2656.48 | 1485.36 | 665.36 | 276.11 | N/A | N/A | N/A | N/A | 0.106 | 5.68 | 0.018 | N/A | 0.106 | Data Source | Data Type | Example Measures | Baseline | Absense of whole house fan | 0 | - | - |  | Model Validation Summary Stats |  | Measure | Whole houe fan 2500 CFM, 1 fan, industrial grade | 1251.7258 | [5 empty] | 1389 | 1329 | 1499
| Number of fans | Continuous | 1,2,4 | 25 | 2656.48 | 1485.36 | 665.36 | 276.11 | N/A | N/A | N/A | N/A | 118.61 | 2.9 | 40.95 | N/A | 118.61 | DEG | Distributor prices |  | Measure | Whole houe fan 2500 CFM, 1 fan, industrial grade | 1251.7258 | 1251.7258 | 190.1782 |  | Mean | -0.037 | Measure | Whole houe fan 1600 CFM, 1 fan | 535.104 | 559 | 559 | 617 | 559
| Industrial grade | Binary | yes | 22 | N/A | N/A | 1139 | 122 | N/A | N/A | N/A | N/A | 570.21 | 6.74 | 84.59 | 0.88 | 501.7848 | Weighting | % CA market |  | Measure | Whole houe fan 1600 CFM, 1 fan | 535.104 | 535.104 | 81.2998 |  | St. Dev. | 0.052 | Measure | Whole houe fan 2500 CFM, 1 fan | 649.584 | 649 | 649 | 671 | 649
|  |  | no | 3 | N/A | N/A | 600.77 | 22.01 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.12 |  | None | Unknown |  | Measure | Whole houe fan 2500 CFM, 1 fan | 649.584 | 649.584 | 98.6931 |  | Min | -0.095 | Measure | Whole houe fan 4500 CFM, 1 fan | 903.984 |  | 999 |  | 999 | 999
| (Do not delete these rows; see cells at right) | [16 empty] | N observations | N unit sales |  | Measure | Whole houe fan 4500 CFM, 1 fan | 903.984 | 903.984 | 137.3448 |  | Max | 0.036 | Measure | Whole houe fan 1150 CFM, 2 fans | 620.196 | 686 | 579 | 550 |  |  | 579
[18 empty] | 25 | N/A |  | Measure | Whole houe fan 1150 CFM, 2 fans | 620.196 | 620.196 | 94.2281
[18 empty] | R2 | Intercept
[18 empty] | 0.789 | 157.71
[18 empty] | MAE | Contr. Markup
[18 empty] | 101.09 | 20%
Diff (Modeled-Actual)
Gas Furnaces (residential) | AFUE | Continuous | 0.78-0.96 | 176 | 0.86875 | 0.0727 | 762.1307 | 283.3864 | Continuous | 0.78 - 0.98 | N/A | N/A | 2056.0641 | 13.74 | 149.6352 | N/A | 2056.0641 | Data Source | Data Type | DEER Measures | Baseline | 78 AFUE (1.242 HIR) Furnace assumed 60 kBtuh capacity without variable speed blower | 586.2321 | 81.4201 | 4.4891 |  | Model Validation Summary Stats |  | Baseline | Furnace AFUE 80 - assumed 60 kBtuh capacity without variable speed blower | 640.5122 | 504.99 | 505 | [10 empty] | 511.79 |  |  |  |  | 489.99 | [7 empty] | 137.5697
| Capacity (Btuh) | Continuous | 32,000-155,000 | 176 | 73738.07 | 23783.26 | 762.1307 | 283.3864 | Continuous | Not specified | N/A | N/A | 0.003247 | 6.88 | 0.0004719 | N/A | 0.003247 | DEG | Distributor prices |  | Measure | Furnace Upgrade to 81% AFUE assumed 60 kBtuh capacity without variable speed blower | 667.6522 |  |  |  | Mean | -0.23407 | Measure | High Efficiency Furnace 90 AFUE(1.11 HIR) - assumed 60 kBtuh capacity without variable speed blower | 911.9126 |  |  |  |  | 914 |  | 976 |  |  |  | 715 | [7 empty] | 791 | [6 empty] | 62.9126
| Variable Speed Blower | Categorical | with variable speed | 50 | N/A | N/A | 1062.7 | 175.0341 | N/A | N/A | N/A | N/A | 319.9647 | 11.83 | 27.0383 | 0.28409 | 90.899 | Weighting | % CA market |  | Baseline | 78 AFUE (1.242 HIR) Furnace assumed 90 kBtuh capacity without variable speed blower | 714.8133 | 325.6806 | 17.9562 |  | St. Dev. | 0.043018 | Baseline | Furnace AFUE 80 - assumed 90 kBtuh capacity without variable speed blower | 769.0934 |  |  | 726.18 |  | 741 |  |  | 867 | [11 empty] | 669 | [5 empty] | 18.2984
|  |  | w/o variable speed | 126 | N/A | N/A | 642.8571 | 223.4827 |  |  | N/A | N/A | 0 | -- | -- | 0.71591 |  | CLASS | Unknown |  | Measure | High Efficiency Furnace 90 AFUE(1.11 HIR) assumed 90 kBtuh capacity without variable speed blower | 1040.4938 |  |  |  | Min | -0.47711 | Measure | Efficient Residential Gas Furnace - AFUE 92 - assumed 90 kBtuh capacity without variable speed blower | 1094.7739 |  | 860 |  | 988.95 |  | 925.68 | [7 empty] | 1079.99 | [11 empty] | 131.1189
| Manufacturer | Categorical | Bryant | 26 | N/A | N/A | 769.8462 | 298.6857 | N/A | N/A | N/A | N/A | -12.2833 | -0.36 | 34.0626 | 0 | 10.2022 | N observations | N unit sales |  | Baseline | 78 AFUE (1.242 HIR) Furnace assumed 120 kBtuh capacity without variable speed blower | 843.3945 | 379.9606 | 20.9489 |  | Max | -0.064678 | Baseline | Furnace AFUE 80 - assumed 120 kBtuh capacity without variable speed blower | 897.6746 | 774.99 | 752 | 818.3 | [17 empty] | 836 |  |  |  |  | 102.3521
|  |  | Day and Night | 6 | N/A | N/A | 676.1667 | 244.2944 | N/A | N/A | N/A | N/A | -171.264 | -2.92 | 58.7054 | 0.0146 |  | 176 | N/A |  | Measure | High Efficiency Furnace 92 AFUE(1.08 HIR) assumed 120 kBtuh capacity without variable speed blower | 1223.3551 | [5 empty] | Measure | Efficient Residential Gas Furnace - AFUE 93 - assumed 120 kBtuh capacity without variable speed blower | 1250.4952 |  |  | 1671.67 | [5 empty] | 1502.55 | [5 empty] | 1837 | [6 empty] | 1969.54 |  |  |  | -494.6948
|  |  | Goodman | 86 | N/A | N/A | 636.5 | 236.8078 | N/A | N/A | N/A | N/A | 36.5412 | 1.3 | 28.2118 | 0.0605 |  | R2 | Intercept |  | Baseline | 78 AFUE (1.242 HIR) Furnace assumed 90 kBtuh capacity without variable speed blower | 714.8133 | 856.5941 | 23.9416 |  |  |  | Baseline | Furnace AFUE 80 - assumed 90 kBtuh capacity without variable speed blower | 769.0934 |  |  | 656 |  |  |  | 760 |  |  | 697 |  | 675 | [13 empty] | 72.0934
|  |  | Ruud | 58 | N/A | N/A | 953.8448 | 237.8094 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0 |  | 0.79427 | -1364.637 |  | Measure | High Efficiency Furnace 94 AFUE(1.06 HIR) assumed 90 kBtuh capacity with variable speed blower | 1571.4074 | [5 empty] | Measure | Efficient Residential Gas Furnace - AFUE 95 - assumed 90 kBtuh capacity with variable speed blower | 1598.5474 | 1527.99 | 1305 | [13 empty] | 1509 | [6 empty] | 1228 |  |  | 206.0499
| (Do not delete these rows; see cells at right) | [16 empty] | MAE | Contr. Markup |  | Baseline | 78 AFUE (1.242 HIR) Furnace assumed 100 kBtuh capacity without variable speed blower | 757.6737 | 910.8742 | 26.9343 |  |  |  | Baseline | Furnace AFUE 80 - assumed 100 kBtuh capacity without variable speed blower | 811.9538 | 672.99 |  |  | 789.95 | 724 | [18 empty] | 695 |  | 91.4688
[18 empty] | 94.48 | 32% |  | Measure | High Efficiency Furnace 96 AFUE(1.03 HIR) assumed 100 kBtuh capacity with variable speed blower | 1668.5479 | [5 empty] | Measure | Efficient Residential Gas Furnace - AFUE 96 - assumed 100 kBtuh capacity with variable speed blower | 1668.5479 |  | 2154.67 |  |  |  | 2098.15 | [10 empty] | 2529 | [7 empty] | 2699 | -701.6571
Split-System HP (residential and commerical) | Cooling Capacity (BtuH) | Continuous | 17400-59000 | 78 | 37376.92 | 12492.23 | 2261.98 | 1388.58 | Discrete | < 55 kBtuh 55 - 64 kBtuh | N/A | N/A | 0.041289 | 7.37 | 0.0056034 | N/A | 0.041289 | Data Source | Data Type | DEER Measures | Baseline | 13 SEER(11.07 EER) / 8.1 HSPF(3.28 COP) A/C Heat pump assumed 36 kBtuh capacity | 1784.6172 | - | - |  |  |  | Baseline | 36 kBtuh 12.5 SEER Split Heat pump | 1510.4721 | 2259 | 1773
| SEER | Continuous | 13-20.5 | 78 | 14.6141 | 2.0272 | 2261.98 | 1388.58 | Continuous | 13 - 16 | N/A | N/A | 456.9085 | 9.54 | 47.8799 | N/A | 456.9085 | DEG/EMCOR | Distributor Prices |  | Measure | 13 SEER(11.07 EER) / 8.1 HSPF(3.28 COP) A/C Heat pump assumed 36 kBtuh capacity | 1784.6172 | 0 | 0 |  |  |  | Baseline | 13 SEER(11.07 EER) / 8.1 HSPF(3.28 COP) A/C Heat pump assumed 36 kBtuh capacity | 1784.6172 |  |  | 2388
| Brand | Categorical | Carrier | 20 | N/A | N/A | 2860.58 | 1463.6 | N/A | N/A | N/A | N/A | 1558.7373 | 8.09 | 192.668 | 0.319 | 533.0532 | Weighting | % CA market |  | Measure | 14 SEER(12.19 EER) / 8.6 HSPF(3.52 COP) A/C Heat Pump assumed 36 kBtuh capacity | 2332.9073 | 548.2902 | 47.8799 |  |  |  | Measure | 14 SEER(12.19 EER) / 8.6 HSPF(3.52 COP) A/C Heat Pump assumed 36 kBtuh capacity | 2332.9073 |  |  | 2799 | 1926.51
|  |  | Day & Night | 20 | N/A | N/A | 1441.3 | 455.66 | N/A | N/A | N/A | N/A | -198.0511 | -1 | 197.3787 | 0 |  | CMST | Unknown |  | Measure | 15 SEER(12.70 EER) / 8.8 HSPF(3.74 COP) A/C Heat Pump assumed 36 kBtuh capacity | 2881.1975 | 1096.5803 | 95.7599 |  |  |  | Measure | 15 SEER(12.70 EER) / 8.8 HSPF(3.74 COP) A/C Heat Pump assumed 36 kBtuh capacity | 2881.1975 |  |  | 3210 | 2204.37
|  |  | Bryant | 19 | N/A | N/A | 3604.42 | 1167.54 | N/A | N/A | N/A | N/A | 675.7732 | 2.61 | 259.3086 | 0.053 |  | N observations | N unit sales |  | Measure | 16 SEER (12.06 EER) / 8.4 HSPF (3.48 COP) A/C Heat Pump assumed 36 kBtuh capacity | 3429.4876 | 1644.8705 | 143.6398 |  |  |  | Measure | 16 SEER (12.06 EER) / 8.4 HSPF (3.48 COP) A/C Heat Pump assumed 36 kBtuh capacity | 3429.4876 |  |  | 3621
|  |  | Goodman | 19 | N/A | N/A | 1153.32 | 241.99 | N/A | N/A | N/A | N/A | 0 | . | . | 0.058 |  | 78 | N/A |  | Baseline | Split HP SEER = 13.0 assumed 18 kBtuh capacity | 892.7748 | - | -
| HSPF | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Continuous | 7.7 - 9 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | R2 | Intercept |  | Measure | Split HP SEER = 14.0 (< 55 kBTUh) - Combined SEER 13 and SEER 14.5 hp assumed 18 kBtuh capacity | 1441.0649 | 548.2902 | 47.8799
| EER | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Continuous | 11.07 - 12.5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.8271 | -6472.0862 |  | Baseline | Split HP SEER = 13.0 (< 55 kbtuh), EER = 11.07, HSPF = 7.7, COP = 3.28; no Econo; 1-spd Fan assumed 24 kBtuh capacity | 1190.0556 | - | -
| (Do not delete these rows; see cells at right) | [16 empty] | MAE | Contr. Markup |  | Measure | Split HP SEER = 13.0 (< 55 kbtuh), EER = 11.07, HSPF = 7.70, COP = 3.28; no Econo; 1-spd Fan assumed 24 kBtuh capacity | 1190.0556 | 0 | 0
[18 empty] | 473.613 | 20% |  | Measure | Split HP SEER = 14.0 (< 55 kbtuh), EER = 12.00, HSPF = 8.50, COP = 3.74; no Econo; 1-spd Fan assumed 24 kBtuh capacity | 1738.3457 | 548.2902 | 47.8799
[21 empty] | Measure | Split HP SEER = 15.0 (< 55 kBtuh), EER = 12.5, HSPF = 9.00, COP = 3.96; no Econo; 1-spd Fan assumed 24 kBtuh capacity | 2286.6359 | 1096.5803 | 95.7599
[21 empty] | Baseline | Split HP SEER = 13.0 assumed 60 kBtuh capacity | 2973.7404 | - | -
[21 empty] | Measure | Split HP SEER = 14.0 (55-64 kBTUh) - Combined SEER 13 and SEER 14.5 hp assumed 60 kBtuh capacity | 3522.0305 | 548.2902 | 47.8799
[21 empty] | Baseline | Split HP SEER = 13.0 (55-64 kbtuh), EER = 11.07, HSPF = 7.7, COP = 3.28; w/Econo; 2-spd Fan assumed 60 kBtuh capacity | 2973.7404 | - | -
[21 empty] | Measure | Split HP SEER = 13.0 (55-64 kbtuh), EER = 11.07, HSPF = 7.70, COP = 3.28; w/Econo; 2-spd Fan assumed 60 kBtuh capacity | 2973.7404 | 0 | 0
[21 empty] | Measure | Split HP SEER = 14.0 (55-64 kbtuh), EER = 12.00, HSPF = 8.50, COP = 3.74; w/Econo; 2-spd Fan assumed 60 kBtuh capacity | 3522.0305 | 548.2902 | 47.8799
[21 empty] | Measure | Split HP SEER = 15.0 (55-64 kBTUh), EER = 12.5, HSPF = 9.00, COP = 3.96; w/Econo; 2-spd Fan assumed 60 kBtuh capacity | 4070.3207 | 1096.5803 | 95.7599
Split-System DX (residential and commerical) | Cooling Capacity (BtuH) | Continuous | 17000-58000 | 83 | 37497.59 | 12344.52 | 1452.318 | 433.4236 | Discrete | < 55 kBtuh 55 - 64 kBtuh | N/A | N/A | 0.023001 | 17.65 | 0.0013033 | N/A | 0.023001 | Data Source | Data Type | DEER Measures | Baseline | 13 SEER (11.09 EER) Split System Air Conditioner assumed 36 kBtuh capacity | 1268.5509 | - | - |  |  |  | Baseline | 36 kBtuh 12.5 SEER Split DX | 1130.3607 | 2050.8 | 1240.5
| SEER | Continuous | 13-18.5 | 83 | 14.5663 | 1.1862 | 1452.318 | 433.4236 | Continuous | 13 - 21 | N/A | N/A | 230.317 | 16.86 | 13.6602 | N/A | 230.317 | DEG/EMCOR | Distributor Prices |  | Measure | 13 SEER(11.09 EER) Split System Air Conditioner assumed 36 kBtuh capacity | 1268.5509 | 0 | 0 |  |  |  | Baseline | 13 SEER(11.09 EER) Split System Air Conditioner assumed 36 kBtuh capacity | 1268.5509 |  | 1404 | 1836
| Brand | Categorical | Bryant | 22 | N/A | N/A | 1375.591 | 406.6431 | N/A | N/A | N/A | N/A | -39.0808 | -0.99 | 39.5337 | 0.26506 | -2.0805 | Weighting | % CA market |  | Measure | 14 SEER(12.15 EER) Split-System Air Conditioner assumed 36 kBtuh capacity | 1544.9312 | 276.3804 | 13.6602 |  |  |  | Measure | 14 SEER(12.15 EER) Split-System Air Conditioner assumed 36 kBtuh capacity | 1544.9312 |  | 2412 | 2193
|  |  | Day and Night | 25 | N/A | N/A | 1491.296 | 431.9159 | N/A | N/A | N/A | N/A | 27.4838 | 0.73 | 37.7992 | 0.3012 |  | None | Unknown |  | Measure | 15 SEER(12.72 EER) Split-System Air Conditioner assumed 36 kBtuh capacity | 1821.3116 | 552.7607 | 27.3204 |  |  |  | Measure | 15 SEER(12.72 EER) Split-System Air Conditioner assumed 36 kBtuh capacity | 1821.3116 |  |  | 2550
|  |  | Goodman | 36 | N/A | N/A | 1472.139 | 455.8442 | N/A | N/A | N/A | N/A | 0 | . | . | 0.43373 |  | N observations | N unit sales |  | Measure | 16 SEER (11.61 EER) Split System Air Conditioner assumed 36 kBtuh capacity | 2097.6919 | 829.1411 | 40.9805 |  |  |  | Measure | 16 SEER (11.61 EER) Split System Air Conditioner assumed 36 kBtuh capacity | 2097.6919 |  |  | 2907
| Clg EIR | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Continuous | 0.2456 - 0.2557 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 83 | N/A |  | Measure | 17 SEER (12.28 EER) Split-System Air Conditioner assumed 36 kBtuh capacity | 2374.0723 | 1105.5214 | 54.6407 |  |  |  | Measure | 17 SEER (12.28 EER) Split-System Air Conditioner assumed 36 kBtuh capacity | 2374.0723 |  |  | 3264
| Supply fan W/cfm | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Continuous | 0.306 - 0.379 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | R2 | Intercept |  | Measure | 18 SEER (13.37 EER) Split-System Air Conditioner assumed 36 kBtuh capacity | 2650.4527 | 1381.9018 | 68.3009 |  |  |  | Measure | 18 SEER (13.37 EER) Split-System Air Conditioner assumed 36 kBtuh capacity | 2650.4527 |  |  | 3624
| Fan speeds | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Discrete | 1 - speed 2 - speed | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.89336 | -2762.9503 |  | Measure | 19 SEER (13.82 EER) Split-System Air Conditioner assumed 36 kBtuh capacity | 2926.833 | 1658.2822 | 81.9611 |  |  |  | Measure | 19 SEER (13.82 EER) Split-System Air Conditioner assumed 36 kBtuh capacity | 2926.833 |  |  | 3981
| (Do not delete these rows; see cells at right) | [16 empty] | MAE | Contr. Markup |  | Measure | 20 SEER (14.43 EER) Split-System Air Conditioner assumed 36 kBtuh capacity | 3203.2134 | 1934.6625 | 95.6213 |  |  |  | Measure | 20 SEER (14.43 EER) Split-System Air Conditioner assumed 36 kBtuh capacity | 3203.2134 |  |  | 4338
[18 empty] | 106.603 | 20% |  | Measure | 21 SEER (15.03 EER) Split-System Air Conditioner assumed 36 kBtuh capacity | 3479.5937 | 2211.0429 | 109.2815 |  |  |  | Measure | 21 SEER (15.03 EER) Split-System Air Conditioner assumed 36 kBtuh capacity | 3479.5937 |  |  | 4560.51
[21 empty] | Baseline | Split AC SEER = 13.0 (< 55 kBtuh), EER = 11.06, Clg EIR = 0.2557, Supply Fan W/cfm = 0.379; no Econo; 1-spd Fan assumed 24 kBtuh capacity | 937.3365 | - | -
[21 empty] | Measure | Split AC SEER = 13.0 (< 55 kBtuh), EER = 11.06, Clg EIR = 0.2557, Supply Fan W/cfm = 0.379; no Econo; 1-spd Fan assumed 24 kBtuh capacity | 937.3365 | 0 | 0
[21 empty] | Measure | Split AC SEER = 14.0 (< 55 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 1-spd Fan assumed 24 kBtuh capacity | 1213.7168 | 276.3804 | 13.6602
[21 empty] | Baseline | Split AC SEER = 13.0 (55-64 kBtuh), EER = 11.06, Clg EIR = 0.2557, Supply Fan W/cfm = 0.379; no Econo; 2-spd Fan assumed 60 kBtuh capacity | 1930.9797 | - | -
[21 empty] | Measure | Split AC SEER = 13.0 (55-64 kBtuh), EER = 11.06, Clg EIR = 0.2557, Supply Fan W/cfm = 0.379; no Econo; 2-spd Fan assumed 60 kBtuh capacity | 1930.9797 | 0 | 0
[21 empty] | Measure | Split AC SEER = 14.0 (55-64 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306; no Econo; 2-spd Fan assumed 60 kBtuh capacity | 2207.36 | 276.3804 | 13.6602
Residential HVAC Fan Motors | Motor Type | Categorical | PSC | 52 | N/A | N/A | 236.49 | 103.95 | N/A | N/A | Categorical | PSC | 0 | . | . | N/A | 0 | Data Source | Data Type | Workpaper measure | Baseline | 0.5 HP Permanent Split Capacitor Motor | 261.7357 | - | - |  | Model Validation Summary Stats |  | Baseline | 0.5 HP Permanent Split Capacitor Motor | 261.7357 | 122.97 | 157.35 | 139.95 | 321.95 | 199.95 | 212.95 | 201.5
|  |  | High-efficiency PSC | 21 | N/A | N/A | 304.39 | 106.89 | N/A | N/A |  | High Eff | 117.02 | 4.7 | 24.91 | N/A | 117.02 | DEG | Distributor Prices |  | Measure | 0.5 HP Brushless Fan Motor | 352.4197 | 90.684 | n/a |  | Mean | 0.26 | Measure | 0.5 HP Brushless Fan Motor | 352.4197 | 198.85 | 507.95 | 674.99 | 640
|  |  | ECM/X13 | 20 | N/A | N/A | 300.52 | 114.92 | N/A | N/A |  | Brushless | 123.15 | 4.91 | 25.09 | N/A | 123.15 | Weighting | % CA market | [7 empty] | St. Dev. | 0.56
| Horsepower | Continuous | 0.167-1 (1/6 - 1 hp) | 93 | 0.47 | 0.22 | 265.5 | 110.85 | N/A | N/A | Discrete | 0.5 hp | 158.75 | 4.1 | 38.72 | N/A | 158.75 | None | Unknown | [7 empty] | Min | -0.48
| Reverisble | Binary | Yes | 64 | N/A | N/A | 243.77 | 107.8 | N/A | N/A | N/A | N/A | -96.81 | 4.12 | 23.48 | 0.68817 | -66.6219 | N observations | N unit sales | [7 empty] | Max | 1.18
|  |  | No | 29 | N/A | N/A | 313.77 | 103.62 | N/A | N/A | N/A | N/A |  |  |  | 0.31183 |  | 93 | Unknown
| Input Voltage > 230 | Binary | Yes | 2 | N/A | N/A | 472.43 | 127.6 | N/A | N/A | N/A | N/A | 100.43 | 1.61 | 62.19 | 0.021505 | 2.1598 | R2 | Intercept
|  |  | No | 91 | N/A | N/A | 261.05 | 106.81 | N/A | N/A | N/A | N/A |  |  |  | 0.97849 |  | 0.51 | 276.73
[5 empty] | N/A | N/A |  |  | N/A | N/A | N/A | N/A |  |  |  | N/A |  | MAE | Contr. Markup
[5 empty] | N/A | N/A |  |  | N/A | N/A | N/A | N/A |  |  |  | N/A |  | 60.34 | 20%
| Number of Speeds | Continuous | 1-5 | 93 | 3.15 | 1.14 | 265.5 | 110.85 | N/A | N/A | N/A | N/A | -23.79 | 2.26 | 10.55 | 1 | -23.79
[5 empty] | N/A | N/A |  |  | N/A | N/A | N/A | N/A |  |  |  | N/A
[5 empty] | N/A | N/A |  |  | N/A | N/A | N/A | N/A |  |  |  | N/A
[5 empty] | N/A | N/A |  |  | N/A | N/A | N/A | N/A |  |  |  | N/A
Non-Residential HVAC
Fan VFDs (>10hp) | Size (horsepower) | Continuous | 1 -100 | 98 | 24.4 | 26.17 | 2714.58 | 1724.19 | N/A | N/A | Continuous | 1-100 | 48.28 | 18.16 | 2.65 | N/A | 45.82 | Data Source | Data Type | Workpaper measures | Baseline | Absence of VFD. Baseline is throttling valves, inlet vanes and fan dampers |  |  |  |  | Model Validation Summary Stats |  | Measure | VFD Supply Fan Motors (20hp, nema 12 enclosure,no bypass) | 2087.8894 | 1603.93 | 1975.76 | 1798.59 | 1605 | 342.0694 | 0.19594
| Manufacturer | Categorical | ABB | 21 | N/A | N/A | 4716.91 | 2334.63 | N/A | N/A | N/A | N/A | 2230.89 | 13 | 171.63 | 0.21429 | 478.0479 | EMCOR | Distributor prices |  | Measure | VFD Supply Fan Motors (20hp, nema 12 enclosure,no bypass) | 2087.8894 | 2087.8894 | 299.4258 |  | Mean | 0.083026 | Measure | VFD Supply Fan Motors (30hp, nema 1 enclosure,no bypass) | 2055.4654 | 1837.72 | 2263.74 | 2060.75 | 1839.3 | 55.0879 | 0.027539
|  |  | Siemens | 77 | N/A | N/A | 2168.49 | 974.65 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.78571 |  | Weighting | % CA market |  | Measure | VFD Supply Fan Motors (30hp, nema 1 enclosure,no bypass) | 2055.4654 | 2055.4654 | 294.7759 |  | St. Dev. | 0.14541 | Measure | VFD Supply Fan Motors (40hp, nema 3 enclosure, with bypass) | 4666.2934 | 4910.98 | 4420.41 | 4024.03 | 4915 | 98.6884 | 0.021606
| Bypass | Binary | Yes | 12 | N/A | N/A | 3150.88 | 1879.64 | N/A | N/A | N/A | N/A | 789.74 | 3.25 | 242.7 | N/A | 789.74 | None | Unknown |  | Measure | VFD Supply Fan Motors (40hp, nema 3 enclosure, with bypass) | 4666.2934 | 4666.2934 | 669.1967 |  | Min | -0.075194 | Measure | VFD Supply Fan Motors (60hp, nema 12 enclosure, no bypass) | 4287.2494 | 4233.8 | 5215.29 | 4747.63 | 4237.5 | -321.3056 | -0.069719
|  |  | No | 86 | N/A | N/A | 2653.69 | 1704.31 | N/A | N/A | N/A | N/A | 0 | -- | -- | N/A | 0 | N observations | N unit sales |  | Measure | VFD Supply Fan Motors (60hp, nema 12 enclosure, no bypass) | 4287.2494 | 4287.2494 | 614.8377 |  | Max | 0.30872 | Measure | VFD Supply Fan Motors (75hp, nema 12 enclosure,no bypass) | 5112.0094 | 3588.51 | 4420.21 | 4024.03 | 3591.7 | 1205.8969 | 0.30872
| NEMA enclosure type | Categorical | 3r | 18 | N/A | N/A | 4001.69 | 2313.43 | N/A | N/A | N/A | N/A | 927.75 | 4.36 | 212.92 | N/A | 927.75 | 98 | N/A |  | Measure | VFD Supply Fan Motors (75hp, nema 12 enclosure,no bypass) | 5112.0094 | 5112.0094 | 733.1172 |  |  |  | Measure | VFD Supply Fan Motors (100hp, nema 1 enclosure,no bypass) | 5904.3454 | 4627 | 5699.65 | 5188.55 | 4631.1 | 867.7704 | 0.17229
|  |  | 12 | 17 | N/A | N/A | 2532.48 | 1220.65 | N/A | N/A | N/A | N/A | 485.22 | 2.74 | 176.85 | N/A | 485.22 | R2 | Intercept |  | Measure | VFD Supply Fan Motors (100hp, nema 1 enclosure,no bypass) | 5904.3454 | 5904.3454 | 846.7467 |  |  |  | Measure | VFD Supply Fan Motors (50hp, nema 1 enclosure,no bypass) | 3155.1454 | 3134.25 | 3860.85 | 3514.64 | 3137 | -256.5396 | -0.075194
|  |  | 1 | 63 | N/A | N/A | 2395.96 | 1485.2 | N/A | N/A | N/A | N/A | 0 | -- | -- | N/A | 0 | 0.8723 | -139.76 |  | Measure | VFD Supply Fan Motors (50hp, nema 1 enclosure,no bypass) | 3155.1454 | 3155.1454 | 452.4818
| (Do not delete these rows; see cells at right) | [16 empty] | MAE | Contr. Markup
[18 empty] | 389.3 | 20%
Fan VFDs (<= 10hp) | Size (horsepower) | Continuous | 1 -100 | 86 | 4.5 | 3.05 | 807.81 | 489.47 | N/A | N/A | Continuous | 1-100 | 38.75 | 11.21 | 3.45 | N/A | 47.97 | Data Source | Data Type | Workpaper measures | Baseline | Absence of VFD. Baseline is throttling valves, inlet vanes and fan dampers |  |  |  |  | Model Validation Summary Stats |  | Measure | VFD Supply Fan Motors (Siemens,1.5hp, nema 12 enclosure,no bypass) | 827.7105 | 591.66 | 728.82 | 663.47 | 592.2 | 183.673 | 0.28519
| Manufacturer | Categorical | ABB | 15 | N/A | N/A | 1408.27 | 625.71 | N/A | N/A | N/A | N/A | 447.68 | 14.54 | 30.79 | 0.17442 | 78.0837 | EMCOR | Distributor prices |  | Measure | VFD Supply Fan Motors (1.5hp, nema 12 enclosure,no bypass) | 827.7105 | 827.7105 | 73.0257 |  | Mean | 0.12866 | Measure | VFD Supply Fan Motors (Siemens,5hp, nema 1 enclosure,no bypass) | 730.8765 | 616.9 | 759.91 | 569 | 617.4 | 90.074 | 0.14056
|  |  | Siemens | 71 | N/A | N/A | 680.95 | 345.01 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.82558 |  | Weighting | % CA market |  | Measure | VFD Supply Fan Motors (5hp, nema 1 enclosure,no bypass) | 730.8765 | 730.8765 | 64.4824 |  | St. Dev. | 0.11536 | Measure | VFD Supply Fan Motors (Siemens,10hp, nema 1 enclosure, no bypass) | 1018.6965 | 916.58 | 1129.07 | 1027.82 | 917.4 | 20.979 | 0.021027
| Bypass | Binary | Yes | 1 | N/A | N/A | 1313 | 0 | N/A | N/A | N/A | N/A | 283.54 | 2.8 | 101.35 | N/A | 283.54 | None | Unknown |  | Measure | VFD Supply Fan Motors (10hp, nema 1 enclosure, no bypass) | 1018.6965 | 1018.6965 | 89.8757 |  | Min | 0.021027 | Measure | VFD Supply Fan Motors (Siemens,10hp, nema 3r enclosure,no bypass) | 2243.1165 | 1929.9 | 2377.29 | 2164.12 | 1931 | 142.539 | 0.067857
|  |  | No | 85 | N/A | N/A | 801.87 | 489.24 | N/A | N/A | N/A | N/A | 0 | -- | -- | N/A | 0 | N observations | N unit sales |  | Measure | VFD Supply Fan Motors (10hp, nema 3r enclosure,no bypass) | 2243.1165 | 2243.1165 | 197.9016 |  | Max | 0.28519
| NEMA enclosure type | Categorical | 3r | 16 | N/A | N/A | 1695.05 | 378.1 | N/A | N/A | N/A | N/A | 1020.35 | 34.53 | 29.55 | N/A | 1020.35 | 86 | N/A
|  |  | 12 | 14 | N/A | N/A | 782.42 | 164.42 | N/A | N/A | N/A | N/A | 248.59 | 8.44 | 29.45 | N/A | 248.59 | R2 | Intercept
|  |  | 1 | 56 | N/A | N/A | 560.67 | 183.09 | N/A | N/A | N/A | N/A | 0 | -- | -- | N/A | 0 | 0.9641 | 291.13
| 500 volts | Binary | Yes | 23 | N/A | N/A | 653.11 | 171.77 | N/A | N/A | N/A | N/A | 114.46 | 4.52 | 25.31 | N/A | 114.46 | MAE | Contr. Markup
|  |  | No | 63 | N/A | N/A | 864.29 | 553.05 | N/A | N/A | N/A | N/A | 0 | -- | -- | N/A | 0 | 71.27 | 20%
Small Packaged DX (<= 5 tons) | SEER | Continuous | 13 - 17 | 41 | 13.6244 | 1.2101 | 2464.8 | 756.06 | Continuous | 12 - 14 | N/A | N/A | 289.4137 | 6.08 | 47.6369 | N/A | 289.4137 | Data Source | Data Type | DEER Measures | Baseline | Pkg AC SEER = 13.00; EER = 11.06; Clg EIR = 0.256; Supply Fan W/cfm = 0.379; no econo assumed 2 ton | 2650.3246 | 361.7672 | 47.6369 |  |  |  | Baseline | Pkg AC SEER = 13.00; EER = 11.06; Clg EIR = 0.256; Supply Fan W/cfm = 0.379; no econo assumed 2 ton | 2650.3246 | 1744 | 1930.8 | 1464 | 1580.8
| Capacity (BtuH) | Continuous | 24,000-60,000 | 41 | 48378.05 | 10868.98 | 2464.8 | 756.06 | Discrete | < 65,000 | N/A | N/A | 0.02587 | 6.43 | 0.0040218 | N/A | 0.02587 | EMCOR | Distributor Prices |  | Measure | Pkg AC SEER = 14.0 (< 65 kBtuh), EER = 11.06, Clg EIR = 0.2557, Supply Fan W/cfm = 0.379 assumed 2 ton | 3012.0918 | [5 empty] | Measure | Pkg AC SEER = 14.0 (< 65 kBtuh), EER = 11.06, Clg EIR = 0.2557, Supply Fan W/cfm = 0.379 assumed 2 ton | 3012.0918 | 2271 | 2126.4 |  | 1635.72
| Phase | Binary | 1 | 24 | N/A | N/A | 2648.92 | 762.03 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.58537 | 16.2844 | Weighting | % CA market |  | Baseline | Pkg AC SEER = 13.00; EER = 11.06; Clg EIR = 0.256; Supply Fan W/cfm = 0.379; no econo assumed 5 ton | 3814.4746 | 361.7672 | 47.6369 |  |  |  | Baseline | Pkg AC SEER = 13.00; EER = 11.06; Clg EIR = 0.256; Supply Fan W/cfm = 0.379; no econo assumed 5 ton | 3814.4746 | 3321 | 4827 | 2484 | 3952
|  |  | 3 | 17 | N/A | N/A | 2204.88 | 686.8 | N/A | N/A | N/A | N/A | 39.2741 | 0.31 | 125.0227 | 0.41463 |  | CMST | Unknown |  | Measure | Pkg AC SEER = 14.0 (< 65 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306 assumed 5 ton | 4176.2418 | [5 empty] | Measure | Pkg AC SEER = 14.0 (< 65 kBtuh), EER = 12.04, Clg EIR = 0.2456, Supply Fan W/cfm = 0.306 assumed 5 ton | 4176.2418 | 4638 | 5316 |  | 4089.3
| Voltage | Binary | 208 | 33 | N/A | N/A | 2478.94 | 716.25 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.80488 | 28.2388 | N observations | N unit sales
|  |  | 460 | 8 | N/A | N/A | 2406.5 | 957.27 | N/A | N/A | N/A | N/A | 144.7239 | 1.09 | 132.9882 | 0.19512 |  | 41 | N/A
| Manufacturer | Categorical | Carrier | 8 | N/A | N/A | 3018.63 | 666.82 | N/A | N/A | N/A | N/A | -80.5703 | -0.57 | 141.8109 | 0 | -12.1275 | R2 | Intercept
|  |  | Lennox | 24 | N/A | N/A | 1971.67 | 236.96 | N/A | N/A | N/A | N/A | -791.3212 | -5.1 | 155.0277 | 0.015326 |  | 0.89431 | -2295.3947
|  |  | Trane | 9 | N/A | N/A | 3287.56 | 714.02 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.17625 |  | MAE | Contr. Markup
| Clg EIR | Continuous | N/A | N/A | N/A | N/A | N/A | N/A | Continuous | 0.2456 - 0.2761 | N/A | N/A | [5 empty] | 184.548 | 25%
| Suppy fan W/cfm | Continuous | N/A | N/A | N/A | N/A | N/A | N/A | Continuous | 0.306 - 0.409 | N/A | N/A
Large Packaged DX (> 5 tons) | EER | Continuous | 9.5-13 | 43 | 10.7535 | 0.95328 | 28230.67 | 28669.07 | Continuous | 9.5 - 12 | N/A | N/A | 2312.2262 | 2.02 | 1147.4072 | N/A | 2312.2262 | Data Source | Data Type | DEER Measures | Baseline | Pkg AC EER = 10.80; Clg EIR = 0.262; Supply Fan W/cfm = 0.269514; Cond Fan W/Btuh = 0.00535136; w/ econo assumed 187 kBtuh | 14805.8033 | - | - |  |  |  | Measure | 240 kBtuh 10.9 EER Air Cooled Pkg DX | 20163.6384 | 17640 | 14180 | 15715.4 | 15317.2 | 12133.6
| Capacity (BtuH) | Continuous | 83,000-1,270,420 | 43 | 387321.8 | 361279.2 | 28230.67 | 28669.07 | Discrete | 65-89, 90-134, 135-239, 240-759, >=760 | N/A | N/A | 0.07988 | 27.45 | 0.00291 | N/A | 0.07988 | EMCOR | Distributor Prices |  | Measure | Pkg AC EER = 10.8 (135-239 kBtuh), Clg EIR = 0.2622, Supply Fan W/cfm = 0.270, Cond Fan W/Btuh = 0.0053 assumed 187 kBtuh | 14805.8033 | 0 | 0 |  |  |  | Measure | 840 kBtuh 10 EER Air Cooled Pkg DX | 75180.0342 | 79200 |  | 38860.5 | 46416.3 | 39329
| Voltage | Binary | 208 | 8 | N/A | N/A | 12200 | 5507.67 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.18605 | -1495.6226 | Weighting | % CA market |  | Measure | Pkg AC EER = 11.5 (135-239 kBtuh), Clg EIR = 0.2439, Supply Fan W/cfm = 0.233, Cond Fan W/Btuh = 0.0064 assumed 187 kBtuh | 16748.0733 | 1942.27 | 803.185
|  |  | 460 | 35 | N/A | N/A | 31894.83 | 30574.09 | N/A | N/A | N/A | N/A | -1837.4792 | -0.77 | 2392.1053 | 0.81395 |  | None | Unknown |  | Measure | Pkg AC EER = 12.0 (135-239 kBtuh), Clg EIR = 0.2307, Supply Fan W/cfm = 0.165, Cond Fan W/Btuh = 0.0089 assumed 187 kBtuh | 18135.409 | 3329.6057 | 1376.8886
| Gas Heat Option | Binary | Yes | 17 | N/A | N/A | 44291.35 | 34696.26 | Binary | Yes | N/A | N/A | -2206.57 | -1.07 | 2064.9251 | 0.39535 | -872.3649 | N observations | N unit sales |  | Baseline | Pkg AC EER = 9.80; w/ furnace; w/ econo assumed 500 kBtuh | 42034.0599 | - | -
|  |  | No | 26 | N/A | N/A | 17729.46 | 17896.3 |  | No | N/A | N/A | 0 | -- | -- | 0.60465 |  | 43 | N/A |  | Measure | Pkg AC EER = 10.5 (240-759 kBtuh) assumed 500 kBtuh | 43976.3299 | 1942.27 | 803.185
| Manufacturer | Categorical | Carrier | 17 | N/A | N/A | 25236.94 | 25925.01 | N/A | N/A | N/A | N/A | -65.4247 | -0.03 | 2399.1318 | 0.39535 | 1351.3608 | R2 | Intercept |  | Measure | Pkg AC EER = 10.8 (240-759 kBtuh) assumed 500 kBtuh | 44808.7313 | 2774.6714 | 1147.4072
|  |  | McQuay | 9 | N/A | N/A | 64166.67 | 29815.05 | N/A | N/A | N/A | N/A | 6580.0814 | 1.79 | 3669.4054 | 0.2093 |  | 0.98181 | -26554.8064 |  | Measure | Pkg AC EER = 9.8 (240-759 kBtuh) assumed 500 kBtuh | 42034.0599 | 0 | 0
|  |  | Trane | 17 | N/A | N/A | 12199.47 | 5653.25 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.39535 |  | MAE | Contr. Markup |  | Baseline | Pkg AC EER = 11.00; Clg EIR = 0.257; Supply Fan W/cfm = 0.298; Cond Fan W/Btuh = 0.0053; no econo assumed 77 kBtuh | 4816.5776 | - | -
| Clg EIR | Continuous | N/A | N/A | N/A | N/A | N/A | N/A | Continuous | 0.2304 - 0.2622 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2801.769 | 20% |  | Measure | Pkg AC EER = 11.0 (65-89 kBtuh), Clg EIR = 0.2570, Supply Fan W/cfm = 0.298, Cond Fan W/Btuh = 0.0053 assumed 77 kBtuh | 4816.5776 | 0 | 0
| Suppy fan W/cfm | Continuous | N/A | N/A | N/A | N/A | N/A | N/A | Continuous | 0.165 - 0.298 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  |  | Measure | Pkg AC EER = 11.5 (65-89 kBtuh), Clg EIR = 0.2401, Supply Fan W/cfm = 0.248, Cond Fan W/Btuh = 0.0060 assumed 77 kBtuh | 6203.9133 | 1387.3357 | 573.7036
| Cond fan W/Btuh | Continuous | N/A | N/A | N/A | N/A | N/A | N/A | Continuous | 0.0053 - 0.0089 | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  |  |  | Measure | Pkg AC EER = 12.0 (65-89 kBtuh), Clg EIR = 0.2304, Supply Fan W/cfm = 0.238, Cond Fan W/Btuh = 0.0057 assumed 77 kBtuh | 7591.249 | 2774.6714 | 1147.4072
| (Do not delete these rows; see cells at right) | [19 empty] | Baseline | Pkg AC EER = 11.00; Clg EIR = 0.257; Supply Fan W/cfm = 0.298; Cond Fan W/Btuh = 0.0053; w/ econo assumed 112 kBtuh | 8171.5376 | - | -
[21 empty] | Measure | Pkg AC EER = 11.0 (90-134 kBtuh), Clg EIR = 0.2570, Supply Fan W/cfm = 0.298, Cond Fan W/Btuh = 0.0053Pkg AC EER = 11.5 (90-134 kBtuh), Clg EIR = 0.2401, Supply Fan W/cfm = 0.248, Cond Fan W/Btuh = 0.0060 assumed 112 kBtuh | 8171.5376 | 0 | 0
[21 empty] | Measure | Pkg AC EER = 11.5 (90-134 kBtuh), Clg EIR = 0.2401, Supply Fan W/cfm = 0.248, Cond Fan W/Btuh = 0.0060 assumed 112 kBtuh | 9558.8733 | 1387.3357 | 573.7036
[21 empty] | Measure | Pkg AC EER = 12.0 (90-134 kBtuh), Clg EIR = 0.2304, Supply Fan W/cfm = 0.238, Cond Fan W/Btuh = 0.0057 assumed 112 kBtuh | 10946.209 | 2774.6714 | 1147.4072
[21 empty] | Baseline | Pkg AC EER = 9.50; w/ furnace; w/ econo assumed 760 kBtuh | 66124.2185 | - | -
[21 empty] | Measure | Pkg AC EER = 10.2 (>= 760 kBtuh) assumed 760 kBtuh | 68066.4884 | 1942.27 | 803.185
[21 empty] | Measure | Pkg AC EER = 9.5 (>= 760 kBtuh) assumed 760 kBtuh | 66124.2185 | 0 | 0
[21 empty] | Measure | Pkg AC EER = 9.7 (>= 760 kBtuh) assumed 760 kBtuh | 66679.1528 | 554.9343 | 229.4814
Air-Cooled Chillers | Capacity (tons) | Continuous | 45-400 | 37 | 202.3541 | 96.0277 | 103957.36 | 46978.97 | Continuous | Not specified | N/A | N/A | 504.8886 | 40.67 | 12.4136 | N/A | 504.8886 | Data Source | Data Type | DEER Measures | Baseline | Air cooled package reciprocating chiller (1.260 kW/ton) | N/A | N/A | N/A |  |  |  | Baseline | Air cooled package screw chiller (1.260 kW/ton) assumed 50 ton | 18617.0523
| kW/ton | Continuous | 1.054-1.25 | 37 | 1.1823 | 0.054673 | 103957.36 | 46978.97 | Continuous | 1.008 - 1.260 | N/A | N/A | -113083.3748 | -5.19 | 21774.9811 | N/A | -113083.3748 | EMCOR | Distributor Prices |  | Measure | Air cooled package reciprocating chiller (1.008 kW/ton) | N/A | [5 empty] | Measure | Air cooled screw chiller (1.008 kW/ton) assumed 50 ton | 54238.3154 |  | 24400 | 27604.5
| Compressor type | Categorical | Screw | 23 | N/A | N/A | 123724.89 | 41052.52 | Categorical | Screw | N/A | N/A | 0 | -- | -- | N/A | 0 | Weighting | % CA market |  | Baseline | Air cooled package screw chiller (1.260 kW/ton) assumed 50 ton | 18617.0523 | 35621.2631 | 5487.2952 |  |  |  | Baseline | Air cooled package Scroll chiller (1.260 kW/ton) assumed 100 ton | 52820.0897 | 62500
|  |  | Scroll | 14 | N/A | N/A | 71482.14 | 37849.62 |  | N/A | N/A | N/A | 2117.9999 | 0.77 | 2736.406 | N/A | 2117.9999 | CEUS | Unknown |  | Measure | Air cooled screw chiller (1.008 kW/ton) assumed 50 ton | 54238.3154 | [5 empty] | Measure | Air cooled Scroll chiller (1.008 kW/ton) assumed 100 ton | 88441.3528
|  |  | Reciprocating | N/A | N/A | N/A | N/A | N/A |  | Reciprocating | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N observations | N unit sales |  | Baseline | Air cooled package screw chiller (1.260 kW/ton) assumed 130 ton | 69105.9123 | 35621.2631 | 5487.2952 |  |  |  | Baseline | Air cooled package screw chiller (1.260 kW/ton) assumed 130 ton | 69105.9123 |  |  |  | 92571
| Manufacturer | Categorical | Carrier | 17 | N/A | N/A | 106925.29 | 52283.32 | N/A | N/A | N/A | N/A | 4253.6888 | 1.86 | 2288.0485 | 0.162 | -4129.8779 | 37 | N/A |  | Measure | Air cooled screw chiller (1.008 kW/ton) assumed 130 ton | 104727.1754 | [5 empty] | Measure | Air cooled screw chiller (1.008 kW/ton) assumed 130 ton | 104727.1754
|  |  | Trane | 7 | N/A | N/A | 119714.29 | 46417.36 | N/A | N/A | N/A | N/A | -18678.1995 | -6.75 | 2767.5444 | 0.258 |  | R2 | Intercept | Example Measures | Baseline | Air cooled package Scroll chiller (1.260 kW/ton) assumed 100 ton | 52820.0897 | 35621.2631 | 5487.2952 |  |  |  | Baseline | Air cooled package Scroll chiller (1.260 kW/ton) assumed 50 ton | 21264.5522 |  |  |  | 41840
|  |  | York | 13 | N/A | N/A | 91591.73 | 39700.1 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.052 |  | 0.98802 | 136264.142 |  | Measure | Air cooled Scroll chiller (1.008 kW/ton) assumed 100 ton | 88441.3528 | [5 empty] | Measure | Air cooled Scroll chiller (1.008 kW/ton) assumed 50 ton | 56885.8153
| (Do not delete these rows; see cells at right) | [16 empty] | MAE | Contr. Markup | Example Measures | Baseline | Air cooled package Scroll chiller (1.260 kW/ton) assumed 50 ton | 21264.5522 | 35621.2631 | 5487.2952
[18 empty] | 3787.716 | 25% |  | Measure | Air cooled Scroll chiller (1.008 kW/ton) assumed 50 ton | 56885.8153
Water-Cooled Chillers (excluding centrifugal VSD) | Capacity (tons) | Continuous | 59.9-550 | 48 | 252.8792 | 124.3673 | 97928.28 | 45776.62 | Discrete | < 150, 150-299, >=300 | N/A | N/A | 251.2925 | 8.45 | 29.7401 | N/A | 251.2925 | Data Source | Data Type | DEER Measures | Baseline | Water cooled centrifugal chiller (0.634 kW/ton) assumed 175 ton | 74824.2142 | 30530.2845 | 7229.5528 |  |  |  | Baseline | Water cooled centrifugal chiller (0.634 kW/ton) assumed 175 ton | 74824.2142
| kW/ton | Continuous | 0.478-0.769 | 48 | 0.62406 | 0.079306 | 97928.28 | 45776.62 | Continuous | 0.461 - 0.790 | N/A | N/A | -200329.9507 | -3.52 | 56925.6128 | N/A | -200329.9507 | EMCOR | Distributor Prices |  | Measure | Water cooled centrifugal chiller (150-299 tons, 0.507 kW/ton) assumed 175 ton | 105354.4987 | [5 empty] | Measure | Water cooled centrifugal chiller (150-299 tons, 0.507 kW/ton) assumed 175 ton | 105354.4987 |  |  |  | 103439
| Compressor type | Categorical | Centrifugal | 10 | N/A | N/A | 116440 | 17458.79 | Categorical | Centrifugal | N/A | N/A | -18496.3034 | -2.93 | 6309.6351 | N/A | -18496.3034 | Weighting | % CA market |  | Baseline | Water cooled centrifugal chiller (0.576 kW/ton) assumed 300 ton | 126461.0538 | 27645.5332 | 6546.4455 |  |  |  | Baseline | Water cooled centrifugal chiller (0.576 kW/ton) assumed 300 ton | 126461.0538 | 145605.6 | 101100
|  |  | Screw | 31 | N/A | N/A | 105028.47 | 46995.32 |  | Screw | N/A | N/A | 0 | -- | -- | N/A | 0 | None | Unknown |  | Measure | Water cooled centrifugal chiller (>= 300 tons, 0.461 kW/ton) assumed 300 ton | 154106.587 | [5 empty] | Measure | Water cooled centrifugal chiller (>= 300 tons, 0.461 kW/ton) assumed 300 ton | 154106.587 |  | 105900 |  | 83703
|  |  | Scroll | 7 | N/A | N/A | 40039.29 | 13170.43 |  | N/A | N/A | N/A | -4315.6964 | -0.58 | 7472.9399 | N/A | -4315.6964 | N observations | N unit sales |  | Baseline | Water cooled centrifugal chiller (0.700 kW/ton) assumed 100 ton | 36341.7571 | 33655.4317 | 7969.5858 |  |  |  | Baseline | Water cooled centrifugal chiller (0.700 kW/ton) assumed 100 ton | 36341.7571 | 50064
|  |  | Reciprocating | N/A | N/A | N/A | N/A | N/A |  | Reciprocating | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 48 | N/A |  | Measure | Water cooled centrifugal chiller (< 150 tons, 0.560 kW/ton) assumed 100 ton | 69997.1888 | [5 empty] | Measure | Water cooled centrifugal chiller (< 150 tons, 0.560 kW/ton) assumed 100 ton | 69997.1888 |  |  |  | 67026
| (Do not delete these rows; see cells at right) | [16 empty] | R2 | Intercept |  | Baseline | Water cooled screw chiller (0.718 kW/ton) assumed 225 ton | 91904.0693 | 34617.0155 | 8197.2882 |  |  |  | Baseline | Water cooled screw chiller (0.718 kW/ton) assumed 225 ton | 91904.0693 |  |  | 78075 | 81227.25 | 94663 | 81729
[18 empty] | 0.9065 | 163882.8165 |  | Measure | Water cooled screw chiller (150-299 tons, 0.574 kW/ton) assumed 225 ton | 126521.0848 | [5 empty] | Measure | Water cooled screw chiller (150-299 tons, 0.574 kW/ton) assumed 225 ton | 126521.0848 |  |  | 83700 | 96979.5
[18 empty] | MAE | Contr. Markup |  | Baseline | Water cooled screw chiller (0.639 kW/ton) assumed 300 ton | 133511.6736 | 30770.6804 | 7286.4784 |  |  |  | Baseline | Water cooled screw chiller (0.639 kW/ton) assumed 300 ton | 133511.6736 | 145605.6 |  |  | 87996 | 119767 | 86643
[18 empty] | 10905.322 | 20% |  | Measure | Water cooled screw chiller (>= 300 tons, 0.511 kW/ton) assumed 300 ton | 164282.354 | [5 empty] | Measure | Water cooled screw chiller (>= 300 tons, 0.511 kW/ton) assumed 300 ton | 164282.354 |  |  |  | 102396
[21 empty] | Baseline | Water cooled screw chiller (0.790 kW/ton) assumed 100 ton | 36901.6865 | 37982.5587 | 8994.2468 |  |  |  | Baseline | Water cooled screw chiller (0.790 kW/ton) assumed 100 ton | 36901.6865 | 50064 |  | 44300 | 47538 | 57530 | 45488
[21 empty] | Measure | Water cooled screw chiller (< 150 tons, 0.632 kW/ton) assumed 100 ton | 74884.2452 | [5 empty] | Measure | Water cooled screw chiller (< 150 tons, 0.632 kW/ton) assumed 100 ton | 74884.2452 |  |  | 49200 | 60351
Water-Cooled Centrifugal VSD Chillers (>= 300 tons) | Capacity (tons) | Continuous | 300-1500 | 23 | 776.087 | 384.9054 | 333054.35 | 176477.45 | Discrete | < 150, 150-299, >=300 | N/A | N/A | 442.7794 | 27.36 | 16.1862 | N/A | 442.7794 | Data Source | Data Type | DEER Measures | Baseline | Water cooled centrifugal chiller (0.573 kW/ton) assumed 500 tons | 187492.4416 | - | - |  |  |  | Baseline | Water cooled centrifugal chiller (0.573 kW/ton) assumed 500 tons | 187492.4416 | 145000
| kW/ton | Continuous | 0.518-0.596 | 23 | 0.55435 | 0.0232 | 333054.35 | 176477.45 | Continuous | 0.461 - 0.560 | N/A | N/A | -448127.4111 | -1.99 | 224689.723 | N/A | -448127.4111 | EMCOR | Distributor Prices |  | Measure | Water cooled VSD centrifugal chiller (>= 300 tons, 0.461 kW/ton), load control tower assumed 500 tons | 302924.3018 | 115431.8602 |  |  |  |  | Measure | Water cooled VSD centrifugal chiller (>= 300 tons, 0.461 kW/ton), load control tower assumed 500 tons | 302924.3018 | 186500 | 237730
| Manufacturer | Categorical | Carrier | 9 | N/A | N/A | 302055.56 | 149658.92 | N/A | N/A | N/A | N/A | -3328.02 | -0.3 | 11015.4867 | 0.254 | -3218.0456 | Weighting | % CA market
|  |  | Trane | 4 | N/A | N/A | 141750 | 17783.42 | N/A | N/A | N/A | N/A | -9845.3466 | -0.59 | 16806.8011 | 0.241 |  | CEUS | Unknown
|  |  | York | 10 | N/A | N/A | 437475 | 163628.58 | N/A | N/A | N/A | N/A | 0 | . | . | 0.139 |  | N observations | N unit sales
| (Do not delete these rows; see cells at right) | [16 empty] | 23 | N/A
[18 empty] | R2 | Intercept
[18 empty] | 0.98767 | 240852.0003
[18 empty] | MAE | Contr. Markup
[18 empty] | 15465.169 | 20%
Small Packaged HP (< 65,000 Btuh) | Rated Capacity (Btuh) | Continuous | 24000-60000 | 34 | 47470.59 | 11089.81 | 2870.69 | 1004.92 | Discrete | < 65,000 btuh | N/A | N/A | 0.024893 | 5.69 | 0.004374 | N/A | 0.024893 | Data Source | Data Type | DEER Measures | Baseline | Pkg HP SEER = 13.0 (< 65 kbtuh) assumed 40,000 btuh capacity | 3446.569 | - | - |  |  |  | Baseline | Pkg HP SEER = 13.0 (< 65 kbtuh) assumed 60,000 btuh capacity | 4044.001 | 3168 | 4795
| SEER | Continuous | 13-15 | 34 | 13.1765 | 0.5758 | 2870.69 | 1004.92 | Continuous | 13 - 15 | N/A | N/A | 354.9078 | 3.64 | 97.4137 | N/A | 354.9078 | EMCOR | Distributor Prices |  | Measure | Pkg HP SEER = 14.0 (< 65 kbtuh), EER = 11.6, HSPF = 8.00, COP = 3.52 assumed 40,000 btuh capacity | 3872.4584 | 425.8894 | 97.4137 |  |  |  | Measure | Pkg HP SEER = 14.0 (< 65 kbtuh), EER = 11.6, HSPF = 8.00, COP = 3.52 assumed 60,000 btuh capacity | 4469.8904 |  | 4975
| Brand | Categorical | JCI | 1 | N/A | N/A | 6256 | N/A | N/A | N/A | N/A | N/A | 3061.6192 | 9.85 | 310.7209 | 0 | 175.6109 | Weighting | % CA market |  | Measure | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 assumed 40,000 btuh capacity | 4298.3478 | 851.7788 | 194.8273 |  |  |  | Measure | Pkg HP SEER = 15.0 (< 65 kbtuh), EER = 12.0, HSPF = 8.50, COP = 3.74 assumed 60,000 btuh capacity | 4895.7798
|  |  | Lennox | 22 | N/A | N/A | 2307.27 | 301.77 | N/A | N/A | N/A | N/A | -527.2933 | -3.22 | 163.5872 | 0.033 |  | CMST | Unknown |  | Measure | Pkg HP SEER = 14.5 (< 65 kBtuh) - Combined SEER 14 and SEER 15 hp assumed 40,000 btuh capacity | 4085.4031 | 638.8341 | 146.1205 |  |  |  | Measure | Pkg HP SEER = 14.5 (< 65 kBtuh) - Combined SEER 14 and SEER 15 hp assumed 60,000 btuh capacity | 4682.8351
|  |  | Carrier | 8 | N/A | N/A | 3987.54 | 630.62 | N/A | N/A | N/A | N/A | 751.0177 | 3.85 | 194.8273 | 0.257 |  | N observations | N unit sales
|  |  | Trane | 3 | N/A | N/A | 2895.67 | 320.15 | N/A | N/A | N/A | N/A | 0 | . | . | 0.112 |  | 34 | N/A
| (Do not delete these rows; see cells at right) | [16 empty] | R2 | Intercept
[18 empty] | 0.9409 | -2912.9919
[18 empty] | MAE | Contr. Markup
[18 empty] | 182.44 | 20%
Large Packaged HP (65,000 - 240,000 Btuh) | Rated Capacity (Btuh) | Continuous | 72000-240000 | 39 | 127384.6 | 53567.77 | 11172.4 | 5748.77 | Discrete | 65-89, 90-134, 135-239 | N/A | N/A | 0.088907 | 10.44 | 0.00852 | N/A | 0.088907 | Data Source | Data Type | DEER Measures | Baseline | Pkg HP EER = 10.6 assumed 187 kBtuh capacity | 18560.5172 | - | - |  |  |  | Measure | Pkg HP EER = 10.7 90 kBtuh capacity | 8406.5937 | 4800
| EER | Continuous | 9.7-12.6 | 39 | 11.2192 | 0.61555 | 11172.4 | 5748.77 | Continuous | 9.5 - 12.0 | N/A | N/A | 1623.761 | 1.99 | 813.9252 | N/A | 1623.761 | EMCOR | Distributor Prices |  | Measure | Pkg HP EER = 11.5 (135-239 kBtuh), COP = 3.2 assumed 187 kBtuh capacity | 20314.1791 | 1753.6619 | 732.5326 |  |  |  | Baseline | Pkg HP EER = 10.9 assumed 120 kBtuh capacity | 11996.9484 |  | 7480
| Power exhaust | Binary | No | 34 | N/A | N/A | 10171.38 | 5281.06 | N/A | N/A | N/A | N/A | -6775.3744 | -5.07 | 1337.5939 | 0.87179 | -5906.7367 | Weighting | % CA market |  | Measure | Pkg HP EER = 12.0 (135-239 kBtuh), COP = 3.2 assumed 187 kBtuh capacity | 21288.4357 | 2727.9185 | 1139.4952 |  |  |  | Baseline | Pkg HP EER = 10.5 (135-239 kBtuh), COP = 3.2 assumed 180 kBtuh capacity | 17618.8471 |  | 11085 |  | 16125
|  |  | Yes | 5 | N/A | N/A | 17979.3 | 4175.55 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.12821 |  | None | Unknown |  | Baseline | Pkg HP EER = 11.0 assumed 77 kBtuh capacity | 7604.1985 | - | - |  |  |  | Baseline | Pkg HP EER = 11.0 assumed 120 kBtuh capacity | 12191.7997 |  |  | 10200
| Distributor | Categorical | US Air Distributors | 7 | N/A | N/A | 8118.31 | 3922.94 | N/A | N/A | N/A | N/A | -5622.1753 | -4.44 | 1264.8456 | 0.17949 | -3133.8976 | N observations | N unit sales |  | Measure | Pkg HP EER = 11.5 (65-89 kBtuh), COP = 3.4 assumed 77 kBtuh capacity | 8578.4551 | 974.2566 | 406.9626 |  |  |  | Baseline | Pkg HP EER = 10.5 assumed 360 kBtuh capacity | 36822.7591 |  | 21870
|  |  | JCI | 3 | N/A | N/A | 14822.67 | 7408.93 | N/A | N/A | N/A | N/A | -513.2507 | -0.33 | 1567.9304 | 0.076923 |  | 39 | N/A |  | Measure | Pkg HP EER = 12.0 (65-89 kBtuh), COP = 3.4 assumed 77 kBtuh capacity | 9552.7117 | 1948.5132 | 813.9252
|  |  | Siglers | 14 | N/A | N/A | 11105.32 | 6184.71 | N/A | N/A | N/A | N/A | -5020.2661 | -4.68 | 1072.6952 | 0.35897 |  | R2 | Intercept |  | Baseline | Pkg HP EER = 11.0 assumed 112 kBtuh capacity | 11338.2925 | - | -
|  |  | Unspecified | 9 | N/A | N/A | 11775.87 | 5076.6 | N/A | N/A | N/A | N/A | 0 | . | . | 0.23077 |  | 0.87297 | -9329.7439 |  | Measure | Pkg HP EER = 11.5 (90-134 kBtuh), COP = 3.4 assumed 112 kBtuh capacity | 12312.5491 | 974.2566 | 406.9626
|  |  | Pacific Coast Trane | 6 | N/A | N/A | 12161.67 | 6867.37 | N/A | N/A | N/A | N/A | -1840.5503 | -1.37 | 1345.2666 | 0.15385 |  | MAE | Contr. Markup |  | Measure | Pkg HP EER = 12.0 (90-134 kBtuh), COP = 3.4 assumed 112 kBtuh capacity | 13286.8057 | 1948.5132 | 813.9252
| (Do not delete these rows; see cells at right) | [16 empty] | 1573.57 | 20%
Residential Water Heating | [42 empty] | Diff (Modeled-Actual) | %Diff (Modeled-Actual)/Actual
Small Storage Gas WH (<= 75,000 BtuH and EF rated) | Energy Factor | Continuous | 0.58-0.7 | 54 | 0.63111 | 0.039029 | 746.58 | 366.44 | Continuous | 0.53 -0.70 | N/A | N/A | 2332.5062 | 2.32 | 1005.1215 | N/A | 2332.5062 | Data Source | Data Type | DEER Measures | Baseline | Small Gas Storage Water Heater 30 Gal; EF = 0.61; Recov Eff = 0.76 | 514.4184 | - | - |  | Model Validation Summary Stats |  | Baseline | Small Gas Storage Water Heater 40 Gal; EF = 0.59; Recov Eff = 0.76 | 565.0488 | 493.95 | 438 | 368.68 | 434 | [6 empty] | 1002
| Rated Volume (gallons) | Continuous | 30-65 | 54 | 43.7222 | 7.3264 | 746.58 | 366.44 | Continuous | 30 - 75 gal | N/A | N/A | 9.0677 | 2.08 | 4.3615 | N/A | 9.0677 | DEG/EMCOR/MESA | Distributor prices |  | Measure | High Efficiency Small Gas Storage Water Heater - 30 Gal , 0.62 EF | 712.5599 | 198.1415 | 10.0512 |  | Mean | #DIV/0! | Measure | High Efficiency Small Gas Storage Water Heater - 40 Gal , 0.62 EF | 816.8379 | 542.95 | 497 | 412.29 | 497
| Forced Draft | Binary | Yes | 17 | N/A | N/A | 1168.55 | 310.6468 | N/A | N/A | N/A | N/A | 473.2047 | 5.17 | 91.4706 | 0.31481 | 148.9719 | Weighting | % CA market |  | Measure | High Efficiency Small Gas Storage Water Heater - 30 Gal , 0.65 EF | 793.0314 | 278.6129 | 40.2049 |  | St. Dev. | #DIV/0! | Measure | High Efficiency Small Gas Storage Water Heater - 40 Gal , 0.67 EF | 950.957 | 795.95 | 924.43 | 1193.51 |  |  |  |  | 649
|  |  | No | 37 | N/A | N/A | 552.7084 | 179.1314 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.68519 |  | CLASS | Unknown |  | Measure | High Efficiency Small Gas Storage Water Heater - 30 Gal , 0.70 EF | 927.1505 | 412.732 | 90.4609 |  | Min | 0 | Measure | High Efficiency Small Gas Storage Water Heater - 40 Gal , 0.70 EF | 1031.4285 | 809.95 |  |  |  | 872.99 |  | 1085
| Manufacturer | Categorical | AO Smith | 2 | N/A | N/A | 442.75 | 16.26 | N/A | N/A | N/A | N/A | -163.9102 | -0.95 | 173.2708 | 0 | 0 | N observations | N unit sales |  | Baseline | Small Gas Storage Water Heater 40 Gal; EF = 0.59; Recov Eff = 0.76 | 565.0488 | - | - |  | Max | 0 | Baseline | Small Gas Storage Water Heater 60 Gal; EF = 0.56; Recov Eff = 0.76 | 693.1333 | 939.95 |  | 810.21 | 728 |  | 754.45 |  |  |  |  | 1428
|  |  | Bradford-White Co. | 8 | N/A | N/A | 529.25 | 210.72 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0 |  | 54 | N/A |  | Measure | High Efficiency Small Gas Storage Water Heater - 40 Gal , 0.62 EF | 816.8379 | 251.7891 | 30.1536 |  |  |  | Baseline | Small Gas Storage Water Heater 75 Gal; EF = 0.53; Recov Eff = 0.76 | 769.0788 |  |  | 742.55 |  |  |  |  | 816.41 | 722.89 | 789.99 | 1512
|  |  | Rheem | 14 | N/A | N/A | 702.04 | 275.46 | N/A | N/A | N/A | N/A | 4.6269 | 0.05 | 100.9471 | 0 |  | R2 | Intercept |  | Measure | High Efficiency Small Gas Storage Water Heater - 40 Gal , 0.67 EF | 950.957 | 385.9082 | 80.4097
|  |  | State Industries | 30 | N/A | N/A | 845.58 | 412.52 | N/A | N/A | N/A | N/A | -33.3115 | -0.35 | 94.7955 | 0 |  | 0.69055 | -1247.5379 |  | Measure | High Efficiency Small Gas Storage Water Heater - 40 Gal , 0.70 EF | 1031.4285 | 466.3797 | 110.5634
| (Do not delete these rows; see cells at right) | [16 empty] | MAE | Contr. Markup |  | Baseline | Small Gas Storage Water Heater 50 Gal; EF = 0.57; Recov Eff = 0.76 | 615.6791 | - | -
[18 empty] | 153.534 | 15% |  | Measure | High Efficiency Small Gas Storage Water Heater - 50 Gal , 0.62 EF | 921.1159 | 305.4367 | 50.2561
[21 empty] | Measure | High Efficiency Small Gas Storage Water Heater - 50 Gal , 0.67 EF | 1055.235 | 439.5559 | 100.5121
[21 empty] | Measure | High Efficiency Small Gas Storage Water Heater - 50 Gal , 0.70 EF | 1135.7064 | 520.0273 | 130.6658
[21 empty] | Baseline | Small Gas Storage Water Heater 60 Gal; EF = 0.56; Recov Eff = 0.76 | 693.1333 | - | -
[21 empty] | Measure | High Efficiency Small Gas Storage Water Heater - 60 Gal , 0.62 EF | 1025.3939 | 332.2606 | 60.3073
[21 empty] | Measure | High Efficiency Small Gas Storage Water Heater - 60 Gal , 0.66 EF | 1132.6891 | 439.5559 | 100.5121
[21 empty] | Measure | High Efficiency Small Gas Storage Water Heater - 60 Gal , 0.70 EF | 1239.9844 | 546.8511 | 140.717
[21 empty] | Baseline | Small Gas Storage Water Heater 75 Gal; EF = 0.53; Recov Eff = 0.76 | 769.0788 | - | -
[21 empty] | Measure | High Efficiency Small Gas Storage Water Heater - 75 Gal , 0.62 EF | 1181.8108 | 412.732 | 90.4609
[21 empty] | Measure | High Efficiency Small Gas Storage Water Heater - 75 Gal , 0.66 EF | 1289.1061 | 520.0273 | 130.6658
[21 empty] | Measure | High Efficiency Small Gas Storage Water Heater - 75 Gal , 0.70 EF | 1396.4014 | 627.3226 | 170.8707
[45 empty] | Diff (Modeled-Actual) | %Diff (Modeled-Actual)/Actual
Electric Storage WH | Energy Factor | Continuous | 0.86-0.95 | 33 | 0.92 | 0.016394 | 427.19 | 188.93 | Continuous | 0.87 - 0.95 | N/A | N/A | 8916.7788 | 5.19 | 1716.4657 | N/A | 8916.7788 | Data Source | Data Type | DEER Measures | Baseline | Small Electric Storage Water Heater 30 Gal; EF = 0.93; Recov Eff = 0.98 | 0 | 0 | 0 |  | Model Validation Summary Stats |  | Baseline | Small Electric Storage Water Heater 30 Gal; EF = 0.93; Recov Eff = 0.98 | 0 | 347 | 248 | 518.04 | 459.49 | [9 empty] | -393.1325 | -1
| Rated Volume | Continuous | 30-80 | 33 | 42.6667 | 12.5864 | 427.19 | 188.93 | Continuous | 30 - 75 gal | N/A | N/A | 14.0859 | 6.7 | 2.1022 | N/A | 14.0859 | DEG/EMCOR | Distributor prices |  | Measure | High Efficiency Small Electric Storage Water Heater - 30 Gal, 0.95 EF | 0 |  |  |  | Mean | #DIV/0! | Measure | High Efficiency Small Electric Storage Water Heater - 30 Gal, 0.95 EF | 0 | [6 empty] | 336.25 | 435.35 | [5 empty] | -385.8 | -1
| Manufacturer | Categorical | A.O. Smith | 7 | N/A | N/A | 375.85 | 67.8 | N/A | N/A | N/A | N/A | 23.9474 | 0.44 | 55.0402 | 0 | 8.7676 | Weighting | % CA market |  | Baseline | Small Electric Storage Water Heater 40 Gal; EF = 0.92; Recov Eff = 0.98 | 0 | 0 | 0 |  | St. Dev. | #DIV/0! | Baseline | Small Electric Storage Water Heater 40 Gal; EF = 0.92; Recov Eff = 0.98 | 0 | 338 | 251.21 | 504.59 | 447.53 | [9 empty] | -385.3325 | -1
|  |  | Bradford-White Co. | 7 | N/A | N/A | 382.73 | 83.27 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0 |  | CLASS | Unknown |  | Measure | High Efficiency Small Electric Storage Water Heater - 40 Gal, 0.94 EF | 0 |  |  |  | Min | 0 | Measure | High Efficiency Small Electric Storage Water Heater - 40 Gal, 0.94 EF | 0 | 799 |  | 847.21 | 751.4 | 995 | [8 empty] | -848.1525 | -1
|  |  | Rheem | 9 | N/A | N/A | 602.93 | 280.51 | N/A | N/A | N/A | N/A | 113.7171 | 2.11 | 53.9492 | 0.0771 |  | N observations | N unit sales |  | Baseline | Small Electric Storage Water Heater 50 Gal; EF = 0.90; Recov Eff = 0.98 | 0 | 0 | 0 |  | Max | 0 | Baseline | Small Electric Storage Water Heater 50 Gal; EF = 0.90; Recov Eff = 0.98 | 0 | 298 | 298 |  |  | 432.95 | 443.95 | [7 empty] | -368.225 | -1
|  |  | State Industries | 10 | N/A | N/A | 336.07 | 74.79 | N/A | N/A | N/A | N/A | -12.29 | -0.24 | 51.7279 | 0 |  | 32 | N/A |  | Measure | High Efficiency Small Electric Storage Water Heater - 50 Gal, 0.93 EF | 0 | [5 empty] | Measure | High Efficiency Small Electric Storage Water Heater - 50 Gal, 0.93 EF | 0 |  | 460.75 |  |  |  | 629.95 | 318.58 | 364.99 | [5 empty] | -443.5675 | -1
| (Do not delete these rows; see cells at right) | [16 empty] | R2 | Intercept |  | Baseline | Small Electric Storage Water Heater 60 Gal; EF = 0.89; Recov Eff = 0.98 | 0 | 0 | 0 |  |  |  | Measure | Electric Storage Water Heater - 66 Gal, .88 EF | 0 |  |  |  |  | 765 | 707.95 | 788.89 | [6 empty] | -753.9467 | -1
[18 empty] | 0.75454 | -8409.6193 |  | Measure | High Efficiency Small Electric Storage Water Heater - 60 Gal, 0.92 EF | 0 | [5 empty] | Measure | Electric Storage Water Heater - 66 Gal, .92 EF | 0 | [5 empty] | 775.95 |  | 629.99 |  |  |  |  | 761.44 | -722.46 | -1
[18 empty] | MAE | Contr. Markup |  | Baseline | Small Electric Storage Water Heater 75 Gal; EF = 0.87; Recov Eff = 0.98 | 0 | 0 | 0
[18 empty] | 71.264 | 15% |  | Measure | High Efficiency Small Electric Storage Water Heater - 75 Gal, 0.91 EF | 0
[45 empty] | Diff (Modeled-Actual) | %Diff (Modeled-Actual)/Actual
Tankless WH | Energy Factor | Continuous | 82 - 92 (.82-.92) | 32 | 87.88 | 4.67 | 916.82 | 226.77 | Discrete | .80, .85, .90 | Discrete | .80, .90 | 13.98 | 2.97 | 4.71 | N/A | 13.98 | Data Source | Data Type | DEER Measures | Baseline | Small Gas Storage Water Heater 40 Gal; EF = 0.59; Recov Eff = 0.76 | 565.0488 | - |  |  | Model Validation Summary Stats |  | Measure | High Efficiency Medium Gas Instantaneous Water heater , 0.82 TE, 120 mbtu/hr | 593.3039 | 549 |  |  |  | 574.4 | 584.99 |  |  |  | 584.99 | [6 empty] | 19.9589 | 0.034811
| Capacity (Mbtu) | Continuous | 120-250 | 32 | 184.99 | 31.84 | 916.82 | 226.77 | N/A | N/A | Discrete | <= 200, > 200 | 5.55 | 8.47 | 0.655 | N/A | 5.55 | QuEST | Distributor prices |  | Measure | High Efficiency Medium Gas Instantaneous Water heater , 0.82 TE, 120 mbtu/hr | 593.3039 | 28.2551 | 57.0059 |  | Mean | 0.011034 | Measure | High Efficiency Medium Gas Instantaneous Water heater, 0.91 TE, 180 mbtu/hr | 1166.8289 |  | 1217.32 | 1124.95 |  |  | 1123.95 | [5 empty] | 1217.32 |  |  |  |  | -4.0561 | -0.0034641
| Rheem | Binary | Yes | 10 | N/A | N/A | 863.7 | 178.16 | N/A | N/A | N/A | N/A | -119.99 | -2.6 | 46.15 | 0.3125 | -37.4969 | Weighting | % CA market |  | Measure | High Efficiency Medium Gas Instantaneous Water heater, 0.91 TE, 180 mbtu/hr | 1166.8289 | 601.7801 | 112.1114 |  | St. Dev. | 0.21823 | Measure | High Efficiency Medium Gas Instantaneous Water heater, 0.93 TE, 150 mbtu/hr | 993.6539 |  | 1356.47 |  |  |  |  | 1356.55 | 1378.61 |  |  |  |  | 1347.46 |  |  |  | -366.1186 | -0.26925
|  |  | No | 22 | N/A | N/A | 940.95 | 245.67 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.6875 |  | None | Unknown |  | Measure | High Efficiency Medium Gas Instantaneous Water heater, 0.93 TE, 150 mbtu/hr | 993.6539 | 428.6051 | 95.4724 |  | Min | -0.26925 | Measure | High Efficiency Large Gas Instantaneous Water heater, 0.82 TE, 200 mbtu/hr | 1148.3039 |  |  |  | 1240.95 |  |  |  | 1115.27 |  |  | 1060.87 |  |  | 1189 |  |  | -3.2186 | -0.0027951
| (Do not delete these rows; see cells at right) | [16 empty] | N observations | N unit sales |  | Baseline | Small Gas Storage Water Heater 75 Gal; EF = 0.53; Recov Eff = 0.76 | 769.0788 | - |  |  | Max | 0.39637 | Measure | High Efficiency Large Gas Instantaneous Water heater, 0.84 TE, 250 mbtu/hr | 1530.1289 |  | 1706.11 |  | 1678.95 |  |  |  |  | 1657.99 | [5 empty] | 1678.88 |  | -150.3536 | -0.08947
[18 empty] | 32 | N/A |  | Measure | High Efficiency Large Gas Instantaneous Water heater, 0.82 TE, 200 mbtu/hr | 1148.3039 | 379.2251 | 110.3315 |  |  |  | Measure | High Efficiency Large Gas Instantaneous Water heater, 0.92 TE, 200 mbtu/hr | 1323.0539 | 945 | 955 | [7 empty] | 989.99 | [5 empty] | 899.98 | 375.5614 | 0.39637
[18 empty] | R2 | Intercept |  | Measure | High Efficiency Large Gas Instantaneous Water heater, 0.84 TE, 250 mbtu/hr | 1530.1289 | 761.0501 | 147.018
[18 empty] | 0.768 | -1300.22 |  | Measure | High Efficiency Large Gas Instantaneous Water heater, 0.92 TE, 200 mbtu/hr | 1323.0539 | 553.9751 | 127.1218
[18 empty] | MAE | Contr. Markup
[18 empty] | 88.09 | 25%
[45 empty] | Diff (Modeled-Actual) | %Diff (Modeled-Actual)/Actual
Heat Pump Water Heaters | Storage Volume (gallons) | Continuous | 40 - 80 | 25 | 59.6 | 13.06 | 1575.36 | 327.67 | N/A | N/A | Continuous | >=40 | 23.23 | 6.47 | 639.71 | N/A | 23.23 | Data Source | Data Type | Example Measures | Baseline | Small Electric Storage Water Heater 40 Gal; EF = 0.92; Recov Eff = 0.98 | #REF! | - | - |  | Model Validation Summary Stats |  | Baseline | 40 gallon electric water heater, .92 EF |  | 1199 | 1139 | 1199 | 1229
| Input KW | Continuous | 2.2 - 5.5 | 25 | 4.43 | 0.626 | 1575.36 | 327.67 | N/A | N/A | N/A | N/A | -230.48 | 3.17 | 72.76 | N/A | -230.48 | DEG/Itron | Retail prices |  | Measure | Heat pump water heater, 40 gallons, 4.0 kw, 2.0 EF, 240 volt | 1761.23 | #REF! | 123.1014 |  | Mean | 0.019668 | Measure | Heat pump water heater, 40 gallons, 4.0 kw, 2.0 EF, 240 volt | 1761.23 |  |  | 1449 | 1599 |  |  |  | 1398 | 1614 | [5 empty] | 246.23 | 0.15741
| Energy Factor | Continuous | 2 - 2.51 | 25 | 2.29 | 0.158 | 1575.36 | 327.67 | N/A | N/A | Continuous | >= 2.0 | -782.21 | 2.52 | 310.08 | N/A | -782.21 | Weighting | % CA market |  | Measure | Heat pump water heater, 50 gallons, 4.5 kw, 2.4 EF, 240 volt | 1565.406 | #REF! | 109.4143 |  | St. Dev. | 0.36138 | Measure | Heat pump water heater, 50 gallons, 4.5 kw, 2.4 EF, 240 volt | 1565.406 |  |  |  |  | 2612 |  |  | 2495 |  | 2399 |  |  |  | 2399 | -910.844 | -0.39704
| Volt 230 | Binary | yes | 22 | N/A | N/A | 1613.64 | 328.68 | N/A | N/A | N/A | N/A | 361.35 | 2.3 | 157.07 | N/A | 361.35 | None | Unknown |  | Measure | Heat pump water heater, 50 gallons, 5.5 kw, 2.45 EF, 230 volt | 1295.8155 | #REF! | 90.5712 |  | Min | -0.39704 | Measure | Heat pump water heater, 50 gallons, 5.5 kw, 2.45 EF, 230 volt | 1295.8155 |  |  |  | 1165 | 1735 | 1219 | 1468 | [7 empty] | -100.9345 | -0.073324
|  |  | no | 3 | N/A | N/A | 1294.67 | 140.43 | N/A | N/A | N/A | N/A | 0 | -- | -- | N/A | 0 | N observations | N unit sales |  | Measure | Heat pump water heater, 60 gallons, 4.5 kw, 2.33 EF, 240 volt | 1852.4607 | #REF! | 129.478 |  | Max | 0.56057 | Measure | Heat pump water heater, 60 gallons, 4.5 kw, 2.33 EF, 240 volt | 1852.4607 |  |  |  | 2279 |  |  |  | 2099 |  |  | 1889 | 2399 |  |  | -314.0393 | -0.14928
| (Do not delete these rows; see cells at right) | [16 empty] | 25 | N/A |  | Measure | Heat pump water heater, 80 gallons, 2.2 kw, 2.51 EF, 240 volt | 2706.3669 | #REF! | 189.1619 |  |  |  | Measure | Heat pump water heater, 80 gallons, 2.2 kw, 2.51 EF, 240 volt | 2706.3669 |  |  |  | 2026 | 1785 | [7 empty] | 1103.89 |  | 1068.0702 | 0.56057
[18 empty] | R2 | Intercept |  | Measure | Heat pump water heater, 80 gallons, 4.5 kw, 2.33 EF, 240 volt | 2317.0607 | #REF! | 161.9513 |  |  |  | Measure | Heat pump water heater, 80 gallons, 4.5 kw, 2.33 EF, 240 volt | 2317.0607
[18 empty] | 0.777 | 2955.87
[18 empty] | MAE | Contr. Markup
[18 empty] | 110.11 | 15%
Non-Residential Water Heating | [42 empty] | Diff (Modeled-Actual) | %Diff (Modeled-Actual)/Actual
Large Storage Gas WH (> 75,000 BtuH and TE rated) | Rated Input (Btuh) | Continuous | 75100-740000 | 65 | 262298.4 | 144055.8 | 6603.16 | 3412.96 | Discrete | > 75,000 Btuh | N/A | N/A | 0.01129 | 8.23 | 0.001371 | N/A | 0.01129 | Data Source | Data Type | DEER Measures | Baseline | Large Gas Storage Water Heater; Et = 0.80; Stdby Loss = 0.56%/hr assumed 75 gal capacity and 125,000 Btuh | 4885.9919 | - | - |  | Model Validation Summary Stats |  | Baseline | Large Gas Storage Water Heater; Et = 0.80; Stdby Loss = 0.56%/hr assumed 75 gal capacity and 125,000 Btuh | 4885.9919 | 3341.77 |  | 3743 |  | 3457.35 |  |  |  |  | 4185 |  |  |  |  | 4250 | 5041 |  |  |  | 882.9719 | 22.06% | 3341.77 | 5041 | 33.71%
| Rated Volume (gallons) | Continuous | 50-130 | 65 | 88.4385 | 19.9817 | 6603.16 | 3412.96 | N/A | N/A | N/A | N/A | 29.923 | 2.77 | 10.7957 | N/A | 29.923 | EMCOR/MESA | Distributor prices |  | Measure | High Efficiency Large Gas Storage Water Heater - 0.83 Et assumed 75 gal capacity and 125,000 Btuh | 5105.9552 | 219.9632 | 86.339 |  | Mean | 0.19728 | Measure | High Efficiency Large Gas Storage Water Heater - 0.95 Et assumed 55 gal capacity and 100,000 Btuh | 5661.2207 | 4689.15 | 3458.31 |  |  |  | 5482.53 | 4016.71 | [12 empty] | 1249.5457 | 28.32% | 3458.31 | 5482.53 | 36.92%
| Thermal Efficiency | Continuous | 0.79-0.99 | 65 | 0.84257 | 0.066915 | 6603.16 | 3412.96 | Continuous | 0.8 - 0.9 | N/A | N/A | 11362.9197 | 3.95 | 2877.9659 | N/A | 11362.9197 | Weighting | % CA market |  | Measure | High Efficiency Large Gas Storage Water Heater - 0.90 Et assumed 75 gal capacity and 125,000 Btuh | 6020.6702 | 1134.6783 | 287.7966 |  | St. Dev. | 0.1513 | Measure | High Efficiency Large Gas Storage Water Heater - 0.92 Et assumed 100 gal capacity and 400,000 Btuh | 10712.7672 | 9235 | [5 empty] | 8572 | 5579 | 9181.76 | 11264 |  | 9959 | 8246 | 11058 | [5 empty] | 1575.9222 | 17.25% | 5579 | 11264 | 50.47%
| ASME Construction | Binary | Yes | 25 | N/A | N/A | 8471.53 | 2967.61 | N/A | N/A | N/A | N/A | 945.4884 | 2.55 | 370.6015 | 0.38462 | 363.6494 | None | Unknown | [7 empty] | Min | -0.037861 | Measure | High Efficiency Large Gas Storage Water Heater - 0.96 Et assumed 130 gal capacity and 300,000 Btuh | 10969.4564 |  |  | 10510 | 9579.95 |  | 11921.94 | 8374.77 | [9 empty] | 12062 |  |  | 479.7244 | 4.573% | 8374.77 | 12062 | 30.57%
|  |  | No | 40 | N/A | N/A | 5435.43 | 3171.64 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.61538 |  | N observations | N unit sales | [7 empty] | Max | 0.39774 | Measure | High Efficiency Large Gas Storage Water Heater - 0.82 Et assumed 100 gal capacity and 199,900 Btuh | 6808.0331 | 4595.07 | 3730.59 |  |  |  |  | 5236 |  |  | 4100 | [7 empty] | 6692 |  | 1937.3011 | 39.77% | 3730.59 | 6692 | 44.25%
| Supplier | Categorical | Cal Steam | 44 | N/A | N/A | 8233.98 | 2607.07 | N/A | N/A | N/A | N/A | 3778.6696 | 2.58 | 1464.4516 | 0.67692 | 2564.9649 | 65 | N/A | [9 empty] | Measure | High Efficiency Large Gas Storage Water Heater - 0.94 Et assumed 80 gal capacity and 150,000 Btuh | 7040.0095 |  |  |  |  | 4297 |  | 5105 |  | 4576.69 |  |  |  | 6017 | [5 empty] | 7101 | 1620.6715 | 29.91% | 4297 | 7101 | 39.49%
|  |  | Pace Supply | 5 | N/A | N/A | 1300.83 | 593.36 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.076923 |  | R2 | Intercept | [9 empty] | Measure | High Efficiency Large Gas Storage Water Heater - 0.80 Et 100 gal capacity and 199,900 Btuh | 6546.686 | 7511 |  | 7155 |  | 5536.11 | 6963 |  |  |  | 5620 | 6935 |  | 7910 | [6 empty] | -257.6154 | -3.786% | 5536.11 | 7910 | 30.01%
|  |  | Heieck Supply | 1 | N/A | N/A | 2032.19 | . | N/A | N/A | N/A | N/A | 0 | -- | -- | 0.015385 |  | 0.87611 | -11575.3546
|  |  | Ferguson Plumbing Supply | 15 | N/A | N/A | 3891.6 | 2122.03 | N/A | N/A | N/A | N/A | 30.7504 | 0.02 | 1473.0272 | 0.23077 |  | MAE | Contr. Markup
| Manufacturer | Categorical | AO Smith | 60 | N/A | N/A | 7045.02 | 3167.08 | N/A | N/A | N/A | N/A | 74.073 | 0.05 | 1407.2883 | 0 | 0 | 862.791 | 15%
|  |  | State Industries | 5 | N/A | N/A | 1300.83 | 593.36 | N/A | N/A | N/A | N/A | 0 | -- | -- | 0
(Do not delete these rows; see cells at right)
Lighting - Controls
Occupancy Sensors | Coverage (ft2) | Continuous | 90 - 2,152 | 40 | 1062 | 579 | 109.35 | 59.31 | Discrete | 200, 1000 | Discrete | 200, 1000 | -0.002 | 0.36 | 0.006 | N/A | 0.006 | Data Source | Data Type | DEER Measures | Baseline | Absence of occupancy sensor, manually controlled switch | 0 | - | - |  | Model Validation Summary Stats |  | Measure | Occupancy sensor (300 sqft) assumed ceiling mount, passive infrared, indoor, 24v | 87.3625 |  |  | 61.67 | 67.84 | 76.31 | [8 empty] | 18.7558 | 0.27338
| Battery Powered | Binary | Yes | 2 | N/A | N/A | 56.88 | 9.72 | N/A | N/A | N/A | N/A | -60.55 | 3.35 | 18.07 | 0.05 | -3.0275 | DEG, QuEST | Distributor Prices |  | Measure | Occupancy sensor (300 sqft) assumed ceiling mount, passive infrared, indoor, 24v | 87.3625 | 87.3625 | 9.8348 |  | Mean | 0 | Measure | Occupancy sensor (1000 sqft) assumed ceiling mount, passive infrared & ultrasonic, indoor, 120v | 164.3875 |  |  |  | 128.33 | 157.79 |  |  |  |  | 134.29 |  |  |  | 24.2508 | 0.17305
|  |  | No | 38 | N/A | N/A | 112.11 | 59.57 | N/A | N/A | N/A | N/A | 0 |  |  | 0.95 |  | Weighting | % CA market |  | Measure | Occupancy sensor (1000 sqft) assumed ceiling mount, passive infrared & ultrasonic, indoor, 120v | 164.3875 | 164.3875 | 18.5058 |  | St. Dev. | 0.107 | Measure | Occupancy sensor (2000 sqft) ceiling mount, passive infrared, outdoor 24v | 323.7125 | 285.54 | 174 | [8 empty] | 189 | 212.06 | 134 | 124.7925 | 0.62735
| Solar Powered | Binary | Yes | 1 | N/A | N/A | 166.69 | N/A | N/A | N/A | N/A | N/A | 49.27 | 2.21 | 22.33 | 0.025 | 1.2318 | None | Unknown | Example Measures | Measure | Occupancy sensor (2000 sqft) ceiling mount, passive infrared, outdoor, 24v | 323.7125 | 323.7125 | 36.4417 |  | Min | -0.104 | Measure | Occupancy sensor (1000 sqft) wall mount, passive infrared & ultrasonic, indoor, 120v | 164.3875 | [5 empty] | 72.2 | 78.57 | 104 | 146 |  |  |  | 119 | 60.4335 | 0.58135
|  |  | No | 39 | N/A | N/A | 107.88 | 59.34 | N/A | N/A | N/A | N/A | 0 |  |  | 0.975 |  | N observations | N unit sales |  | Measure | Occupancy sensor (1000 sqft) wall mount, passive infrared & ultrasonic, indoor, 120v | 164.3875 | 164.3875 | 18.5058 |  | Max | 0.147
| Outdoor | Binary | Yes | 3 | N/A | N/A | 246.97 | 0 | N/A | N/A | N/A | N/A | 178.88 | 14.08 | 12.71 | 0.075 | 13.416 | 40 | N/A
|  |  | No | 37 | N/A | N/A | 98.19 | 45.88 | N/A | N/A | N/A | N/A | 0 |  |  | 0.925 |  | R2 | Intercept
| Two Loads | Binary | Yes | 2 | N/A | N/A | 197.29 | 0 | N/A | N/A | N/A | N/A | 101.15 | 5.91 | 17.13 | 0.05 | 5.0575 | 0.927 | 117.42
|  |  | No | 38 | N/A | N/A | 104.72 | 57.17 | N/A | N/A | N/A | N/A | 0 |  |  | 0.95 |  | MAE | Contr. Markup
| Ultrasonic | Binary | Yes | 15 | N/A | N/A | 136.07 | 40.41 | N/A | N/A | N/A | N/A | 42.36 | 5.14 | 8.24 | 0.375 | 15.885 | 12.31 | 25%
|  |  | No | 25 | N/A | N/A | 93.32 | 63.65 | N/A | N/A | N/A | N/A | 0 |  |  | 0.625
| 12 volt | Binary | Yes | 1 | N/A | N/A | 67.89 | N/A | N/A | N/A | N/A | N/A | -49.53 | 2.22 | 22.33 | 0.025 | -1.2383
|  |  | No | 39 | N/A | N/A | 110.41 | 59.7 | N/A | N/A | N/A | N/A | 0 |  |  | 0.975
| 18 volt | Binary | Yes | 3 | N/A | N/A | 144.78 | 41.79 | N/A | N/A | N/A | N/A | 48.54 | 4.1 | 11.83 | 0.075 | 3.6405
|  |  | No | 37 | N/A | N/A | 106.48 | 60.01 | N/A | N/A | N/A | N/A | 0 |  |  | 0.925
| 24 volt | Binary | Yes | 20 | N/A | N/A | 123.37 | 62.27 | N/A | N/A | N/A | N/A | -49.33 | 4.15 | 11.88 | 0.5 | -24.665
|  |  | No | 20 | N/A | N/A | 95.34 | 54.13 | N/A | N/A | N/A | N/A | 0 |  |  | 0.5
| 120 volt | Binary | Yes | 12 | N/A | N/A | 88.56 | 55.65 | N/A | N/A | N/A | N/A | -34.27 | 3 | 11.42 | 0.3 | -10.281
|  |  | No | 28 | N/A | N/A | 118.26 | 59.54 | N/A | N/A | N/A | N/A | 0 |  |  | 0.7
| 277 volt | Binary | Yes | 11 | N/A | N/A | 86.1 | 57.68 | N/A | N/A | N/A | N/A | -29.37 | 2.56 | 11.46 | 0.275 | -8.0768
|  |  | No | 29 | N/A | N/A | 118.17 | 58.47 | N/A | N/A | N/A | N/A | 0 |  |  | 0.725
(Do not delete this row; see cells at right)
Note on AA5: Lucas Scheidler: =s.e.*(kWh_baseline - kWh_measure)
Note on AD5: Lucas Scheidler: Descriptive stats are on percentage difference between modeled and actual prices ((Modeled - Actual)/Actual)
Note on AD28: Jeremy Eddy: Descriptive stats are on percentage difference between modeled and actual prices ((Modeled - Actual)/Actual)
Note on AD56: Jeremy Eddy: Descriptive stats are on percentage difference between modeled and actual prices ((Modeled - Actual)/Actual)
Note on AD96: Lucas Scheidler: Descriptive stats are on percentage difference between modeled and actual prices ((Modeled - Actual)/Actual)
Note on V113: Mike Ting: No product specs specified in DEER or WPs
Note on AD113: Lucas Scheidler: Descriptive stats are on percentage difference between modeled and actual prices ((Modeled - Actual)/Actual)
Note on AN113: Phillip Kelsven: http://www.hvacquick.com
Note on AO113: Phillip Kelsven: http://www.ventmasters.com
Note on AP113: Phillip Kelsven: http://wholehousefanman.com
Note on AI114: Phillip Kelsven: http://www.amazon.com
Note on AJ114: Phillip Kelsven: http://www.rewci.com
Note on AK114: Phillip Kelsven: http://www.wholehousefansdirect.com
Note on AL114: Phillip Kelsven: http://www.homeperfect.com
Note on AM116: Phillip Kelsven: http://www.h-mac.com
Note on T122: Mike Ting: placeholder value; DEG still developing markup estimate
Note on AM123: Lucas Scheidler: http://heatingandairwholesale.com
Note on AN123: Lucas Scheidler: http://www.theacoutlet.com
Note on AO123: Lucas Scheidler: http://www.routeac.com
Note on AP123: Lucas Scheidler: http://www.ecoairandwater.com
Note on AQ123: Lucas Scheidler: https://www.acwholesalers.com
Note on AR123: Lucas Scheidler: http://welcomehvac.com
Note on AS123: Lucas Scheidler: http://acunitsdirect.com
Note on AT123: Lucas Scheidler: http://shortyshvac.com
Note on AD124: Lucas Scheidler: Descriptive stats are on percentage difference between modeled and actual prices ((Modeled - Actual)/Actual)
Note on AI124: Lucas Scheidler: http://www.alpinehomeair.com/viewproduct.cfm?productID=453064740 Goodman GDS80603AX
Note on AJ124: Lucas Scheidler: http://ecomfort.com/gds80603ax-multi-speed-gas-furnace-downflow-low-nox-80-afue-60000-btu-37134.html
Note on AU124: Lucas Scheidler: http://shop.thefurnaceoutlet.com/60000-BTU-80-Downflow-Furnace-GDS80603AX.htm
Note on AZ124: Lucas Scheidler: http://www.aclinesets.com/products/gds80603ax-80-afue-multi-speed-downflow-gas-furnace-60-000-btu-low-nox
Note on AM125: Lucas Scheidler: http://heatingandairwholesale.com/payne-90-afue-gas-furnace-60000-btu-psc-motor-2/
Note on AO125: Lucas Scheidler: http://www.routeac.com/payne-2-ton-gas-furnace-90-afue-60k-btu-multipoise.html
Note on AS125: Lucas Scheidler: http://acunitsdirect.com/pg9mab024060-payne-upflow-downflow-horizontal-2-to-2-5-ton-multipoise-60k-btu-90-afue-gas-furnace.html
Note on BA125: Lucas Scheidler: http://www.ductlessairunit.com/pg9mab024060-payne-upflow-downflow-horizontal-2-to-2.5-ton-multipoise-60k-btu-90-afue-gas-furnace.html
Note on AK126: Dawdy, John: http://ingramswaterandair.com/goodman-furnace-gmh80903bna-upflow-p-17145.html
Note on AM126: Dawdy, John: http://heatingandairwholesale.com/hvac-direct-gas-furnace-gmh80903bna-80-90k-btu-upflow/
Note on AP126: Dawdy, John: http://www.ecoairandwater.com/store/90000-btu-gmh80903bna-80-efficiency-2-stage-3-ton-multi-speed-goodman-upflow-or-horizontal-flow-furnace.html
Note on BB126: Dawdy, John: http://www.alloysafe.com/index.php/heating-air-conditioning/gas-furnaces/80-afue-gas-furnace/goodman-gas-furnace-gmh80903bna-80-90k-btu-upflow.html
Note on AJ127: Lucas Scheidler: http://ecomfort.com/gks90904cx-multi-speed-gas-furnace-upflow-low-nox-921-afue-92000-btu-37076.html
Note on AL127: Lucas Scheidler: http://www.pexsupply.com/Goodman-GKS90904CX-Goodman-90000-BTU-921-Efficiency-Single-Stage-Burner-Multi-Speed-Blower-Upflow-Application-Gas-Furnace-12595000-p
Note on AN127: Lucas Scheidler: http://www.theacoutlet.com/GKS90904CX-90000-Btu-92-Percent-Afue-Goodman-Gas-Furnace.htm?gclid=CNj1saeDg7gCFaN7Qgodg3UACw
Note on AV127: Lucas Scheidler: http://www.greendroplet.com/goodman-gks90904cx-gas-furnace-upflow-horizontal-single-stage-burner-93-90-000-btu.html
Note on Q128: Lucas Scheidler: These weights are from 2006 - 2012 CLASS. Weights are the following: Bryant 13.39%, Day&*Night 1.46%, Goodman 6.05% and Ruud 5.13%. Only weights for day and night and goodman were applied, as these were the only brands in the model that had a significant/marginally significant coefficient.
Note on AI128: Dawdy, John: http://www.alpinehomeair.com/viewproduct.cfm?productID=453064684
Note on AJ128: Dawdy, John: http://ecomfort.com/gmh81205dn-2-stage-multi-speed-gas-furnace-upflow-horizontal-high-air-flow-80-afue-120000-btu-37107.html
Note on AK128: Dawdy, John: http://ingramswaterandair.com/goodman-furnace-gmh81205dn-afue-120k-upflowhorizontal-stage-multispeed-p-18563.html
Note on BC128: Dawdy, John: http://www.godirectappliance.com/ac-heat/gas-furnaces/goodman-120-000-btu-80-multi-position-gas-furnace-gmh81205dn.html
Note on AK129: Dawdy, John: http://ingramswaterandair.com/rheem-furnaces-120k-afue-upflow-p-16375.html
Note on AQ129: Dawdy, John: https://www.acwholesalers.com/Rheem/RGRA12ERAJS-93-5-AFUE-120000-BTU-Upflow-Gas-Furnace-Classic-Series/19956.ac?gclid=CPTej736hLgCFUlxQgod0BcARw
Note on AW129: Dawdy, John: https://www.expresshvac.com/res_components/gas_furnace/hvac_rheem.asp
Note on BD129: Dawdy, John: http://www.nationalairwarehouse.com/gas-systems/furnaces/rheem-93-5-afue-120-000-btu-upflow-gas-furnace.html
Note on AK130: Dawdy, John: http://ingramswaterandair.com/payne-afue-furnace-deluxe-multipoise-88000-motor-p-18263.html
Note on AO130: Dawdy, John: http://www.routeac.com/payne-3.5-ton-gas-furnace-80-afue-88k-btu-multipoise.html
Note on AR130: Dawdy, John: http://welcomehvac.com/shop/article_PG8MAA042090/Payne-Upflow_Downflow_Horizontal-3-1_2-Ton-Multi-Positional-90K-BTU-80%25-AFUE-Gas-Furnace.html?sessid=15rWwz6oRD6EbsKslzgJMrWfw7YWg4e5Oj0QSiI8caB0Et4ZAGWPEE00qcOPwnwn&shop_param=cid%3D255%26aid%3DPG8MAA042090%26
Note on AT130: Dawdy, John: http://shortyshvac.com/index.php?main_page=product_info&products_id=202
Note on AI131: Lucas Scheidler: http://www.alpinehomeair.com/viewproduct.cfm?productID=453063474
Note on AJ131: Lucas Scheidler: http://ecomfort.com/gcvc950915dx-2-stage-variable-speed-gas-furnace-comfortnet-controls-downflow-horizontal-low-nox-95-afue-92000-btu-37054.html
Note on AX131: Lucas Scheidler: http://www.amanadealer.com/product.sc?productId=279
Note on BE131: Lucas Scheidler: http://libertywholesalesupply.com/goodman-gcvc950915dx-92-000-btu-gas-furnace-95-efficient-two-stage-burner-down-flow-direct-drive-variable-speed-ecm-blower.html
Note on AI132: Dawdy, John: http://www.alpinehomeair.com/viewproduct.cfm?productID=453064683
Note on AL132: Dawdy, John: http://www.pexsupply.com/Goodman-GMH81005CN-Goodman-100000-BTU-80-Efficiency-Two-Stage-Burner-Multi-Speed-Blower-Upflow-Horizontal-Application-Gas-Furnace
Note on AM132: Dawdy, John: http://heatingandairwholesale.com/goodman-gas-furnace-gmh81005cn-80-afue-100k-btu-upflowhorizontal-2-stage-multi-speed-gas/
Note on BF132: Dawdy, John: http://www.budgetheating.com/80-Single-Stage-100K-BTU-Gas-Furnace-up-to-5-Ton-p/90004.htm
Note on AJ133: Dawdy, John: http://ecomfort.com/amvm961005dx-dual-stage-variable-speed-gas-furnace-96-100000-btu-40627.html
Note on AN133: Dawdy, John: https://www.theacoutlet.com/AMVM961005DX-100000-Btu-96-Percent-Afue-Amana-Modulating-Gas-Furnace.htm
Note on AY133: Dawdy, John: http://acforsale.com/index.php?dispatch=products.view&product_id=29929
Note on BG133: Dawdy, John: http://www.djsonline.com/amana_amvm96furnaces.htm
Note on AI136: Lucas Scheidler: EMCOR artificial bid
Note on AJ136: Lucas Scheidler: DEER 2001 Update average of 3 ton, 12 SEER and 3 ton, 13 SEER
Note on AK137: Lucas Scheidler: DEER 2008 13 SEER(11.07 EER)/8.1 HSPF(3.28 COP) A/C Heat pump (Code Case)
Note on Q138: Lucas Scheidler: These weights are from CMST. These four brands made up 43% of total record counts in CMST. Cross checking with CSS provided similar weighting.
Note on AK138: Lucas Scheidler: DEER 2008 14 SEER(12.19 EER)/8.6 HSPF(3.52 COP) A/C Heat Pump
Note on AL138: Lucas Scheidler: Workpaper SCE13HC019.0 for 14 SEER (12.19EER) HP - referencing 2005 DEER
Note on AK139: Lucas Scheidler: DEER2008 15 SEER(12.70 EER)/8.8 HSPF(3.74 COP) A/C Heat Pump
Note on AL139: Lucas Scheidler: Workpaper SCE13HC019.0 for 15 SEER (12.5 EER) HP - extrapolating from 2005 DEER
Note on AK140: Lucas Scheidler: DEER2008 16 SEER (12.06 EER) / 8.4 HSPF (3.48 COP) A/C Heat Pump
Note on B142: Lucas Scheidler: HSPF and EER,are colinear with SEER. Heating capacity is also colinear with cooling capacity.
Note on T145: Lucas Scheidler: contractor markup estimate from EMCOR
Note on AI155: Lucas Scheidler: EMCOR artificial bid
Note on AJ155: Lucas Scheidler: DEER 2001 Update average of 3 ton, 12 SEER and 3 ton, 13 SEER
Note on AJ156: Lucas Scheidler: DEER2001 update 3 ton, 13 SEER
Note on AK156: Lucas Scheidler: DEER2008 3 ton 13 SEER(11.09 EER) Split System Air Conditioner (Code Case)
Note on AJ157: Lucas Scheidler: DEER2001 update 3 ton, 14+ SEER
Note on AK157: Lucas Scheidler: DEER2008 3 ton 14 SEER(12.15 EER) Split-System Air Conditioner
Note on AK158: Lucas Scheidler: DEER2008 3 ton 15 SEER(12.72 EER) Split-System Air Conditioner
Note on AK159: Lucas Scheidler: DEER2008 3 ton 16 SEER (11.61 EER) Split System Air Conditioner
Note on AK160: Lucas Scheidler: DEER2008 3 ton, 17 SEER (12.28 EER) Split-System Air Conditioner
Note on AK161: Lucas Scheidler: DEER2008 3 ton 18 SEER (13.37 EER) Split-System Air Conditioner
Note on AK162: Lucas Scheidler: DEER2008 3 ton 19 SEER Split-System Air Conditioner
Note on AK163: Lucas Scheidler: DEER2008 3 ton 20 SEER Split-System Air Conditioner
Note on T164: Lucas Scheidler: contractor markup estimate from EMCOR
Note on AK164: Lucas Scheidler: DEER2008 3 ton 21 SEER Split-System Air Conditioner
Note on AD174: Lucas Scheidler: Descriptive stats are on percentage difference between modeled and actual prices ((Modeled - Actual)/Actual)
Note on AI174: Lucas Scheidler: Workpaper SCE13HC028.0 - average of online distributors
Note on AJ174: Lucas Scheidler: http://www.pexsupply.com/Rheem-51-102500-01-1-2-HP-1075-RPM-4-Speed-Motor-120V
Note on AK174: Lucas Scheidler: http://www.pexsupply.com/Rheem-51-22858-01-1-2-HP-1075-RPM-3-Speed-Motor-120V
Note on AL174: Lucas Scheidler: http://www.pexsupply.com/Rheem-51-23102-08-1-2-HP-825-RPM-Motor-208-230V
Note on AM174: Lucas Scheidler: http://www.pexsupply.com/Rheem-51-23609-04-1-2-HP-1075-RPM-CCW-Motor-208-230V
Note on AN174: Lucas Scheidler: http://www.pexsupply.com/Rheem-51-23679-01-1-2-HP-1075-RPM-Motor-208-230V
Note on AO174: Lucas Scheidler: http://www.grainger.com/Grainger/DAYTON-Direct-Drive-Blower-Motor-3M714?Pid=search
Note on AI175: Lucas Scheidler: Workpaper SCE13HC028.0 - provided by one distributor for EFI Concept 3 brushless fan motor.
Note on AJ175: Lucas Scheidler: http://www.pexsupply.com/Rheem-51-24374-05-1-2-HP-Variable-Speed-ECM-Motor
Note on AK175: Lucas Scheidler: http://www.northamericahvac.com/servlet/the-9279/OEM-GE-Carrier-Bryant/Detail?gclid=CPat_qzSsLoCFco9Qgod9w0AKw
Note on AL175: Lucas Scheidler: http://www.grainger.com/Grainger/DAYTON-ECM-DirectDrive-Motor-43Y137?Pid=search
Note on AD189: Lucas Scheidler: Descriptive stats are on percentage difference between modeled and actual prices ((Modeled - Actual)/Actual)
Note on AI189: Mike Ting: http://www.procureline.net
Note on AJ189: Mike Ting: http://www.partsguy.com
Note on AK189: Mike Ting: http://www.galco.com
Note on AL189: Mike Ting: http://www.apexcontrols.com
Note on AA190: Mike Ting: = (MAE/sample mean) * predicted measure cost
Note on T198: Mike Ting: placeholder value; EMCOR still developing markup estimate
Note on AI200: Mike Ting: http://www.procureline.net
Note on AJ200: Mike Ting: http://www.partsguy.com
Note on AK200: Mike Ting: http://www.galco.com
Note on AL200: Mike Ting: http://www.apexcontrols.com
Note on AA201: Mike Ting: = (MAE/sample mean) * predicted measure cost
Note on T209: Mike Ting: placeholder value; EMCOR still developing markup estimate
Note on AI211: Lucas Scheidler: DEER 2001 Update 2 ton 13 SEER
Note on AJ211: Lucas Scheidler: DEER 2008 average of single and three phase package A/C 13 SEER $/ton airAC-Pkg-lt65kBtuh1phs-13p0seer airAC-Pkg-lt65kBtuh3phs-13p0seer
Note on AK211: Lucas Scheidler: RS Means Online for 2 ton unit. No efficiency information given.
Note on AL211: Lucas Scheidler: DEER 2005 13 SEER packaged ac $/ton
Note on X212: Lucas Scheidler: Modified SEER for this measure from 13 to 14 based on a conversation with Kevin Madison on 7/30/13
Note on AG212: Lucas Scheidler: Modified SEER for this measure from 13 to 14 based on a conversation with Kevin Madison on 7/30/13
Note on AI212: Lucas Scheidler: DEER 2001 Update 2 ton 14+ SEER
Note on AJ212: Lucas Scheidler: DEER 2008 14 SEER package AC airAC-Pkg-lt65kBtuh1phs-14p0seer
Note on AL212: Lucas Scheidler: DEER 2005 14 SEER $/ton
Note on AI213: Lucas Scheidler: DEER 2001 Update 5 ton 13 SEER
Note on AJ213: Lucas Scheidler: DEER 2008 average of single and three phase package A/C 13 SEER $/ton airAC-Pkg-lt65kBtuh1phs-13p0seer airAC-Pkg-lt65kBtuh3phs-13p0seer
Note on AK213: Lucas Scheidler: RS Means Online for 5 ton unit. No efficiency information given.
Note on AL213: Lucas Scheidler: DEER 2005 13 SEER packaged ac $/ton
Note on AI214: Lucas Scheidler: DEER 2001 Update 5 ton 14+ SEER
Note on AJ214: Lucas Scheidler: DEER 2008 14 SEER package AC airAC-Pkg-lt65kBtuh1phs-14p0seer
Note on AL214: Lucas Scheidler: DEER 2005 14 SEER $/ton
Note on Q217: Lucas Scheidler: These weights are from CMST. These three brands made up 51% of total record counts in CMST. Cross checking with CSS provided similar weighting. Of these brands, Carrier had the biggest market share in CMST (32%), but the weighting here has been adjusted to zero because the coefficient is not statistically significant for this brand.
Note on T220: Lucas Scheidler: placeholder until we get contractor markups from EMCOR
Note on AI224: Lucas Scheidler: EMCOR artifical bid
Note on AJ224: Lucas Scheidler: DEER 2001 for Pkg AC 10.5 EER @ $709/ton
Note on AK224: Lucas Scheidler: DEER 2005 for 239k btuh 10.8 EER Pkg AC at $785.77/ton
Note on AL224: Lucas Scheidler: 2008 DEER for 240-759 kbtuh 10.8 EER pkg AC @ $765.86/ton
Note on AM224: Lucas Scheidler: RSMeans Online for 20 ton air cooled - no efficiency provided
Note on Z225: Lucas Scheidler: Incremental costs of $0 for this measure results from DEER measure definitions from READI having the same efficiency rating. Kevin Madison indicated in a call on 7/30/13 that these measure definitions need revision.
Note on AI225: Lucas Scheidler: EMCOR Artificial Bid
Note on AK225: Lucas Scheidler: DEER 2005 for > 760,000 k btuh 10 EER @ $555.15/ton
Note on AL225: Lucas Scheidler: DEER 2008 for > 760 kBtuh 10 EER pkg AC @ $ $663.09/ton
Note on AM225: Lucas Scheidler: RSMeans Online for 7 0 ton air cooled - no efficiency provided
Note on T233: Lucas Scheidler: based on contractor markups from EMCOR
Note on Y245: Lucas Scheidler: EMCOR indicated this is not a technology that is used in the market
Note on Y246: Lucas Scheidler: EMCOR indicated this is not a technology that is used in the market
Note on AJ246: Lucas Scheidler: DEER 2005 1.008 kW/ton air cooled screw chiller @$488/ton
Note on AK246: Lucas Scheidler: DEER 2008 Chlr-AirScrew-AllSizes-1p008kwpton @ $552.09/ton
Note on AI247: Lucas Scheidler: EMCOR artificial bid. 100 ton air cooled unit. Efficiency and technology type not provided.
Note on AL249: Lucas Scheidler: RS Means Online - no efficiecny procided
Note on Q250: Lucas Scheidler: These weights are from CEUS for air cooled chillers. CEUS weights were also benchmarked to CSS. Brand weights from the two studies are similar, but given the smaller sample size for CSS and no differentiantion between air cooled and water cooled units in the data, CEUS weights were applied.
Note on AL251: Lucas Scheidler: RS Means Online - no efficiecny procided
Note on T254: Lucas Scheidler: placeholder until we get contractor markups from EMCOR
Note on AL268: Lucas Scheidler: DEER 2008 Chlr-Cent-150to299tons-0p507kwpton-ConstSpd @$591.08/ton
Note on AI269: Lucas Scheidler: EMCOR artificial bid - no efficiency or technology type provided
Note on AJ269: Lucas Scheidler: DEER 2001 300 ton 0.54 kw/ton @$337/ton
Note on AJ270: Lucas Scheidler: DEER 2001 300 ton 0.47 kw/ton @$353/ton
Note on AL270: Lucas Scheidler: DEER 2008 Chlr-Cent-gte300tons-0p461kwpton-ConstSpd @ $279.01/ton
Note on AI271: Lucas Scheidler: EMCOR artificial bid - no efficiency or technology type provided
Note on AL272: Lucas Scheidler: DEER 2008 Chlr-Cent-lt150tons-0p560kwpton-ConstSpd @ $670.26
Note on AK273: Lucas Scheidler: DEER 2005 same efficiency @$347/ton
Note on AL273: Lucas Scheidler: DEER 2008 Chlr-Screw-150to299tons-0p718kwpton @$361.01/ton
Note on AM273: Lucas Scheidler: RS Means Online - average of 200 and 250 ton unit - no efficieny provided
Note on AN273: Lucas Scheidler: Workpaper SCE13HC043 @ $363.24/ton
Note on AK274: Lucas Scheidler: DEER 2005 same efficiency @$372/ton
Note on AL274: Lucas Scheidler: DEER 2008 Chlr-Screw-150to299tons-0p574kwpton @ $431.02/ton
Note on AI275: Lucas Scheidler: EMCOR artificial bid - no efficiency or technology type provided
Note on AL275: Lucas Scheidler: DEER 2008 Chlr-Screw-gte300tons-0p639kwpton @$293.32/ton
Note on AM275: Lucas Scheidler: RS Means Online - no efficiency procided
Note on AN275: Lucas Scheidler: Workpaper SCE13HC043 @ $288.81/ton
Note on T276: Lucas Scheidler: markup from EMCOR
Note on AL276: Lucas Scheidler: DEER 2008 Chlr-Screw-gte300tons-0p511kwpton @ $341.32/ton
Note on AI277: Lucas Scheidler: EMCOR artificial bid - no efficiency or technology type provided
Note on AK277: Lucas Scheidler: DEER 2005 same efficiency @$443/ton
Note on AL277: Lucas Scheidler: DEER 2008 Chlr-Screw-lt150tons-0p790kwpton @ $475.38 / ton
Note on AM277: Lucas Scheidler: RS Means Online - no efficiency procided
Note on AN277: Lucas Scheidler: Workpaper SCE13HC043 @ $454.88/ton
Note on AK278: Lucas Scheidler: DEER 2005 same efficiency @$492/ton
Note on AL278: Lucas Scheidler: DEER 2008 Chlr-Screw-lt150tons-0p632kwpton @ $ 603.51/ton
Note on A280: Lucas Scheidler: Workpapers indicate there are no centrifugal VSD chillers < 150 tons in the market. Our research confirms this. Additionally, our subcontractors found very few (4) units less than 300 tons. Given the small sample size, a regression model could only be developed for units >= 300 tons.
Note on AI280: Lucas Scheidler: 2005 DEER 0.576 kw/ton @$290/ton
Note on AI281: Lucas Scheidler: 2005 DEER 0.461 kw/ton @$373/ton
Note on AJ281: Lucas Scheidler: 2008 DEER Chlr-Cent-gte300tons-0p461kwpton-VSD @ $475.46/ton
Note on Q282: Lucas Scheidler: These weights are from CEUS for water cooled chillers. CEUS weights were also benchmarked to CSS. Brand weights from the two studies are similar, but given the smaller sample size for CSS and no differentiantion between air cooled and water cooled units in the data, CEUS weights were applied.
Note on T289: Lucas Scheidler: markups from EMCOR
Note on AI291: Lucas Scheidler: DEER 2001 for 5 ton 12.7 SEER
Note on AJ291: Lucas Scheidler: DEER 2005 13 SEER / 7.7 HSPF three phase package A/C Heat Pump @$959/ton
Note on AJ292: Lucas Scheidler: DEER 2005 14 SEER(12.19 EER)/8.6 HSPF(3.52 COP) Package A/C Heat Pump @$995/ton
Note on Q293: Lucas Scheidler: These weights are from CMST. These four brands made up 40% of total record counts in CMST. Cross checking with CSS provided similar weighting.
Note on T300: Lucas Scheidler: placeholder until we get contractor markups from EMCOR
Note on AH302: Lucas Scheidler: Products meeting this description in the cost data set range from approximately $4000 to $8600 before contractor markup
Note on AI302: Lucas Scheidler: Emcor artifical bid
Note on AJ303: Lucas Scheidler: DEER 2001 10 ton 10.9 EER
Note on AJ304: Lucas Scheidler: DEER 2001 15 ton 10.5 EER
Note on AL304: Lucas Scheidler: DEER 2008 15 ton EER 10.8
Note on S305: Lucas Scheidler: CMST and CSS weights are available for large pkg heat pump. However, the brand information was not consistently available in the raw data for our model. One distributor, pacific coast trane, likely only sells Trane equipment. Trane has a market share of 13.45% in CMST. However, because the coefficient on the brand for Pacific coast trane is not significant, this weighting was not applied. Currently, only sample weights are used.
Note on AK305: Lucas Scheidler: 2005 DEER 10 ton 11 EER
Note on AJ306: Lucas Scheidler: DEER 2001 30 ton 10.5 EER
Note on T311: Lucas Scheidler: contractor markup estimate from EMCOR
Note on AM312: Dawdy, John: www.sears.com
Note on AN312: Dawdy, John: www.wallingtonplumbingsupply.com
Note on AO312: Dawdy, John: www.jupiterheating.com
Note on AP312: Dawdy, John: www.ronshomeandhardware.com
Note on AQ312: Dawdy, John: www.plumbersurplus.com
Note on AR312: Dawdy, John: www.menards.com
Note on AS312: Lucas Scheidler: RSMeans Online item 223430
Note on Y313: Lucas Scheidler: For all measures, Baseline units modeled as atmospheric draft. Measure units modeled with the rolled up forced draft coefficient.
Note on AD313: Jeremy Eddy: Descriptive stats are of the percentage difference between the two costs (Modeled-Actual / Actual)
Note on AI313: Dawdy, John: http://www.pexsupply.com/AO-Smith-GCVL-40-40-Gallon-ProMax-6-Yr-Warranty-Residential-Gas-Water-Heater-Short-Model
Note on AJ313: Dawdy, John: http://www.lowes.com/pd_333578-135-NU40T61-403_0__?productId=3284918&Ntt=gas+water+heater&pl=1&currentURL=%3FNtt%3Dgas%2Bwater%2Bheater&facetInfo=
Note on AK313: Dawdy, John: http://www.ventingdirect.com/rheem-22v40f1-40-gallon-tall-natural-gas-residential-water-heater-38000-max-btu-input/p2143047
Note on AL313: Dawdy, John: http://www.homedepot.com/p/GE-40-Gal-Tall-6-Year-36-000-BTU-Natural-Gas-Water-Heater-GG40T06AVG01/100013742
Note on AI314: Dawdy, John: http://www.pexsupply.com/AO-Smith-GVR-40-40-Gallon-40000-BTU-ProMax-Plus-High-Efficiency-Residential-Gas-Water-Heater-Tall-Model-Nat-Gas
Note on AJ314: Dawdy, John: http://www.lowes.com/pd_333591-135-NU40T62-403_0__?productId=3284924&Ntt=gas+water+heater&pl=1&currentURL=%3FNtt%3Dgas%2Bwater%2Bheater&facetInfo=
Note on AK314: Dawdy, John: http://www.ventingdirect.com/rheem-rhgpro40-40f-professional-40-gallon-tall-natural-gas-residential-water-heater-40000-max-btu-input/p2143123
Note on AL314: Dawdy, John: http://www.homedepot.com/p/GE-40-Gal-Tall-6-Year-38-000-BTU-Natural-Gas-High-Efficiency-Ultra-Low-NOx-Water-Heater-GG40T06TXK00/100614634
Note on AI315: Dawdy, John: http://www.pexsupply.com/AO-Smith-GCFL-40-40-Gallon-40000-BTU-Series-100-High-Efficiency-Residential-Water-Heater-Short-Model-Nat-Gas
Note on AJ315: Dawdy, John: http://www.lowes.com/pd_89263-135-PDVG62-40T42-PV_0__?productId=3046938&Ntt=gas+water+heater&pl=1&currentURL=%3FNtt%3Dgas%2Bwater%2Bheater&facetInfo=
Note on AK315: Dawdy, John: http://www.ventingdirect.com/rheem-pdv40ng-power-direct-vent-40-gallon-tall-natural-gas-residential-water-heater-40000-max-btu-input/p2143110
Note on AP315: Dawdy, John: http://www.ronshomeandhardware.com/Reliance-6-40-GBFT-40GAL-NATGas-WTR-Heater-p/138302.htm
Note on AI316: Dawdy, John: http://www.pexsupply.com/AO-Smith-GAHH-40-40-Gallon-40000-BTU-Effex-High-Efficiency-Residential-Gas-Water-Heater
Note on AM316: Dawdy, John: http://www.sears.com/kenmore-elite-40-gal-12-year-natural-gas/p-04233262000P?prdNo=9
Note on AO316: Dawdy, John: http://www.jupiterheating.com/a-o-smith/gahh-effex.html
Note on Q317: Lucas Scheidler: These weights are from 2006 - 2012 CLASS. Weights are the following: AO Smith 10.79%, Bradford White 16.75%, Rheem 10.97% and State 3.77%. No weights were applied, as none of the brands in the model had a significant coefficient.
Note on AI317: Dawdy, John: http://www.pexsupply.com/Bradford-White-M-I-60T6FBN-60-Gallon-40000-BTU-Defender-Safety-System-Atmospheric-Vent-Energy-Saver-Residential-Water-Heater-Nat-Gas
Note on AK317: Dawdy, John: http://www.ventingdirect.com/rheem-42v60f-60-gallon-tall-natural-gas-residential-water-heater-50000-max-btu-input/p2143063
Note on AL317: Dawdy, John: http://www.homedepot.com/p/GE-60-Gal-Tall-12-Year-45-000-BTU-Natural-Gas-Ultra-Low-NOx-Water-Heater-SG60T12YXS10/202020646#specifications
Note on AN317: Dawdy, John: http://www.wallingtonplumbingsupply.com/index.jsp?path=product&part=663951&ds=dept&process=search&qdx=0&text=Rheem
Note on AK318: Dawdy, John: http://www.ventingdirect.com/rheem-rhgpro75f-75-gallon-tall-natural-gas-residential-heavy-duty-water-heater-75100-max-btu-input/p2143131
Note on AP318: Dawdy, John: http://www.ronshomeandhardware.com/6-75-XRRS-75GAL-Natural-GasWater-Heater-p/747124.htm
Note on AQ318: Dawdy, John: http://www.plumbersurplus.com/Prod/Reliance-6-75-XRRS-75-Gallon-Gas-Water-Heater/168648/Cat/771
Note on AR318: Dawdy, John: http://www.menards.com/main/plumbing/water-heaters/residential-water-heaters/richmond-75-gal-lp-gas-6-year-tall-heavy-duty-water-heater/p-1494283-c-8690.htm
Note on K334: Lucas Scheidler: DEER 2013 update
Note on X334: Lucas Scheidler: Baseline Efs adjusted according to DEER 2013 update
Note on AD334: Jeremy Eddy: Descriptive stats are of the percentage difference between the two costs (Modeled-Actual / Actual)
Note on Q336: Lucas Scheidler: These weights are from 2006 - 2012 CLASS. Weights are the following: AO Smith 7.19%, Bradford White 16.49%, Rheem 7.71% and State 7.68%. Only the weight for Rheem is applied, as it is the only brand with a significant coefficient.
Note on AD345: Jeremy Eddy: Descriptive stats are of the percentage difference between the two costs (Modeled-Actual / Actual)
Note on AI345: http://www.tanklessking.com
Note on AM345: Phillip Kelsven: http://www.ecodirect.com
Note on AN345: Phillip Kelsven: https://www.acwholesalers.com
Note on AR345: Phillip Kelsven: http://www.westsidewholesale.com
Note on X346: Lucas Scheidler: Assume TE is approximately equal to EF for instantaneous heaters due to no standby losses. AHRI database confirms that recovery efficiency is equal to EF for most units.
Note on AJ346: Phillip Kelsven: http://www.amazon.com
Note on AK346: Phillip Kelsven: http://www.pexsupply.com
Note on AT346: Phillip Kelsven: http://www.buyzillion.com/1117179175620356/takagi-t-h2s-osng-8-0-gpm-outdoor-condensing-tankless-water-heater
Note on AO347: Phillip Kelsven: http://www.faucetdepot.com/prod/Noritz-NRC98-OD-NG-Outdoor-9.8-Gpm-Natural-Gas-Condensing-Tankless-Water-Heater-141451.asp
Note on AP347: Phillip Kelsven: http://www.pricegrabber.com
Note on AU347: Phillip Kelsven: http://www.theenergyconscious.com
Note on AL348: Phillip Kelsven: http://ecomfort.com
Note on AS348: Phillip Kelsven: http://shop.designerplumbing.com
Note on AV348: Phillip Kelsven: http://www.sears.com/noritz-protough-nr981-dvc-lp-residential-tankless-water/p-SP102A18042S6999341109?prdNo=17
Note on AQ349: Phillip Kelsven: http://www.alpinehomeair.com/viewproduct.cfm?productID=453061611&displaytab=instructions_brochures
Note on AW349: Phillip Kelsven: http://www.homeclick.com
Note on AX350: Phillip Kelsven: http://www.atanklesslife.com
Note on V356: Mike Ting: No product specs specified in DEER or WPs
Note on AD356: Lucas Scheidler: Descriptive stats are on percentage difference between modeled and actual prices ((Modeled - Actual)/Actual)
Note on AI356: Phillip Kelsven: http://www.lowes.com
Note on AJ356: Phillip Kelsven: http://www.sears.com
Note on AK356: Phillip Kelsven: http://www.appliancesconnection.com
Note on AL356: Phillip Kelsven: Phillip Kelsven: http://www.amazon.com
Note on AP357: Phillip Kelsven: http://www.pexsupply.com
Note on AQ357: Phillip Kelsven: http://hotwater1.com
Note on AM358: Phillip Kelsven: http://www.theenergyconscious.com
Note on AR358: Phillip Kelsven: http://www.buyplumbingsupply.com
Note on AV358: Phillip Kelsven: http://www.homedepot.com
Note on AN359: Phillip Kelsven: http://www.ventingdirect.com
Note on AO359: Phillip Kelsven: Phillip Kelsven: http://www.google.com/url?sa=t&rct=j&q=&esrc=s&source=web&cd=24&ved=0CE4QFjADOBQ&url=http%3A%2F%2Fcatalog.standardsupplyco.com%2Fdefault.aspx%3Fpage%3Ditem%2520detail%26itemcode%3DRHEEM%2BHP40RH&ei=M7fuUab3CoL-iQLu4ICYDg&usg=AFQjCNHfolrh9rVB2jL-_By7Nh-qBfO2Bg&sig2=aWc9Va2Ht1gaxLX7QxUp1w&bvm=bv.49641647,d.cGE
Note on AS360: Phillip Kelsven: http://www.homeperfect.com/ao-smith-phpt-80-80-gallon-voltex-residential-hybrid-electric-heat-pump-water-heater.html
Note on AT360: Phillip Kelsven: http://www.acsuperstore.com
Note on AU361: Phillip Kelsven: http://www.buyplumbing.net
Note on AI366: Lucas Scheidler: www.build.com
Note on AJ366: Lucas Scheidler: www.buyplumbingsupply.com
Note on AK366: Lucas Scheidler: www.globalindustrial.com
Note on AL366: Lucas Scheidler: www.pexsupply.com
Note on AM366: Lucas Scheidler: waterheaterstore.com
Note on AN366: Lucas Scheidler: www.wayfair.com
Note on AO366: Lucas Scheidler: www.wallingfordsales.com
Note on AP366: Lucas Scheidler: www.commercialwaterheaters.com
Note on AQ366: Lucas Scheidler: www.bostonheatingsupply.com
Note on AR366: Lucas Scheidler: www.grainger.com
Note on AS366: Lucas Scheidler: faucet.com
Note on AT366: Lucas Scheidler: newyorkwaterheaters.com
Note on AU366: Lucas Scheidler: plumbersurplus.com
Note on AV366: Lucas Scheidler: drillspot.com
Note on AW366: Lucas Scheidler: saberandsons.com
Note on AX366: Lucas Scheidler: amazon.com
Note on AY366: Lucas Scheidler: designerplumbing.com
Note on AZ366: Lucas Scheidler: homedepot.com
Note on BA366: Lucas Scheidler: consumersplumbing.com
Note on AD367: Jeremy Eddy: Descriptive stats are of the percentage difference between the two costs (Modeled-Actual / Actual)
Note on Q376: Lucas Scheidler: These weights are from 2006 - 2012 CLASS. Weights are the following: AO Smith 30.92%, and State 8.83%. No weighting is applied, as it no brand had a significant coefficient.
Note on AD392: Lucas Scheidler: Descriptive stats are on percentage difference between modeled and actual prices ((Modeled - Actual)/Actual)
Note on AG392: Mike Ting: unable to find 200 sqft coverage products
Note on AK392: Phillip Kelsven: http://shop.kendallelectric.com
Note on AL392: Phillip Kelsven: webstore.servelectric.com
Note on AM392: Phillip Kelsven: www.platt.com
Note on X393: Mike Ting: unable to find 200 sqft coverage products
Note on AJ393: Phillip Kelsven: http://www.warehouse-lighting.com
Note on AR393: Phillip Kelsven: http://www.readywholesaleelectric.com
Note on AI394: Phillip Kelsven: http://www.kele.com
Note on AJ394: Phillip Kelsven: http://www.shamrocksupply.com
Note on AS394: Phillip Kelsven: http://www.goodmart.com
Note on AT394: Phillip Kelsven: www.northcoastelectric.com
Note on AU394: Lucas Scheidler: Average of artificial bids
Note on AN395: Phillip Kelsven: quest artificial bid
Note on AO395: Phillip Kelsven: quest artificial bid
Note on AP395: Phillip Kelsven: quest artificial bid
Note on AQ395: Phillip Kelsven: quest artificial bid
Note on AU395: Lucas Scheidler: Average of artificial bids
Note on T401: Lucas Scheidler: placeholder until we get contractor markups from EMCOR

## Labor Results Matrix
| Labor Cost Recommended Values | [10 empty] | Labor Cost Benchmarking | [7 empty] | Labor Cost Supporting Data
Technology |  |  | Recommended Values | [8 empty] | Benchmarking | [8 empty] | Subcontractor Artificial Bids | [11 empty] | Contractor Surveys | [6 empty] | RSMeans
| Installation Dimension/Scenario | Common Unit | Source of recommend values | Labor Hours per unit | Total Labor Hours Formula | Labor Hourly Rate | Labor Cost per unit | Miscellaneous Costs per unit | Miscellaneous Fixed Costs (per project) | Markup | Total Non-equipment costs ($/unit) excluding fixed costs | Source | Total Labor Hours Formula | Labor Hours / unit | Labor Hourly Rate | Labor Cost per unit | Miscellaneous Costs per unit | Miscellaneous Fixed Costs (per project) | Total Non-equipment costs ($/unit) before markup excluding fixed costs | Scenario | Labor Hours 1 | Labor Hourly Rate 1 | Labor Cost 1 | Non-equipment materials 1 | Misc expenses 1 | Fees 1 | Labor Hours 2 | Labor Hourly Rate 2 | Labor Cost 2 | Non-equipment materials 2 | Misc expenses 2 | Fees 2 | Labor Hours 3 | Labor Hours 3 Std err | Labor Hours N | Labor Hourly Rate 3 | Misc expenses 3 | Misc expenses 3 Std err | Misc expenses N | Labor Hours 5 | Labor Hourly Rate 5
Residential HVAC | [54 empty] | Table G-1: Statewide RSMeans Cost Indices Weighted by 2010-2012 HVAC Measure Claims
Gas Furnaces (residential) | Labor Cost | MBH | RSMeans | 0.058789 | H = 0.017(MBH) + 3.2398 | 55.563 | 3.2665 |  |  | 23% | 4.0178 | DEER 2008 |  | 0.086 | 67.88 |  |  |  | 5.8377 | Up-flow 45 MBH | [19 empty] | 4 | 47.98 | [13 empty] | Climate Zone | Reference City | Material1 | Installation1 | Weights2 | Weighted Material | Weighted Installation
[20 empty] | Up-flow 75 MBH | [19 empty] | 4.444 | 47.98 | [13 empty] | 1 | Eureka | 0.94 | 1.017 | 0.0032678 | 0.0030717 | 0.0033234 | SF to statewide weight
[20 empty] | Up-flow 100 MBH | [19 empty] | 5 | 47.98 | [13 empty] | 2 | Santa Rosa | 0.94 | 1.653 | 0.0096952 | 0.0091135 | 0.016026 | 0.6922
[20 empty] | Up-flow 120 MBH | [19 empty] | 5.333 | 47.98 | [13 empty] | 3 | San Francisco | 1.001 | 1.673 | 0.030274 | 0.030304 | 0.050648
[20 empty] | Up-flow 125 MBH | [19 empty] | 5.333 | 47.98 | [13 empty] | 4 | San Jose | 1 | 1.448 | 0.015286 | 0.015286 | 0.022134
[20 empty] | Up-flow 150 MBH | [19 empty] | 5.714 | 47.98 | [13 empty] | 5 | San Luis Obispo | 0.94 | 1.055 | 0.00043296 | 0.00040698 | 0.00045677
[20 empty] | Horizontal flow 45 MBH | [19 empty] | 4 | 47.98 | [13 empty] | 6 | Santa Barbara | 1 | 1.167 | 0.1391 | 0.1391 | 0.16233
[20 empty] | Horizontal flow 60 MBH | [19 empty] | 4.211 | 47.98 | [13 empty] | 7 | San Diego | 1 | 1.152 | 0.046714 | 0.046714 | 0.053815
[20 empty] | Horizontal flow 70 MBH | [19 empty] | 4.444 | 47.98 | [13 empty] | 8 | Santa Ana | 0.94 | 1.055 | 0.16224 | 0.15251 | 0.17117
[20 empty] | Horizontal flow 90 MBH | [19 empty] | 4.848 | 47.98 | [11 empty] | means labor markup |  | 9 | Los Angeles | 1.001 | 1.167 | 0.2181 | 0.21832 | 0.25453
[20 empty] | Horizontal flow 110 MBH | [19 empty] | 5.161 | 47.98 | [13 empty] | 10 | Riverside | 1 | 1.166 | 0.21278 | 0.21278 | 0.2481
[42 empty] | 45 | 0.088889 | Average | 0.058789 | [5 empty] | 919.79 | 1152.1 | 1.2526 |  | 11 | Redding | 1 | 1.07 | 0.010239 | 0.010239 | 0.010956
Split-System HP (residential and commerical) | Non-Res Labor and non-equipment costs | unt | Contractor survey | 31.3538 |  |  | 2235.4109 | 58.7346 | 598.378 |  | 5132.698 | RSMeans | H = 7.7894e0.4643(tons) | 30.4763 | 60.3339 | 1838.7554 |  |  | 1838.7554 | 3 ton 1.1 kw/ton (10.9 EER) | 27 | 108 | 2912 | 1000 | 500 | 2003 | 49 | 98 | 4784 | 219 | - | 241 | [9 empty] | 75 | 0.059253 | Std dev | 0.017609 | [5 empty] | 936.89 | 1181.17 | 1.2607 |  | 12 | Sacramento | 1 | 1.198 | 0.036051 | 0.036051 | 0.04319
| Non-Res Labor rate | unit | Artificial bids |  |  | 71.2963 |  |  |  | 27.5% |  | Artificial bids |  | 38 |  | 2709.2578 | 1790.2346 | 500 | 4499.4924 | Crane rental | [16 empty] | 598.378 | 83.2621 | 37 |  |  | 100 | 0.05 | min | 0.038093 | [5 empty] | 996.96 | 1252.67 | 1.2565 |  | 13 | Fresno | 1.001 | 1.113 | 0.021693 | 0.021715 | 0.024144
| Non-Res Micellanous costs | unit | Artificial bids |  |  |  |  | 1731.5 |  |  |  | DEER 2008 |  | 18 | 67.88 | 1221.84 |  |  | 1221.84 | Installation (5 ton) | [12 empty] | 15.4134 | 1.7538 | 36 | [6 empty] | 120 | 0.044442 | max | 0.088889 | [5 empty] | 1098.15 | 1380.68 | 1.2573 |  | 14 | Mojave | 0.94 | 0.992 | 0.034946 | 0.032849 | 0.034666
| Res Labor and non-equipment costs | unit | DOE TSD & bids | 8.0043 |  | 71.2963 | 570.68 |  |  |  | 727.617 | [8 empty] | Removal | [12 empty] | 12.6446 | 2.2566 | 37 | [6 empty] | 125 | 0.042664 | [7 empty] | 1157.61 | 1455.52 | 1.2573 |  | 15 | Palm Springs | 0.94 | 1.054 | 0.047199 | 0.044367 | 0.049748
[20 empty] | Disposal | [16 empty] | 58.7346 | 12.7201 | 33 |  |  | 150 | 0.038093 | [7 empty] | 1206.73 | 1529.75 | 1.2677 |  | 16 | Susanville | 0.94 | 1.07 | 0.011973 | 0.011255 | 0.012811
[20 empty] | Testing/commissioning (5 ton) | [12 empty] | 3.2958 | 0.48883 | 36 | [6 empty] | 45 | 0.088889 | [7 empty] | 3072.05 | 3589.28 | 1.1684 |  |  | Average | 0.97394 | 1.1906 | 1 | 0.98408 | 1.158
[20 empty] | 1.5 ton condensing unit | [19 empty] | 6.667 | 50.98 | 60 | 0.070183 | [7 empty] | 3415.55 | 4012.83 | 1.1749 |  | 1 - Table 21, 22, 23 (Fire Suppression, Plumbing, & HVAC) RSMeans MasterFormat City Cost Indexes, Year 2013 National Average Base
[20 empty] | 2 ton condensing unit | [19 empty] | 8 | 50.98 | 70 | 0.063486 | [7 empty] | 3822 | 4484.95 | 1.1735 |  | 2 - 2010-2012 Standard Program Tracking Data (all in-scope deemed HVAC claims)
[20 empty] | 2.5 ton condensing unit | [19 empty] | 10 | 50.98 | 90 | 0.053867 | [9 empty] | 1.2299
[20 empty] | 3 ton condensing unit | [19 empty] | 13.3333 | 50.98 | 110 | 0.046918
[20 empty] | 3.5 ton condensing unit | [19 empty] | 16 | 50.98 | [13 empty] | Table G-2: Statewide RSMeans Cost Indices Weighted by 2010-2012 Lighting Measure Claims
[20 empty] | 4 ton condensing unit | [19 empty] | 20 | 50.98 | [13 empty] | Climate Zone | Reference City | Material1 | Installation1 | Weights2 | Weighted Material | Weighted Installation
[20 empty] | 5 ton condensing unit | [19 empty] | 32 | 50.98 | [13 empty] | 1 | Eureka | 1.002 | 1.146 | 0.0054359 | 0.0054468 | 0.0062295
[20 empty] | 2 ton fan coil | [19 empty] | 12 | 52.87 | [13 empty] | 2 | Santa Rosa | 0.965 | 1.187 | 0.013086 | 0.012628 | 0.015533
[20 empty] | 2.5 ton fan coil | [19 empty] | 15 | 52.87 | [13 empty] | 3 | San Francisco | 1.061 | 1.571 | 0.04861 | 0.051575 | 0.076367
[20 empty] | 3 ton fan coil | [19 empty] | 17.143 | 52.87 | [13 empty] | 4 | San Jose | 1.025 | 1.532 | 0.019217 | 0.019697 | 0.02944
[20 empty] | 4 ton fan coil | [19 empty] | 30 | 52.87 | [13 empty] | 5 | San Luis Obispo | 0.904 | 0.962 | 0.0051419 | 0.0046483 | 0.0049465
[20 empty] | 5 ton fan coil | [19 empty] | 48 | 52.87 | tons | cond. + coil labor | hr/ton | [10 empty] | 6 | Santa Barbara | 0.894 | 1.097 | 0.13381 | 0.11963 | 0.14679
[20 empty] | DOE TSD | 8.0043 | 90.9027 | 727.617 | [18 empty] | 2 | 20 | 10 | 52.114 | [9 empty] | 7 | San Diego | 0.992 | 0.991 | 0.033253 | 0.032987 | 0.032954
[42 empty] | 2.5 | 25 | 10 | 52.114 | [9 empty] | 8 | Santa Ana | 0.962 | 1.03 | 0.19239 | 0.18508 | 0.19816
Split-System DX (residential and commerical) | Non-Res Labor and non-equipment costs | unt | Contractor survey | 31.3538 |  |  | 2246.2624 | 58.7346 | 598.378 |  | 5801.2461 | RSMeans | H = 1.6543(tons) + 5.2908 | 10.878 | 59.0371 | 642.206 |  |  | 642.206 | 3 ton 1.1 kw/ton (10.9 EER) | 44 | 109 | 4816 | 1375 | 500 | 2655 | 57 | 98 | 5574 | 219 | - | 241 | [9 empty] | 3 | 30.4763 | 10.1588 | 52.0431 | [9 empty] | 9 | Los Angeles | 0.998 | 1.208 | 0.16605 | 0.16572 | 0.20059
| Non-Res Labor rate | unit | Artificial bids |  |  | 71.6424 |  |  |  | 27.5% |  | Artificial bids |  | 50.5 |  | 3617.9389 | 2303.7346 | 500 | 5921.6735 | Crane rental | [16 empty] | 598.378 | 83.2621 | 37 |  |  | 4 | 50 | 12.5 | 52.114 | [9 empty] | 10 | Riverside | 0.925 | 1.065 | 0.19969 | 0.18471 | 0.21267
| Non-Res Micellanous costs | unit | Artificial bids |  |  |  |  | 2245 |  |  |  | DEER 2008 |  | 18 | 67.88 | 1221.84 |  |  | 1221.84 | Installation (5 ton) | [12 empty] | 15.4134 | 1.7538 | 36 | [6 empty] | 5 | 80 | 16 | 52.114 | [9 empty] | 11 | Redding | 0.997 | 1.018 | 0.01062 | 0.010589 | 0.010812
| Res Labor and non-equipment costs | unit | DOE TSD & bids | 7.2557 |  | 71.6424 | 519.8173 |  |  |  | 662.767 | [8 empty] | Removal | [12 empty] | 12.6446 | 2.2566 | 37 | [7 empty] | Average | 11.7318 | 52.0998 | [9 empty] | 12 | Sacramento | 1.012 | 1.133 | 0.038485 | 0.038947 | 0.043604
[20 empty] | Disposal | [16 empty] | 58.7346 | 12.7201 | 33 |  |  |  | Std dev | 2.6115 | [10 empty] | 13 | Fresno | 0.918 | 1.015 | 0.05595 | 0.051362 | 0.056789
[20 empty] | Testing/commissioning (5 ton) | [12 empty] | 3.2958 | 0.48883 | 36 | [19 empty] | 14 | Mojave | 0.904 | 0.964 | 0.048091 | 0.043474 | 0.04636
[20 empty] | 1 ton condensing unit | [19 empty] | 4.211 | 50.98 | [13 empty] | 15 | Palm Springs | 0.962 | 1.024 | 0.025533 | 0.024563 | 0.026146
[20 empty] | 1.5 ton condensing unit | [19 empty] | 4.444 | 50.98 | [13 empty] | 16 | Susanville | 1.001 | 1.018 | 0.0046397 | 0.0046444 | 0.0047232
[20 empty] | 2 ton condensing unit | [19 empty] | 5 | 50.98 | [14 empty] | Average | 0.97012 | 1.1226 | 1 | 0.9557 | 1.1121
[20 empty] | 3 ton condensing unit | [19 empty] | 6.667 | 50.98
[20 empty] | 5 ton condensing unit | [19 empty] | 8 | 50.98 | [13 empty] | 1 - Table 26, 27, 3370 (Electrical, Communications, & Utilities) RSMeans MasterFormat City Cost Indexes, Year 2013 National Average Base
[20 empty] | 1.5 ton fan coil | [19 empty] | 3.2 | 50.98 | [13 empty] | 2 - 2010-2012 Standard Program Tracking Data (all in-scope deemed nonresidential lighting claims)
[20 empty] | 2 ton fan coil | [19 empty] | 3.333 | 50.98
[20 empty] | 2.5 ton fan coil | [19 empty] | 3.636 | 50.98 | [13 empty] | Table G-3: Statewide RSMeans Cost Indices Weighted by 2010-2012 Buidling Shell Measure Claims
[20 empty] | 3 ton fan coil | [19 empty] | 4.211 | 50.98 | [13 empty] | Climate Zone | Reference City | Material1 | Installation1 | Weights2 | Weighted Material | Weighted Installation
[20 empty] | 3.5 ton fan coil | [19 empty] | 4.444 | 50.98 | [13 empty] | 1 | Eureka | 1.041 | 1.137 | 0.00102 | 0.0010619 | 0.0011598
[20 empty] | 4 ton fan coil | [19 empty] | 4.706 | 50.98 | tons | cond. + coil labor | hr/ton | [10 empty] | 2 | Santa Rosa | 1.004 | 1.335 | 0.020813 | 0.020896 | 0.027785
[20 empty] | 5 ton fan coil | [19 empty] | 5.333 | 50.98 | 1.5 | 7.644 | 5.096 | [10 empty] | 3 | San Francisco | 1.095 | 1.381 | 0.096689 | 0.10587 | 0.13353
[20 empty] | DOE TSD | 7.2557 | 91.344 | 662.767 | [18 empty] | 2 | 8.333 | 4.1665 | [10 empty] | 4 | San Jose | 0.996 | 1.389 | 0.062498 | 0.062248 | 0.086809
[42 empty] | 3 | 10.878 | 3.626 | [10 empty] | 5 | San Luis Obispo | 1.009 | 1.141 | 0.0013143 | 0.0013261 | 0.0014996
Residential HVAC Fan Motors | Labor Cost | unit | NREL | 2.5938 |  | 56.5821 | 146.7598 |  |  | 18% | 173.1765 | RSMeans | H = 2.4721(HP) + 2.8865 | 12.9053 | 56.5821 | 730.2106 |  |  | 730.2106 | Direct drive, 150 CFM, 1/8HP | [19 empty] | 3.125 | 48.86 | 5 | 13.333 | 2.6666 | [10 empty] | 6 | Santa Barbara | 1.002 | 1.17 | 0.072404 | 0.072549 | 0.084712
[12 empty] | RSMeans | H = 1.5942(HP) + 3.1808 | 8.9728 | 56.5821 | 507.7016 |  |  | 507.7016 | Direct drive, 485 CFM, 1/6HP | [19 empty] | 3.448 | 48.86 | [13 empty] | 7 | San Diego | 1.012 | 1.048 | 0.05471 | 0.055366 | 0.057336
[12 empty] | workpaper references Means 2002 | [7 empty] | Direct drive, 1950 CFM, 1/2HP | [19 empty] | 4.167 | 48.86 | [13 empty] | 8 | Santa Ana | 1 | 1.175 | 0.11244 | 0.11244 | 0.13212
[20 empty] | Direct drive, 2410 CFM, 3/4HP | [19 empty] | 4.545 | 48.86 | [13 empty] | 9 | Los Angeles | 1.022 | 1.212 | 0.17515 | 0.17901 | 0.21229
[20 empty] | Direct drive, 3328 CFM, 1-1/2HP | [19 empty] | 6.667 | 48.86 | [13 empty] | 10 | Riverside | 1.002 | 1.212 | 0.15571 | 0.15603 | 0.18873
[20 empty] | V-belt drive, 800 CFM, 1/4 HP | [19 empty] | 3.333 | 48.86 | [13 empty] | 11 | Redding | 1.036 | 1.157 | 0.037546 | 0.038897 | 0.04344
[20 empty] | V-belt drive, 1300 CFM, 1/3 HP | [19 empty] | 4 | 48.86 | [13 empty] | 12 | Sacramento | 1.163 | 1.225 | 0.10265 | 0.11938 | 0.12575
[20 empty] | V-belt drive, 2000 CFM, 3/4 HP | [19 empty] | 4.348 | 48.86 | [13 empty] | 13 | Fresno | 0.939 | 1.148 | 0.04194 | 0.039381 | 0.048147
[20 empty] | V-belt drive, 2900 CFM, 1 HP | [19 empty] | 4.762 | 48.86 | CFM | HP | hr/HP | [10 empty] | 14 | Mojave | 1 | 1.087 | 0.01328 | 0.01328 | 0.014436
[20 empty] | Average of NREL study | 2.5938 | [20 empty] | 150 | 0.125 | 25 | [9 empty] | rs means markup | 15 | Palm Springs | 0.997 | 1.174 | 0.041273 | 0.041149 | 0.048454
[42 empty] | 485 | 0.16667 | 20.688 | [7 empty] | 1146.74 | 1371.69 | 1.1962 | 16 | Susanville | 1.041 | 1.157 | 0.010554 | 0.010986 | 0.01221
[42 empty] | 1950 | 0.5 | 8.334 | [7 empty] | 1394.37 | 1650.71 | 1.1838 |  | Average | 1.0224 | 1.1967 | 1 | 1.0299 | 1.2184
[42 empty] | 2410 | 0.75 | 6.06 | [7 empty] | 1644.72 | 1958.43 | 1.1907 | 1 - Table 07 (Thermal and Moisture Protection) RSMeans MasterFormat City Cost Indexes, Year 2013 National Average Base
[42 empty] | 3328 | 1.5 | 4.4447 | [7 empty] | 2787.09 | 3221.05 | 1.1557 | 2 - 2010-2012 Standard Program Tracking Data (all in-scope deemed nonresidential building shell claims)
Non-Residential HVAC | [41 empty] | 800 | 0.25 | 13.332 | [7 empty] | 3258.5 | 3815.35 | 1.1709
Fan VFDs (>10hp) | Labor Cost > 50 HP | HP | RSMeans | 0.39524 | H = 0.0796(HP) + 30.5 | 65.3142 | 25.8145 |  |  | 20% | 30.9774 | [8 empty] | Variable frequency drives, enclosed, 460 volt, 15HP, NEMA1 | [19 empty] | 17.978 | 52.4 | 1300 | 0.33333 | 12 | [7 empty] | 1277.47 | 1527.09 | 1.1954
| Labor Cost 15 - 50 HP | HP | RSMeans | 0.81885 | H = 0.3405(HP) + 12.225 | 58.2745 | 47.7184 |  |  |  | 57.262 | [8 empty] | Variable frequency drives, enclosed, 460 volt, 20HP, NEMA1 | [19 empty] | 17.978 | 52.4 | 2000 | 0.75 | 5.7973 | [7 empty] | 1380.05 | 1665.34 | 1.2067
[20 empty] | Variable frequency drives, enclosed, 460 volt, 30HP, NEMA1 | [19 empty] | 23.881 | 52.4 | 2900 | 1 | 4.762 | [7 empty] | 1603.91 | 1929.38 | 1.2029
[20 empty] | Variable frequency drives, enclosed, 460 volt, 40HP, NEMA1 | [19 empty] | 23.881 | 52.4 |  |  | avg direct | 12.9053 | [6 empty] | 2073.19 | 2440.9 | 1.1774
[20 empty] | Variable frequency drives, enclosed, 460 volt, 50HP, NEMA1 | [19 empty] | 30.189 | 52.4 |  |  | std direct | 9.3031 | [6 empty] | 2471.42 | 2900.1 | 1.1735
[20 empty] | Variable frequency drives, enclosed, 460 volt, 60HP, NEMA1 | [19 empty] | 35.714 | 58.73 |  |  | avg v-belt | 8.9728 | [6 empty] | 2909.97 | 3399.38 | 1.1682
[20 empty] | Variable frequency drives, enclosed, 460 volt, 75HP, NEMA1 | [19 empty] | 35.714 | 58.73 |  |  | std v-belt | 4.3198 | [8 empty] | 1.1838
[20 empty] | Variable frequency drives, enclosed, 460 volt, 100HP, NEMA1 | [19 empty] | 40 | 58.73
[20 empty] | Variable frequency drives, enclosed, 460 volt, 150HP, NEMA1 | [19 empty] | 40 | 58.73 | HP | Hours/HP
[20 empty] | Variable frequency drives, enclosed, 460 volt, 200HP, NEMA1 | [19 empty] | 47.619 | 58.73 | 15 | 1.1985 | Average | 0.60705 | [6 empty] | 4282.01 | 5289.58 | 1.2353
[42 empty] | 20 | 0.8989 | Std dev | 0.29495 | [6 empty] | 4784.66 | 5845.08 | 1.2216
Fan VFDs (<= 10hp) | Labor Cost 3 - 10 HP | HP | RSMeans | 3.3333 | H = 0.3328(HP) + 8.8483 | 58.2745 | 194.2484 |  |  | 20% | 233.0981 | [8 empty] | Variable frequency drives, enclosed, 460 volt, 3HP, NEMA1 | [19 empty] | 10 | 52.4 | 30 | 0.79603 | [8 empty] | 6076.2 | 7494.65 | 1.2334
[20 empty] | Variable frequency drives, enclosed, 460 volt, 5HP, NEMA1 | [19 empty] | 10 | 52.4 | 40 | 0.59703 | [8 empty] | 6997.73 | 8527.88 | 1.2187
[20 empty] | Variable frequency drives, enclosed, 460 volt, 7.5HP, NEMA1 | [19 empty] | 11.94 | 52.4 | 50 | 0.60378 | [8 empty] | 8030.95 | 9644.88 | 1.201
[20 empty] | Variable frequency drives, enclosed, 460 volt, 10HP, NEMA1 | [19 empty] | 11.94 | 52.4 | 60 | 0.59523 | [8 empty] | 10017.35 | 12058.6 | 1.2038
[42 empty] | 75 | 0.47619 | [8 empty] | 12190.07 | 14630.87 | 1.2002
[42 empty] | 100 | 0.4 | [8 empty] | 13586.32 | 16138.62 | 1.1879
[42 empty] | 150 | 0.26667 | [8 empty] | 15551.8 | 18494.1 | 1.1892
[42 empty] | 200 | 0.2381 | [8 empty] | 17003.9 | 20057.9 | 1.1796
1.2071
[42 empty] | 3 | 3.3333 | Average | 3.3333
Small Packaged DX (<= 5 tons) | Labor and non-equipment costs | tons | Contractor survey | 6.2708 | y = 0.845(tons) + 27.129 |  | 443.2841 | 11.7469 | 598.378 | 27.5% | 898.8736 | RSMeans | H = 3.4156e0.413(tons) | 5.3334 | 59.0371 | 314.8687 |  |  | 314.8687 | Crane rental | [16 empty] | 598.378 | 83.2621 | 37
| Labor Rate | tons | Artificial bids |  |  | 70.6906 | [5 empty] | DEER 2008 |  | 5.27 | 67.88 | 357.7276 |  |  | 357.7276 | Installation (5 ton) | [12 empty] | 15.4134 | 1.7538 | 36
| Micellanous costs | tons | Artificial bids |  |  |  |  | 249.9679 | [11 empty] | Removal | [12 empty] | 12.6446 | 2.2566 | 37
[20 empty] | Disposal | [16 empty] | 58.7346 | 12.7201 | 33
[20 empty] | Testing/commissioning (5 ton) | [12 empty] | 3.2958 | 0.48883 | 36
[20 empty] | 1.5 ton | [19 empty] | 6.4 | 50.98
[20 empty] | 2 ton | [19 empty] | 7.619 | 50.98
[20 empty] | 2.5 ton | [19 empty] | 9.412 | 50.98
[20 empty] | 3 ton | [19 empty] | 12.308 | 50.98
[20 empty] | 3.5 ton | [19 empty] | 14.545 | 50.98 | [9 empty] | means markup
[20 empty] | 4 ton | [19 empty] | 17.778 | 50.98 | [7 empty] | 1902.25 | 2315.08 | 1.217
[20 empty] | 5 ton | [19 empty] | 26.667 | 50.98 | [7 empty] | 2174.2 | 2664.55 | 1.2255
[49 empty] | 2406.78 | 2972.73 | 1.2351
Large Packaged DX (> 5 tons) | Labor and non-equipment costs | tons | Contractor survey | 1.5232 | y = 0.845(tons) + 27.129 |  | 107.675 | 1.4684 | 598.378 | 27.5% | 457.8669 | RSMeans less than 20 tons | H = 2.5122(tons) + 7.235 | 3.2485 | 59.0371 | 191.7815 |  |  | 191.7815 | 20 ton ground mounted | 27 | 108 | 2912 | 1000 | 1500 | 6587 | 50 | 96 | 5091 | 714 | 600 | 799 | [9 empty] | tons | hr/ton | [5 empty] | 2650.38 | 3350.73 | 1.2642
| Labor rate | tons | Artificial bids |  |  | 70.6906 | [5 empty] | RSMeans 20 tons or more |  | 2.7162 | 61.2258 | 166.3009 |  |  | 166.3009 | 20 ton ground mounted gas heat | 27 | 108 | 2912 | 1100 | 1500 | 6387 | 53 | 96 | 5381 | 814 | 600 | 799 | [9 empty] | 1.5 | 4.2667 | average | 4.2682 |  |  |  | 3087.7 | 3924.38 | 1.271
| Micellanous costs | tons | Artificial bids |  |  |  |  | 249.9679 |  |  |  | Artificial bids - 20 ton ground |  | 1.9625 | 70.6906 | 138.7303 | 227.5 | 1050 | 366.2303 | 20 ton roof mounted | 27 | 108 | 2912 | 1910 | 2500 | 7196 | 47 | 97 | 4541 | 714 | 1400 | 799 | [9 empty] | 2 | 3.8095 | std dev | 0.52751 |  |  |  | 3609.03 | 4615.63 | 1.2789
[12 empty] | Artificial bids - 20 ton roof |  | 1.85 | 70.6906 | 130.7776 | 265.475 | 1950 | 396.2526 | 70 ton roof mounted | 70 | 109 | 7616 | 6175 | 4500 | 27781 | 86 | 95 | 8213 | 964 | 2000 | 1050 | [9 empty] | 2.5 | 3.7648 | [5 empty] | 4844.88 | 6292.13 | 1.2987
[12 empty] | Artificial bids - 70 ton roof |  | 1.1143 | 70.6906 | 78.7695 | 256.9286 | 3250 | 335.6981 | Crane rental | [16 empty] | 598.378 | 83.2621 | 37 |  |  | 3 | 4.1027 | [5 empty] | 6655.25 | 8322.13 | 1.2505
[12 empty] | DEER 2008 5-60+ton |  | 2.23-4.55 | 67.88 | $151 - $309 |  |  | $151 - $309 | Installation (40 ton) | [12 empty] | 38.6014 | 4.7597 | 26 | [6 empty] | 3.5 | 4.1557 | [5 empty] | 7730.63 | 9548 | 1.2351
[20 empty] | Removal | [12 empty] | 12.6446 | 2.2566 | 37 | [6 empty] | 4 | 4.4445 | [7 empty] | 1.2529
[20 empty] | Disposal | [16 empty] | 58.7346 | 12.7201 | 33 |  |  | 5 | 5.3334
[20 empty] | Testing/commissioning (40 ton) | [12 empty] | 9.6815 | 2.1567 | 26
[20 empty] | 7.5 ton | [19 empty] | 29.091 | 50.98 | 1.35 | 2.5 | [8 empty] | contractor survey
[20 empty] | 10 ton | [19 empty] | 32 | 50.98 | 1.35 | 2.65 | [8 empty] | tons | hrs/ton | hrs
[20 empty] | 15 ton | [19 empty] | 40 | 50.98 | 1.35 | 2.35 | [8 empty] | 5 | 6.27 | 31.3538
[20 empty] | 20 ton | [19 empty] | 60 | 52.87 | 1 | 1.2286 | [8 empty] | 40 | 1.52 | 60.9275
[20 empty] | 25 ton | [19 empty] | 68.571 | 52.87 | [10 empty] | artificial bids
[20 empty] | 30 ton | [19 empty] | 80 | 52.87 | [10 empty] | 20 |  | 50
[20 empty] | 40 ton | [19 empty] | 120 | 52.87 | [10 empty] | 20 |  | 53
[20 empty] | 50 ton | [19 empty] | 133 | 52.87 | [10 empty] | 20 |  | 47
[20 empty] | 60 ton | [19 empty] | 150 | 52.87 | tons | hours/ton | [8 empty] | 70 |  | 70
[20 empty] | 80 ton | [19 empty] | 200 | 52.87 | 7.5 | 3.8788 | average | 2.8614 | [6 empty] | 70 |  | 86
[20 empty] | 100 ton | [19 empty] | 266 | 52.87 | 10 | 3.2 | std dev | 0.40254
[42 empty] | 15 | 2.6667
Air-Cooled Chillers | 100 ton ground mount Labor and non-equipment costs | tons | Artificial bids | 0.795 |  | 71.2963 | 56.6805 | 181.935 | 1400 | 25% | 298.2694 | RSMeans 130 to 320 ton screw | H = 0.221(tons) + 207.06 | 1.2922 | 62.4649 | 80.7189 |  |  | 80.7189 | EMCOR 100 ton ground level | 79 | 108 | 8568 | 5471 | 2000 | 22724 | 80 | 98 | 7811 | 6492 | 800 | 1700 | [9 empty] | 20 | 3 | ave lt 20 | 3.2485
| 200 ton ground mount Labor and non-equipment costs | tons | Artificial bids | 0.4375 |  |  | 31.1921 | 137.5773 | 1650 |  | 210.9618 | RSMeans 10 to 50 ton scroll | H = 0.5261(tons) + 85.493 | 4.2086 | 62.4649 | 262.8891 |  |  | 262.8891 | EMCOR 200 ton ground level | 79 | 108 | 8568 | 6152 | 2500 | 37617 | 96 | 97 | 9354 | 8561.94 | 800 | 2700 | [9 empty] | 25 | 2.7428 | ave ge 20 | 2.7162
| 300 ton ground mount Labor and non-equipment costs | tons | Artificial bids | 0.38167 |  |  | 27.2114 | 133.7818 | 2350 |  | 201.2416 | DEER 2008 screw |  | 1.8 | 67.88 | 122.184 |  |  | 122.184 | EMCOR 300 ton ground level | 114 | 108 | 12278 | 6500 | 3500 | 57892 | 115 | 98 | 11225 | 12077.11 | 1200 | 3800 | [9 empty] | 30 | 2.6667
| 100 ton roof mount Labor and non-equipment costs | tons | Artificial bids | 0.825 |  |  | 58.8194 | 182.0536 | 3500 |  | 301.0913 | [8 empty] | EMCOR 100 ton roof | 75 | 108 | 8120 | 5471 | 4000 | 23186 | 90 | 98 | 8816 | 5953.72 | 3000 | 1800 | [9 empty] | 40 | 3
| 200 ton roof mount Labor and non-equipment costs | tons | Artificial bids | 0.4525 |  |  | 32.2616 | 142.7804 | 4250 |  | 218.8025 | [8 empty] | EMCOR 200 ton roof | 75 | 108 | 8120 | 7152 | 5000 | 38553 | 106 | 98 | 10359 | 8607.17 | 3500 | 2800 | [9 empty] | 50 | 2.66
| 300 ton roof mount Labor and non-equipment costs | tons | Artificial bids | 0.395 |  |  | 28.162 | 138.1233 | 5000 |  | 207.8566 | [8 empty] | EMCOR 300 ton roof | 114 | 108 | 12278 | 7500 | 6000 | 58962 | 123 | 98 | 11999 | 12511.97 | 4000 | 3900 | [9 empty] | 60 | 2.5
[20 empty] | 130 ton screw | [19 empty] | 228 | 53.94 | 80 | 2.5
[20 empty] | 160 ton screw | [19 empty] | 246 | 53.94 | 100 | 2.66
[20 empty] | 180 ton screw | [19 empty] | 250 | 53.94
[20 empty] | 210 ton screw | [19 empty] | 258 | 53.94
[20 empty] | 270 ton screw | [19 empty] | 266 | 53.94
[20 empty] | 320 ton screw | [19 empty] | 275 | 53.94
[20 empty] | 10 ton scroll | [19 empty] | 94.118 | 53.94
[20 empty] | 15 ton scroll | [19 empty] | 94.118 | 53.94
[20 empty] | 20 ton scroll | [19 empty] | 94.118 | 53.94 | tons | hours/ton
[20 empty] | 25 ton scroll | [19 empty] | 94.118 | 53.94 | 130 | 1.7538 | average | 1.2922
[20 empty] | 30 ton scroll | [19 empty] | 101 | 53.94 | 160 | 1.5375 | std dev | 0.33713
[20 empty] | 35 ton scroll | [19 empty] | 104 | 53.94 | 180 | 1.3889
[20 empty] | 40 ton scroll | [19 empty] | 108 | 53.94 | 210 | 1.2286
[20 empty] | 45 ton scroll | [19 empty] | 109 | 53.94 | 270 | 0.98519
[20 empty] | 50 ton scroll | [19 empty] | 113 | 53.94 | 320 | 0.85938
[42 empty] | 10 | 9.4118 | average | 4.2086
Water-Cooled Chillers (excluding centrifugal VSD) | 100 ton ground mount Labor and non-equipment costs | tons | Artificial bids | 1.145 |  | 71.492 | 81.8583 | 203.9031 | 1400 | 25% | 357.2018 | RSMeans 80 - 350 ton screw | H = 0.188x + 210.89 | 1.5221 | 62.4649 | 95.0795 |  |  | 95.0795 | EMCOR 100 ton ground level | 106 | 109.09 | 11564 | 8700 | 2000 | 20339 | 123 | 98 | 12036 | 9441.62 | 800 | 2300 | [9 empty] | 15 | 6.2745 | std dev | 2.3262
| 200 ton ground mount Labor and non-equipment costs | tons | Artificial bids | 0.7875 |  |  | 56.2999 | 179.949 | 2150 |  | 295.3112 | RSMeans 2 - 30 ton scroll | H = 2.6114x + 26.927 | 6.4316 | 60.4413 | 388.7345 |  |  | 388.7345 | EMCOR 200 ton ground level | 156 | 109 | 16940 | 15261 | 3500 | 38418 | 159 | 98 | 15546 | 14700.59 | 800 | 3600 | [9 empty] | 20 | 4.7059
| 300 ton ground mount Labor and non-equipment costs | tons | Artificial bids | 0.605 |  |  | 43.2527 | 155.0163 | 2750 |  | 247.8362 | RSMeans 400 - 2500 centrifugal | H = 0.1177x + 246.68 | 0.36343 | 62.4649 | 22.7016 |  |  | 22.7016 | EMCOR 300 ton ground level | 174 | 108 | 18872 | 15461 | 4000 | 51141 | 189 | 98 | 18439 | 21807.76 | 1500 | 4600 | [9 empty] | 25 | 3.7647
| 100 ton basement Labor and non-equipment costs | tons | Artificial bids | 1.585 |  |  | 113.3148 | 215.6396 | 5000 |  | 411.193 | DEER 2008 screw |  | 1.06-2.97 | 67.88 | $71.95 - $201.60 |  |  | $71.95 - $201.60 | EMCOR 100 ton basement | 134 | 108 | 14476 | 8350 | 6500 | 22444 | 183 | 101 | 18531 | 9833.91 | 3500 | 2500 | [9 empty] | 30 | 3.3667
| 200 ton basement Labor and non-equipment costs | tons | Artificial bids | 1.0575 |  |  | 75.6028 | 185.5025 | 5500 |  | 326.3816 | DEER 2008 centrifugal |  | 1.23-1.41 | 67.88 | $83.49 - 95.71 |  |  | $83.49 - 95.71 | EMCOR 200 ton basement | 182 | 108 | 19712 | 15061 | 6500 | 40081 | 241 | 98 | 23511 | 15058.99 | 4500 | 4000 | [9 empty] | 35 | 2.9714
| 300 ton basement Labor and non-equipment costs | tons | Artificial bids | 0.74 |  |  | 52.9041 | 159.1166 | 6250 |  | 265.0258 | [8 empty] | EMCOR 300 ton basement | 212 | 108 | 22960 | 15161 | 7500 | 53313 | 232 | 98 | 22621 | 21995.95 | 5000 | 5000 | [9 empty] | 40 | 2.7
| 100 ton roof mount Labor and non-equipment costs | tons | Artificial bids | 1.33 |  |  | 95.0844 | 214.7769 | 3250 |  | 387.3266 | [8 empty] | EMCOR 100 ton roof | 132 | 108 | 14252 | 9300 | 3500 | 21766 | 134 | 98 | 13097 | 9489.38 | 3000 | 2400 | [9 empty] | 45 | 2.4222
| 200 ton roof mount Labor and non-equipment costs | tons | Artificial bids | 0.855 |  |  | 61.1257 | 183.0231 | 4000 |  | 305.1859 | [8 empty] | EMCOR 200 ton roof | 172 | 108 | 18592 | 15561 | 4500 | 39300 | 170 | 98 | 16605 | 14748.24 | 3500 | 3600 | [9 empty] | 50 | 2.26
| 300 ton roof mount Labor and non-equipment costs | tons | Artificial bids | 0.67333 |  |  | 48.1379 | 157.4424 | 4750 |  | 256.9754 | [8 empty] | EMCOR 300 ton roof | 204 | 108 | 22064 | 15161 | 5500 | 52450 | 200 | 98 | 19498 | 21854.41 | 4000 | 5000
[20 empty] | 80 ton screw | [19 empty] | 223 | 53.94
[20 empty] | 100 ton screw | [19 empty] | 230 | 53.94
[20 empty] | 150 ton screw | [19 empty] | 240 | 53.94
[20 empty] | 200 ton screw | [19 empty] | 251 | 53.94
[20 empty] | 250 ton screw | [19 empty] | 260 | 53.94
[20 empty] | 300 ton screw | [19 empty] | 266 | 53.94
[20 empty] | 350 ton screw | [19 empty] | 275 | 53.94
[20 empty] | 2 ton scroll | [19 empty] | 28.07 | 50.98
[20 empty] | 5 ton scroll | [19 empty] | 28.07 | 50.98
[20 empty] | 6 ton scroll | [19 empty] | 38.005 | 50.98 | 80 | 2.7875 | average | 1.5221
[20 empty] | 8 ton scroll | [19 empty] | 52.117 | 50.98 | 100 | 2.3 | std dev | 0.75963
[20 empty] | 10 ton scroll | [19 empty] | 67.039 | 52.87 | 150 | 1.6
[20 empty] | 15 ton scroll | [19 empty] | 72.727 | 52.87 | 200 | 1.255
[20 empty] | 20 ton scroll | [19 empty] | 83.99 | 53.94 | 250 | 1.04
[20 empty] | 30 ton scroll | [19 empty] | 96.096 | 53.94 | 300 | 0.88667
[20 empty] | 400 ton centrifugal | [19 empty] | 283 | 53.94 | 350 | 0.78571
[20 empty] | 600 ton centrifugal | [19 empty] | 310 | 53.94 | 2 | 14.035 | average | 6.4316
[20 empty] | 800 ton centrifugal | [19 empty] | 340 | 53.94 | 5 | 5.614 | std dev | 3.3054
[20 empty] | 1000 ton centrifugal | [19 empty] | 372 | 53.94 | 6 | 6.3342
[20 empty] | 1200 ton centrifugal | [19 empty] | 395 | 53.94 | 8 | 6.5146
[20 empty] | 1400 ton centrifugal | [19 empty] | 421 | 53.94 | 10 | 6.7039
[20 empty] | 1600 ton centrifugal | [19 empty] | 438 | 53.94 | 15 | 4.8485
[20 empty] | 1800 ton centrifugal | [19 empty] | 457 | 53.94 | 20 | 4.1995
[20 empty] | 2000 ton centrifugal | [19 empty] | 492 | 53.94 | 30 | 3.2032
[20 empty] | 2500 ton centrifugal | [19 empty] | 524 | 53.94 | 400 | 0.7075 | average | 0.36343
[42 empty] | 600 | 0.51667 | std dev | 0.15214
Water-Cooled Centrifugal VSD Chillers (>= 300 tons) | 300 ton ground Labor and non-equipment costs | tons | Artificial bids | 0.605 |  | 71.2963 | 43.1342 | 155.0163 | 2750 | 25% | 247.6881 | RSMeans 400 - 2500 centrifugal | H = 0.1177x + 246.68 | 0.36343 | 62.4649 | 22.7016 |  |  | 22.7016 | EMCOR 300 ton ground level | 174 | 108 | 18872 | 15461 | 4000 | 51141 | 189 | 98 | 18439 | 21807.76 | 1500 | 4600 | [9 empty] | 800 | 0.425
| 300 ton basement Labor and non-equipment costs | tons | Artificial bids | 0.74 |  |  | 52.7592 | 159.1166 | 6250 |  | 264.8448 | DEER 2008 centrifugal |  | 1.23-1.41 | 67.88 | $83.49 - 95.71 |  |  | $83.49 - 95.71 | EMCOR 300 ton basement | 212 | 108 | 22960 | 15161 | 7500 | 53313 | 232 | 98 | 22621 | 21995.95 | 5000 | 5000 | [9 empty] | 1000 | 0.372
| 300 ton roof Labor and non-equipment costs | tons | Artificial bids | 0.67333 |  |  | 48.0061 | 157.4424 | 4750 |  | 256.8106 | [8 empty] | EMCOR 300 ton roof | 204 | 108 | 22064 | 15161 | 5500 | 52450 | 200 | 98 | 19498 | 21854.41 | 4000 | 5000 | [9 empty] | 1200 | 0.32917
[20 empty] | 400 ton centrifugal | [19 empty] | 283 | 53.94 | 1400 | 0.30071
[20 empty] | 600 ton centrifugal | [19 empty] | 310 | 53.94 | 1600 | 0.27375
[20 empty] | 800 ton centrifugal | [19 empty] | 340 | 53.94 | 1800 | 0.25389
[20 empty] | 1000 ton centrifugal | [19 empty] | 372 | 53.94 | 2000 | 0.246
[20 empty] | 1200 ton centrifugal | [19 empty] | 395 | 53.94 | 2500 | 0.2096
[20 empty] | 1400 ton centrifugal | [19 empty] | 421 | 53.94
[20 empty] | 1600 ton centrifugal | [19 empty] | 438 | 53.94
[20 empty] | 1800 ton centrifugal | [19 empty] | 457 | 53.94
[20 empty] | 2000 ton centrifugal | [19 empty] | 492 | 53.94
[20 empty] | 2500 ton centrifugal | [19 empty] | 524 | 53.94 | 400 | 0.7075 | average | 0.36343
[42 empty] | 600 | 0.51667 | std dev | 0.15214
Small Packaged HP (< 65,000 Btuh) | Labor and non-equipment costs | tons | Contractor survey | 6.2708 |  |  | 443.8267 | 11.7469 | 598.378 | 27.5% | 997.7389 | RSMeans | H = 3.4156e0.413(tons) | 4.0199 | 59.0371 | 237.3216 |  |  | 237.3216 | Crane rental | [16 empty] | 598.378 | 83.2621 | 37 |  |  | 800 | 0.425
| Micellanous costs | tons | Artificial bids |  |  | 70.7771 |  | 326.9667 | [11 empty] | Installation (5 ton) | [12 empty] | 15.4134 | 1.7538 | 36 | [6 empty] | 1000 | 0.372
[20 empty] | Removal | [12 empty] | 12.6446 | 2.2566 | 37 | [6 empty] | 1200 | 0.32917
[20 empty] | Disposal | [16 empty] | 58.7346 | 12.7201 | 33 |  |  | 1400 | 0.30071
[20 empty] | Testing/commissioning (5 ton) | [12 empty] | 3.2958 | 0.48883 | 36 | [6 empty] | 1600 | 0.27375
[20 empty] | 1.5 ton | [19 empty] | 6.4 | 50.98 | 1800 | 0.25389
[20 empty] | 2 ton | [19 empty] | 7.619 | 50.98 | 2000 | 0.246
[20 empty] | 2.5 ton | [19 empty] | 9.412 | 50.98 | 2500 | 0.2096
[20 empty] | 3 ton | [19 empty] | 12.308 | 50.98 | HP | hr/hp
[20 empty] | 3.5 ton | [19 empty] | 14.545 | 50.98
[20 empty] | 4 ton | [19 empty] | 17.778 | 50.98
[20 empty] | 5 ton | [19 empty] | 26.667 | 50.98
Large Packaged HP (65,000 - 240,000 Btuh) | 7.5 ton ground | tons | Artificial bids | 4.4667 |  | 70.9502 | 316.9107 | 321.4 |  | 27.5% | 813.8462 | RSMeans 20 tons or less | H = 2.4283(tons) + 8.4007 | #REF! | 59.5843 | #REF! |  |  | #REF! | 7.5 ton Ground level | 27 | 108 | 2912 | 810 | 500 | 2648 | 40 | 97 | 3896 | 846 | 600 | 517 | [9 empty] | tons | hr/ton
| 7.5 ton roof | tons | Artificial bids | 4.1333 |  | 70.6041 | 291.8301 | 332.5333 |  |  | 796.0634 | Artificial bid 7.5 ton ground | [5 empty] | 550 |  | 7.5 ton Roof | 26 | 108 | 2800 | 980 | 1500 | 2961 | 36 | 96 | 3447 | 438 | 1000 | 609 | [9 empty] | 1.5 | 4.2667 | average | 4.0199
| Crane Rental | tons | Contractor survey | [5 empty] | 598.378 |  |  | Artificial bid 7.5 ton roof | [5 empty] | 1250 |  | 7.5 ton | [19 empty] | 29.091 | 50.98 | 2 | 3.8095 | std dev | 0.2211
[20 empty] | 10 ton | [19 empty] | 32 | 50.98 | 2.5 | 3.7648
[20 empty] | 15 ton | [19 empty] | 40 | 50.98 | 3 | 4.1027
[20 empty] | 20 ton | [19 empty] | 60 | 52.87 | 3.5 | 4.1557
Residential Water Heating
Small Storage Gas WH (<= 75,000 BtuH and EF rated) | 30 - 100 gal Atmospheric gas storage WH labor hours and rates | unit | RSMeans | 4.8067 | H = 0.0315(gal) + 2.9443 | 64.6189 | 310.6016 |  |  | 21% | 375.8279 | DEER 2008 |  | 2.25 | 59 | 132.75 |  |  | 132.75 | 30 gal atmospheric gas storage | [19 empty] | 4 | 55.8
[12 empty] | DOE TSD |  | 4.75 | 48.38 | 229.805 |  |  | 229.805 | 40 gal atmospheric gas storage | [19 empty] | 4.21 | 55.8
[12 empty] | DOE TSD adder for 66 and 75 gal or attic install |  | 1 | 48.38 | 48.38 |  |  | 48.38 | 50 gal atmospheric gas storage | [19 empty] | 4.44 | 55.8
[20 empty] | 60 gal atmospheric gas storage | [19 empty] | 4.71 | 55.8
[20 empty] | 75 gal atmospheric gas storage | [19 empty] | 5.33 | 55.8
[20 empty] | 100 gal atmospheric gas storage | [19 empty] | 6.15 | 55.8
means markup
[42 empty] | 30 | [9 empty] | 1395.1 | 1693.14 | 1.2136
[42 empty] | 40 | [9 empty] | 1416.24 | 1728.36 | 1.2204
[42 empty] | 50 | [9 empty] | 1483.93 | 1808.38 | 1.2186
[42 empty] | 60 | [9 empty] | 1891.14 | 2263.6 | 1.1969
[42 empty] | 75 | [9 empty] | 2036.78 | 2472.45 | 1.2139
[42 empty] | 100 | [9 empty] | 2315.55 | 2782.92 | 1.2018
1.2109
[42 empty] | 30 | [9 empty] | 783.08 | 1001.91 | 1.2794
Tankless WH | Natural gas / propane 3.2 - 9.5 GPM | unit | RSMeans | 4.4138 | H = 0.1395(gpm) + 3.4545 | 64.6189 | 285.2117 |  |  | 26% | 359.3668 | DEER 2008 |  | 2.25 | 59 | 132.75 |  |  | 132.75 | Natural gas / propane 3.2 GPM | [19 empty] | 4 | 55.8 | 40 | [9 empty] | 1135.88 | 1393.91 | 1.2272
[12 empty] | DOE TSD | [6 empty] | 967 | Natural gas / propane 6.4 GPM | [19 empty] | 4.211 | 55.8 | 52 | [9 empty] | 1221.5 | 1502.74 | 1.2302
[20 empty] | Natural gas / propane 8.4 GPM | [19 empty] | 4.444 | 55.8 | 66 | [9 empty] | 1322.3 | 1614.74 | 1.2212
[20 empty] | Natural gas / propane 9.5 GPM | [19 empty] | 5 | 55.8 | 80 | [9 empty] | 1696.73 | 2032.38 | 1.1978
[42 empty] | 120 | [9 empty] | 1891.32 | 2279.62 | 1.2053
[52 empty] | 2523.52 | 3001.28 | 1.1893
1.2215
[42 empty] | 3.2 | [11 empty] | means markup
[42 empty] | 6.4 | [9 empty] | 779.1 | 1015.54 | 1.3035
Heat Pump Water Heaters | Labor and non-equipment costs | unit | DOE TSD | 4.25 |  | 47.063 | 200.0175 | 153.58 |  | 25% | 441.9969 | [8 empty] | DOE TSD for electric WH | 3.25 | 40.64 | [19 empty] | 8.4 | [9 empty] | 1102.64 | 1386.76 | 1.2577
| Labor and non-equipment costs for venting adder (if needed) | unit | DOE TSD | 3.7 |  |  | 174.1329 | 115 |  |  | 361.4161 | [8 empty] | DOE TSD adder for HPWH | 1 | 40.64 | [19 empty] | 9.5 | [9 empty] | 1271.13 | 1578.78 | 1.242
[20 empty] | DOE TSD adder for condensate pump |  |  |  | 153.58 | [27 empty] | 1488.12 | 1837.22 | 1.2346
[20 empty] | DOE TSD adder for venting system (if needed) | 3.7 | 40.64 |  | 115 | [29 empty] | 1.2594
Non-Residential Water Heating
Large Storage Gas WH (> 75,000 BtuH and TE rated) | 75 - 250 MBH, 73 - 245 GPH labor hours and rates | unit | RSMeans | 9.3478 | H = 0.0655(MBH) - 0.3869 | 64.6189 | 604.0432 |  |  | 15% | 694.6497 | DEER 2008 |  | 2.25 | 59 | 132.75 |  |  | 132.75 | 75 MBH, 73 GPH | [19 empty] | 5.714 | 55.8
| 260 - 725 MBH, 250 - 690 GPH labor hours and rates | unit | RSMeans | 22.381 | H = 0.0153(MBH) + 15.304 | 58.1686 | 1301.8715 |  |  |  | 1497.1522 | DOE TSD |  | 4.75 | 48.38 | 229.805 |  |  | 229.805 | 98 MBH, 95 GPH | [19 empty] | 5.714 | 55.8
[12 empty] | DOE TSD adder for 66 and 75 gal or attic install |  | 1 | 48.38 | 48.38 |  |  | 48.38 | 120 MBH, 110 GPH | [19 empty] | 6.667 | 55.8
[20 empty] | 120 MBH, 115 GPH | [19 empty] | 7.273 | 55.8
[20 empty] | 140 MBH, 130 GPH | [19 empty] | 8 | 55.8
[20 empty] | 155 MBH, 150 GPH | [19 empty] | 10 | 55.8
[20 empty] | 180 MBH, 170 GPH | [19 empty] | 11.429 | 55.8
[20 empty] | 200 MBH, 192 GPH | [19 empty] | 13.333 | 55.8
[20 empty] | 250 MBH, 245 GPH | [19 empty] | 16 | 55.8 | MBH | hours/mbh | [9 empty] | means markup
[20 empty] | 260 MBH, 250 GPH | [19 empty] | 20 | 50.23 | 75 | 0.076187 | [7 empty] | 4091.52 | 4737.28 | 1.1578
[20 empty] | 360 MBH, 360 GPH | [19 empty] | 20 | 50.23 | 98 | 0.058306 | [7 empty] | 6219.52 | 7061 | 1.1353
[20 empty] | 500 MBH, 480 GPH | [19 empty] | 22.857 | 50.23 | 120 | 0.055558 | [7 empty] | 6503.57 | 7426.16 | 1.1419
[20 empty] | 725 MBH, 690 GPH | [19 empty] | 26.667 | 50.23 | 120 | 0.060608 | [7 empty] | 7797.21 | 8858.21 | 1.1361
[42 empty] | 140 | 0.057143 | [7 empty] | 9771.65 | 11063.87 | 1.1322
[42 empty] | 155 | 0.064516 | [7 empty] | 9722.16 | 11083.24 | 1.14
Lighting - Controls | [45 empty] | 878.02 | 1058.48 | 1.2055
Occupancy Sensors | Wall mounted labor | sensor | Contractor survey | 1.1946 |  |  | 66.0557 |  |  | 26% | 89.9624 | RSMeans |  | 1.1723 | 58.2745 | 68.3172 |  |  | 68.3172 | Wall mounted / per sensor | [12 empty] | 1.1946 | 0.10734 | 83 | [11 empty] | #REF!
| Wall mounted disposal and taxes | sensor | Artificial bids |  |  |  |  | 5.3431 |  |  |  | DEER 2008 |  | 0.65 | 67.88 | 44.122 |  |  | 44.122 | Ceiling mounted /per sensor | [12 empty] | 1.5098 | 0.13257 | 84
| Ceiling mounted labor | sensor | Contractor survey | 1.5098 |  |  | 83.485 |  |  |  | 121.7199 | Artificial bids, wall mounted |  | 0.3615 | 67.88 | 24.5385 |  |  | 24.5385 | Fixture integrated / per sensor | [12 empty] | 1.1355 | 0.09453 | 79
| Ceiling mounted disposal and taxes | sensor | Artificial bids |  |  |  |  | 13.1181 |  |  |  | Artificial bids, cieling mounted |  | 0.85088 | 67.88 | 57.7578 |  |  | 57.7578 | Occupancy sensors, passive infrared ceiling mounted | [19 empty] | 1.143 | 52.4
| Fixture integrated labor | sensor | Contractor survey | 1.1355 |  |  | 62.7859 |  |  |  | 88.6633 | Artificial bids, fixture integrated |  | 0.52227 | 67.88 | 35.4514 |  |  | 35.4514 | Occupancy sensors, ultrasonic ceiling mounted | [19 empty] | 1.143 | 52.4
| Fixture integrated disposal and taxes | sensor | Artificial bids |  |  |  |  | 7.5818 | [11 empty] | Occupancy sensors, dual technology ceiling mounted | [19 empty] | 1.231 | 52.4
| Labor rate | sensor | Artificial bids |  |  | 55.2947 | [13 empty] | Occupancy sensors, automatic wall switches | [19 empty] | 0.333 | 52.4
[20 empty] | Artificial bid 1: Install 20 wall mounted occupancy sensors | 0.08 | 95.1515 | 31.4 |  | 2.15 | 2.82
[20 empty] | Artificial bid 2: Install 20 wall mounted occupancy sensors | 0.4125 | 75 | 30.9375 |  |  | 2.8286
[20 empty] | Artificial bid 3: Install 20 wall mounted occupancy sensors | 0.5 | 60 | 30 |  | 1 | 3.536 | [20 empty] | means markup
[20 empty] | Artificial bid 4: Install 20 wall mounted occupancy sensors | 0.4 | 95 | 38 | 1.25 | 1.25 | 0 | [18 empty] | 223.74 | 285.65 | 1.2767
[20 empty] | Artificial bid 5: Install 20 wall mounted occupancy sensors | 0.41499 | 81.2879 | 33.7335 |  | 2.1 | 3.1558 | [18 empty] | 237.15 | 299.05 | 1.261
[20 empty] | Artificial bid 1: Install 20 ceiling mounted occupancy sensors | 1 | 98.5 | 98.5 |  |  | 13.15 | [18 empty] | 305.98 | 378.7 | 1.2377
[20 empty] | Artificial bid 2: Install 20 ceiling mounted occupancy sensors | 1.33 | 79 | 105.07 |  |  | 12.7287 | [20 empty] | 1.2585
[20 empty] | Artificial bid 3: Install 20 ceiling mounted occupancy sensors | 0.5 | 77.5 | 38.75 |  |  | 6.718
[20 empty] | Artificial bid 4: Install 20 ceiling mounted occupancy sensors | 0.41667 | 60 | 25 |  |  | 13.18
[20 empty] | Artificial bid 5: Install 20 ceiling mounted occupancy sensors | 0.33333 | 60 | 20 |  |  | 3.19
[20 empty] | Artificial bid 6: Install 20 ceiling mounted occupancy sensors | 1 | 95 | 95 | 1.25 | 1.75 | 0
[20 empty] | Artificial bid 7: Install 20 ceiling mounted occupancy sensors | 1.3762 | 78.3333 | 107.8 |  | 5.25 | 9.61
[20 empty] | Artificial bid 1: Install 50 fixture integrated occupancy sensors | 0.5 | 93.6 | 46.8 |  |  | 6.72
[20 empty] | Artificial bid 2: Install 50 fixture integrated occupancy sensors | 0.75 | 79 | 59.25 |  |  | 7.2443
[20 empty] | Artificial bid 3: Install 50 fixture integrated occupancy sensors | 0.415 | 75 | 31.125 |  |  | 3.4714
[20 empty] | Artificial bid 4: Install 50 fixture integrated occupancy sensors | 0.5 | 60 | 30 |  |  | 8.08
[20 empty] | Artificial bid 5: Install 50 fixture integrated occupancy sensors | 0.24 | 95 | 22.8 | 0.5 | 0.7 | 0
[20 empty] | Artificial bid 6: Install 50 fixture integrated occupancy sensors | 0.7286 | 80.52 | 58.6666 | 1.8 | 2.1 | 4.675
Note on AO2: Lucas Scheidler: Labor hours and rates are from Q4 2013 RSMeans
Note on G3: Lucas Scheidler: Bare Labor - CA statewide
Note on P3: Lucas Scheidler: Bare Labor
Note on K5: Lucas Scheidler: RSMeasns average
Note on U5: Lucas Scheidler: RSMeans item 235416.13
Note on AP5: Lucas Scheidler: National Average - crew Q-9
Note on E17: Lucas Scheidler: Based on 5 ton unit
Note on I17: Lucas Scheidler: disposal - based on a 5 ton unit
Note on J17: Lucas Scheidler: Crane rental - based on 5 ton unit
Note on O17: Lucas Scheidler: Based on 3 ton unit
Note on W17: Lucas Scheidler: EMCOR - does not include markup
Note on X17: Lucas Scheidler: EMCOR - does not include markup
Note on Y17: Lucas Scheidler: Misc - includes tubing/wiring, misc elec, mis sheet metal - does not include markup
Note on Z17: Lucas Scheidler: EMCOR - includes sign crane / set condenser - does not include markup
Note on AA17: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC17: Lucas Scheidler: EMCOR - does not include markup
Note on AD17: Lucas Scheidler: EMCOR - does not include markup
Note on AE17: Lucas Scheidler: Misc - includes tubing/wiring, misc elec, mis sheet metal - does not include markup
Note on AF17: Lucas Scheidler: EMCOR - includes sign crane / set condenser - does not include markup
Note on AG17: Lucas Scheidler: EMCOR - project mgmt, warranty - Does not include markup
Note on K18: Lucas Scheidler: average markup of bids
Note on O18: Lucas Scheidler: Based on 3 ton unit
Note on U18: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how much does it cost to rent a crane to remove an old outdoor unit and install a new unit? Please exclude any costs related to required permits.
Note on I19: Lucas Scheidler: based on a 3 ton unit
Note on O19: Lucas Scheidler: based on a 3 ton unit
Note on U19: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to install a new 5 ton unit? Please include the time required for preparing the curb and installing new curb gaskets, moving the unit into place with the crane, attaching refrigerant piping, connecting electrical and gas as necessary, and connecting ductwork. Assume no new curb is required and no new screen is required to conceal the unit.
Note on U20: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to remove an old unit, assuming a crane is used for the removal? Please include time associated with pulling refrigerant out, disconnecting electrical and controls, disconnecting the unit from the curb, removal of the unit by crane, and taking the unit to the recycler.
Note on U21: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, what is the disposal fee for the old unit?
Note on U22: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to perform testing/commissioning on a newly installed 5 ton unit to ensure it is running properly? Please include time required for checking belt alignment, starting compressors and making sure pressure is correct, checking combustion efficiency (in the case of gas units), checking for air leaks in the ductwork, making sure amperage is in the acceptable range, and balancing air flow.
Note on U23: Lucas Scheidler: RSMeans item 238143
Note on AP23: Lucas Scheidler: National Average - crew Q-5
Note on U30: Lucas Scheidler: Rsmean item 238219.2
Note on AP30: Lucas Scheidler: National Average - crew Q-6
Note on V35: Lucas Scheidler: implied hours based on DOE TSD installed cost and artificial bid hourly rate
Note on W35: Lucas Scheidler: average from artificial bids
Note on X35: Lucas Scheidler: DOE TSD base cost national average cost of $561 times the CA state multiplier 1.297
Note on E37: Lucas Scheidler: Based on 5 ton unit
Note on I37: Lucas Scheidler: disposal - based on a 5 ton unit
Note on J37: Lucas Scheidler: Crane rental - based on 5 ton unit
Note on O37: Lucas Scheidler: Based on 3 ton unit
Note on W37: Lucas Scheidler: EMCOR - does not include markup
Note on X37: Lucas Scheidler: EMCOR - does not include markup
Note on Y37: Lucas Scheidler: Misc - includes tubing/wiring, misc elec, mis sheet metal - does not include markup
Note on Z37: Lucas Scheidler: EMCOR - includes sign crane / set condenser - does not include markup
Note on AA37: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC37: Lucas Scheidler: EMCOR - does not include markup
Note on AD37: Lucas Scheidler: EMCOR - does not include markup
Note on AE37: Lucas Scheidler: Misc - includes tubing/wiring, misc elec, mis sheet metal - does not include markup
Note on AF37: Lucas Scheidler: EMCOR - includes sign crane / set condenser - does not include markup
Note on AG37: Lucas Scheidler: EMCOR - project mgmt, warranty - Does not include markup
Note on K38: Lucas Scheidler: average markup of bids
Note on O38: Lucas Scheidler: Based on 3 ton unit
Note on U38: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how much does it cost to rent a crane to remove an old outdoor unit and install a new unit? Please exclude any costs related to required permits.
Note on I39: Lucas Scheidler: based on a 3 ton unit
Note on O39: Lucas Scheidler: based on a 3 ton unit
Note on U39: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to install a new 5 ton unit? Please include the time required for preparing the curb and installing new curb gaskets, moving the unit into place with the crane, attaching refrigerant piping, connecting electrical and gas as necessary, and connecting ductwork. Assume no new curb is required and no new screen is required to conceal the unit.
Note on U40: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to remove an old unit, assuming a crane is used for the removal? Please include time associated with pulling refrigerant out, disconnecting electrical and controls, disconnecting the unit from the curb, removal of the unit by crane, and taking the unit to the recycler.
Note on U41: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, what is the disposal fee for the old unit?
Note on U42: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to perform testing/commissioning on a newly installed 5 ton unit to ensure it is running properly? Please include time required for checking belt alignment, starting compressors and making sure pressure is correct, checking combustion efficiency (in the case of gas units), checking for air leaks in the ductwork, making sure amperage is in the acceptable range, and balancing air flow.
Note on U43: Lucas Scheidler: RSMeans item 238126
Note on AP43: Lucas Scheidler: National Average - crew Q-5
Note on U48: Lucas Scheidler: RSMeans item 238219.1
Note on V55: Lucas Scheidler: implied hours based on DOE TSD installed cost and artificial bid hourly rate
Note on W55: Lucas Scheidler: average from artificial bids
Note on X55: Lucas Scheidler: DOE TSD base cost national average cost of $511 times the CA state multiplier 1.297
Note on K57: Lucas Scheidler: RSMeans average
Note on U57: Lucas Scheidler: RSMeans item 233414
Note on AP57: Lucas Scheidler: National Average crew Q-20
Note on U66: Lucas Scheidler: NREL, Jan, 2014. Evaluation of Retrofit Variable-Speed Furnace Fan Motors. http://www.nrel.gov/docs/fy14osti/60760.pdf
Note on V66: Lucas Scheidler: Simple Average of 8 data points for retrofits of PSM motors with Concept 3 motors
Note on K72: Lucas Scheidler: average RSMeans
Note on M72: Lucas Scheidler: workpapers refer to DEER 2011, which refers to Means and gives the same values at left
Note on U72: Lucas Scheidler: RSMeans item 2629231001
Note on AP72: Lucas Scheidler: National Average - 1 electrician
Note on AP77: Lucas Scheidler: National Average crew R-3
Note on K83: Lucas Scheidler: RSMeans average
Note on M83: Lucas Scheidler: workpapers refer to DEER 2011, which refers to Means and gives the same values at left
Note on U83: Lucas Scheidler: RSMeans item 2629231001
Note on AP83: Lucas Scheidler: National Average - 1 electrician
Note on E93: Lucas Scheidler: Based on 5 ton unit
Note on I93: Lucas Scheidler: disposal - based on a 5 ton unit
Note on J93: Lucas Scheidler: Crane rental - based on 5 ton unit
Note on K93: Lucas Scheidler: artificial bids average
Note on O93: Lucas Scheidler: based on a 5 ton unit
Note on U93: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how much does it cost to rent a crane to remove an old outdoor unit and install a new unit? Please exclude any costs related to required permits.
Note on G94: Lucas Scheidler: There was no artificial bids for small package units so the labor rate for large packaged DX is used.
Note on U94: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to install a new 5 ton unit? Please include the time required for preparing the curb and installing new curb gaskets, moving the unit into place with the crane, attaching refrigerant piping, connecting electrical and gas as necessary, and connecting ductwork. Assume no new curb is required and no new screen is required to conceal the unit.
Note on I95: Lucas Scheidler: No artificial bids to draw miscellaneous costs from for small packaged units. Given the similarity in miscellaneous costs per ton for 20 to 70 ton units, the average miscellaneous costs per ton from the large package units was used here.
Note on U95: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to remove an old unit, assuming a crane is used for the removal? Please include time associated with pulling refrigerant out, disconnecting electrical and controls, disconnecting the unit from the curb, removal of the unit by crane, and taking the unit to the recycler.
Note on U96: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, what is the disposal fee for the old unit?
Note on U97: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to perform testing/commissioning on a newly installed 5 ton unit to ensure it is running properly? Please include time required for checking belt alignment, starting compressors and making sure pressure is correct, checking combustion efficiency (in the case of gas units), checking for air leaks in the ductwork, making sure amperage is in the acceptable range, and balancing air flow.
Note on U98: Lucas Scheidler: RSMeans item 236213. Item number 2374 provides additional estimates for units with heating option and multi-zone + curb
Note on AP98: Lucas Scheidler: National Average - crew Q-5
Note on E106: Lucas Scheidler: Based on 40 ton unit
Note on I106: Lucas Scheidler: disposal - based on a 40 ton unit
Note on J106: Lucas Scheidler: Crane rental - based on 5 ton unit
Note on K106: Lucas Scheidler: Average artificial bids
Note on O106: Lucas Scheidler: average hours/ton for 7.5 to 15 ton unit
Note on W106: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X106: Lucas Scheidler: Does not include markup
Note on Y106: Lucas Scheidler: EMCOR -misc electrical and plumbing, misc sheet metal - Does not include markup or tax
Note on Z106: Lucas Scheidler: EMCOR - Crane - Does not include markup
Note on AA106: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC106: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD106: Lucas Scheidler: Does not include markup
Note on AE106: Lucas Scheidler: EMCOR - small tools / etc- Does not include markup or tax
Note on AF106: Lucas Scheidler: EMCOR - Rigging/crane, - Does not include markup
Note on AG106: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt,warranty - Does not include markup
Note on O107: Lucas Scheidler: average hours/ton for 20 to 100 ton unit
Note on W107: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X107: Lucas Scheidler: Does not include markup
Note on Y107: Lucas Scheidler: EMCOR -misc electrical and plumbing, misc sheet metal - Does not include markup or tax
Note on Z107: Lucas Scheidler: EMCOR - Crane - Does not include markup
Note on AA107: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC107: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD107: Lucas Scheidler: Does not include markup
Note on AE107: Lucas Scheidler: EMCOR - small tools / etc- Does not include markup or tax
Note on AF107: Lucas Scheidler: EMCOR - Rigging/crane, - Does not include markup
Note on AG107: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt,warranty - Does not include markup
Note on I108: Lucas Scheidler: average miscellaneous costs per ton for 20 to 70 ton units
Note on R108: Lucas Scheidler: Based on 20 ton unit
Note on W108: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X108: Lucas Scheidler: Does not include markup
Note on Y108: Lucas Scheidler: EMCOR -misc electrical and plumbing, curb/adaptor - Does not include markup or tax
Note on Z108: Lucas Scheidler: EMCOR - Crane - Does not include markup
Note on AA108: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC108: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD108: Lucas Scheidler: Does not include markup
Note on AE108: Lucas Scheidler: EMCOR - small tools / etc, curb/adapter- Does not include markup or tax
Note on AF108: Lucas Scheidler: EMCOR - Rigging/crane, - Does not include markup
Note on AG108: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt,warranty - Does not include markup
Note on R109: Lucas Scheidler: Based on 20 ton unit
Note on W109: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X109: Lucas Scheidler: Does not include markup
Note on Y109: Lucas Scheidler: EMCOR -misc electrical and plumbing, curb/adaptor - Does not include markup or tax
Note on Z109: Lucas Scheidler: EMCOR - Crane - Does not include markup
Note on AA109: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC109: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD109: Lucas Scheidler: Does not include markup
Note on AE109: Lucas Scheidler: EMCOR - small tools / etc, curb/adapter- Does not include markup or tax
Note on AF109: Lucas Scheidler: EMCOR - Rigging/crane, - Does not include markup
Note on AG109: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt,warranty - Does not include markup
Note on R110: Lucas Scheidler: Based on 70 ton unit
Note on U110: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how much does it cost to rent a crane to remove an old outdoor unit and install a new unit? Please exclude any costs related to required permits.
Note on U111: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to install a new 40 ton unit? Please include the time required for preparing the curb and installing new curb gaskets, moving the unit into place with the crane, attaching refrigerant piping, connecting electrical and gas as necessary, and connecting ductwork. Assume no new curb is required and no new screen is required to conceal the unit.
Note on U112: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to remove an old unit, assuming a crane is used for the removal? Please include time associated with pulling refrigerant out, disconnecting electrical and controls, disconnecting the unit from the curb, removal of the unit by crane, and taking the unit to the recycler.
Note on U113: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, what is the disposal fee for the old unit?
Note on U114: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to perform testing/commissioning on a newly installed 40 ton unit to ensure it is running properly? Please include time required for checking belt alignment, starting compressors and making sure pressure is correct, checking combustion efficiency (in the case of gas units), checking for air leaks in the ductwork, making sure amperage is in the acceptable range, and balancing air flow.
Note on U115: Lucas Scheidler: RSMeans item 236213. Item number 2374 provides additional estimates for units with heating option and multi-zone + curb
Note on AP115: Lucas Scheidler: National Average - crew Q-5
Note on AP118: Lucas Scheidler: National Average - crew Q-6
Note on K127: Lucas Scheidler: average artificial bids
Note on O127: Lucas Scheidler: Average hours/ton for 130 to 320 ton screw
Note on W127: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X127: Lucas Scheidler: Does not include markup
Note on Y127: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z127: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA127: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC127: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD127: Lucas Scheidler: Does not include markup
Note on AE127: Lucas Scheidler: EMCOR - piping and electrical, small tools, consumables, insulation, chemical treatment - Does not include markup or tax
Note on AF127: Lucas Scheidler: EMCOR - Rigging/crane, - Does not include markup
Note on AG127: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt,warranty - Does not include markup
Note on O128: Lucas Scheidler: Average hours/ton for 10 to 50 ton scroll
Note on W128: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X128: Lucas Scheidler: Does not include markup
Note on Y128: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z128: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA128: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC128: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD128: Lucas Scheidler: Does not include markup
Note on AE128: Lucas Scheidler: EMCOR - piping and electrical, small tools, consumables, insulation, chemical treatment - Does not include markup or tax
Note on AF128: Lucas Scheidler: EMCOR - Rigging/crane, - Does not include markup
Note on AG128: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt,warranty - Does not include markup
Note on W129: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X129: Lucas Scheidler: Does not include markup
Note on Y129: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z129: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA129: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC129: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD129: Lucas Scheidler: Does not include markup
Note on AE129: Lucas Scheidler: EMCOR - piping and electrical, small tools, consumables, insulation, chemical treatment - Does not include markup or tax
Note on AF129: Lucas Scheidler: EMCOR - Rigging/crane, - Does not include markup
Note on AG129: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt,warranty - Does not include markup
Note on W130: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X130: Lucas Scheidler: Does not include markup
Note on Y130: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z130: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA130: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC130: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD130: Lucas Scheidler: Does not include markup
Note on AE130: Lucas Scheidler: EMCOR - piping and electrical, small tools, consumables, insulation, chemical treatment - Does not include markup or tax
Note on AF130: Lucas Scheidler: EMCOR - Rigging/crane, - Does not include markup
Note on AG130: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt,warranty - Does not include markup
Note on W131: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X131: Lucas Scheidler: Does not include markup
Note on Y131: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z131: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA131: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC131: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD131: Lucas Scheidler: Does not include markup
Note on AE131: Lucas Scheidler: EMCOR - piping and electrical, small tools, consumables, insulation, chemical treatment - Does not include markup or tax
Note on AF131: Lucas Scheidler: EMCOR - Rigging/crane, - Does not include markup
Note on AG131: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt,warranty - Does not include markup
Note on W132: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X132: Lucas Scheidler: Does not include markup
Note on Y132: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z132: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA132: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC132: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD132: Lucas Scheidler: Does not include markup
Note on AE132: Lucas Scheidler: EMCOR - piping and electrical, small tools, consumables, insulation, chemical treatment - Does not include markup or tax
Note on AF132: Lucas Scheidler: EMCOR - Rigging/crane, - Does not include markup
Note on AG132: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt,warranty - Does not include markup
Note on AP133: Lucas Scheidler: National average crew Q-7
Note on K149: Lucas Scheidler: average artificial bids
Note on O149: Lucas Scheidler: average hours/ton for 80 - 350 ton screw
Note on W149: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X149: Lucas Scheidler: Does not include markup
Note on Y149: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z149: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA149: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC149: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD149: Lucas Scheidler: Does not include markup
Note on AE149: Lucas Scheidler: EMCOR - field material, small tools, consumables, insulation, and water treatment Does not include markup or tax
Note on AF149: Lucas Scheidler: EMCOR - Crane rental- Does not include markup
Note on AG149: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on O150: Lucas Scheidler: average hours/ton for 2 - 30 ton scroll
Note on W150: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X150: Lucas Scheidler: Does not include markup
Note on Y150: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z150: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA150: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC150: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD150: Lucas Scheidler: Does not include markup
Note on AE150: Lucas Scheidler: EMCOR - field material, small tools, consumables, insulation, and water treatment Does not include markup or tax
Note on AF150: Lucas Scheidler: EMCOR - Crane rental- Does not include markup
Note on AG150: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on O151: Lucas Scheidler: average hours/ton for 400 - 2500 ton centrifugal
Note on W151: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X151: Lucas Scheidler: Does not include markup
Note on Y151: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z151: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA151: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC151: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD151: Lucas Scheidler: Does not include markup
Note on AE151: Lucas Scheidler: EMCOR - field material, small tools, consumables, insulation, and water treatment Does not include markup or tax
Note on AF151: Lucas Scheidler: EMCOR - Crane rental- Does not include markup
Note on AG151: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on W152: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X152: Lucas Scheidler: Does not include markup
Note on Y152: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z152: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA152: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC152: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD152: Lucas Scheidler: Does not include markup
Note on AE152: Lucas Scheidler: EMCOR - field material, small tools, consumables, insulation, and water treatment Does not include markup or tax
Note on AF152: Lucas Scheidler: EMCOR - Crane rental- Does not include markup
Note on AG152: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on W153: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X153: Lucas Scheidler: Does not include markup
Note on Y153: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z153: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA153: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC153: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD153: Lucas Scheidler: Does not include markup
Note on AE153: Lucas Scheidler: EMCOR - field material, small tools, consumables, insulation, and water treatment Does not include markup or tax
Note on AF153: Lucas Scheidler: EMCOR - Crane rental- Does not include markup
Note on AG153: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on W154: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X154: Lucas Scheidler: Does not include markup
Note on Y154: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z154: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA154: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC154: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD154: Lucas Scheidler: Does not include markup
Note on AE154: Lucas Scheidler: EMCOR - field material, small tools, consumables, insulation, and water treatment Does not include markup or tax
Note on AF154: Lucas Scheidler: EMCOR - Crane rental- Does not include markup
Note on AG154: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on W155: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X155: Lucas Scheidler: Does not include markup
Note on Y155: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z155: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA155: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC155: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD155: Lucas Scheidler: Does not include markup
Note on AE155: Lucas Scheidler: EMCOR - field material, small tools, consumables, insulation, and water treatment Does not include markup or tax
Note on AF155: Lucas Scheidler: EMCOR - Crane rental- Does not include markup
Note on AG155: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on W156: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X156: Lucas Scheidler: Does not include markup
Note on Y156: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z156: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA156: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC156: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD156: Lucas Scheidler: Does not include markup
Note on AE156: Lucas Scheidler: EMCOR - field material, small tools, consumables, insulation, and water treatment Does not include markup or tax
Note on AF156: Lucas Scheidler: EMCOR - Crane rental- Does not include markup
Note on AG156: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on W157: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X157: Lucas Scheidler: Does not include markup
Note on Y157: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z157: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA157: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC157: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD157: Lucas Scheidler: Does not include markup
Note on AE157: Lucas Scheidler: EMCOR - field material, small tools, consumables, insulation, and water treatment Does not include markup or tax
Note on AF157: Lucas Scheidler: EMCOR - Crane rental- Does not include markup
Note on AG157: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on U158: Lucas Scheidler: RSMeans iteam 236426
Note on AP158: Lucas Scheidler: National average crew Q-7
Note on U165: Lucas Scheidler: RSMeans iteam 236423
Note on AP165: Lucas Scheidler: National average crew Q-5
Note on AP169: Lucas Scheidler: National average crew Q-6
Note on AP171: Lucas Scheidler: National average crew Q-7
Note on U173: Lucas Scheidler: RSMeans item 236416
Note on A184: Lucas Scheidler: Workpapers indicate there are no centrifugal VSD chillers < 150 tons in the market. Our research confirms this. Additionally, our subcontractors found very few (4) units less than 300 tons. Given the small sample size, a regression model could only be developed for units >= 300 tons.
Note on K184: Lucas Scheidler: average artificial bids
Note on O184: Lucas Scheidler: average hours/ton for 400 - 2500 ton centrifugal
Note on W184: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X184: Lucas Scheidler: Does not include markup
Note on Y184: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z184: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA184: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC184: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD184: Lucas Scheidler: Does not include markup
Note on AE184: Lucas Scheidler: EMCOR - field material, small tools, consumables, insulation, and water treatment Does not include markup or tax
Note on AF184: Lucas Scheidler: EMCOR - Crane rental- Does not include markup
Note on AG184: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on W185: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X185: Lucas Scheidler: Does not include markup
Note on Y185: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z185: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA185: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC185: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD185: Lucas Scheidler: Does not include markup
Note on AE185: Lucas Scheidler: EMCOR - field material, small tools, consumables, insulation, and water treatment Does not include markup or tax
Note on AF185: Lucas Scheidler: EMCOR - Crane rental- Does not include markup
Note on AG185: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on W186: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X186: Lucas Scheidler: Does not include markup
Note on Y186: Lucas Scheidler: EMCOR - piping and electrical and insulation - Does not include markup or tax
Note on Z186: Lucas Scheidler: EMCOR - Crane rental - Does not include markup
Note on AA186: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC186: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD186: Lucas Scheidler: Does not include markup
Note on AE186: Lucas Scheidler: EMCOR - field material, small tools, consumables, insulation, and water treatment Does not include markup or tax
Note on AF186: Lucas Scheidler: EMCOR - Crane rental- Does not include markup
Note on AG186: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on U187: Lucas Scheidler: RSMeans item 236416
Note on AP187: Lucas Scheidler: National average crew Q-7
Note on E198: Lucas Scheidler: Based on 5 ton unit
Note on I198: Lucas Scheidler: disposal - based on a 5 ton unit
Note on J198: Lucas Scheidler: Crane rental
Note on K198: Lucas Scheidler: average artificial bids
Note on O198: Lucas Scheidler: average hrs/ton for 1.5 to 5 ton units (from RS means for small packaged DX)
Note on U198: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how much does it cost to rent a crane to remove an old outdoor unit and install a new unit? Please exclude any costs related to required permits.
Note on I199: Lucas Scheidler: There were no artificial bids for small packaged HP. Miscellaneous costs per ton are assumed to be the same as for large package HP)
Note on U199: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to install a new 5 ton unit? Please include the time required for preparing the curb and installing new curb gaskets, moving the unit into place with the crane, attaching refrigerant piping, connecting electrical and gas as necessary, and connecting ductwork. Assume no new curb is required and no new screen is required to conceal the unit.
Note on U200: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to remove an old unit, assuming a crane is used for the removal? Please include time associated with pulling refrigerant out, disconnecting electrical and controls, disconnecting the unit from the curb, removal of the unit by crane, and taking the unit to the recycler.
Note on U201: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, what is the disposal fee for the old unit?
Note on U202: Lucas Scheidler: MCS HVAC contractor survey: The following questions apply to retrofitting a split DX or packaged DX system on a low rise, flat roof, commercial building. On average, how many man-hours does it take to perform testing/commissioning on a newly installed 5 ton unit to ensure it is running properly? Please include time required for checking belt alignment, starting compressors and making sure pressure is correct, checking combustion efficiency (in the case of gas units), checking for air leaks in the ductwork, making sure amperage is in the acceptable range, and balancing air flow.
Note on U203: Lucas Scheidler: RSMeans item 236213. Item number 2374 provides additional estimates for units with heating option and multi-zone + curb - These are the small packaged DX entries from RS means - assume the labor hours for small packaged air source heat pumps are similar.
Note on AP203: Lucas Scheidler: National Average - crew Q-5
Note on K211: Lucas Scheidler: Average artificial bids
Note on O211: Lucas Scheidler: average hours/ton for 7.5 to 20 ton unit
Note on W211: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X211: Lucas Scheidler: Does not include markup
Note on Y211: Lucas Scheidler: EMCOR -misc electrical and plumbing, misc sheet metal - Does not include markup or tax
Note on Z211: Lucas Scheidler: EMCOR - Crane - Does not include markup
Note on AA211: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC211: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD211: Lucas Scheidler: Does not include markup
Note on AE211: Lucas Scheidler: EMCOR - small tools / etc- Does not include markup or tax
Note on AF211: Lucas Scheidler: EMCOR - Rigging/crane, - Does not include markup
Note on AG211: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt,warranty - Does not include markup
Note on S212: Lucas Scheidler: Crane rental - based on 7.5 ton unit
Note on W212: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on X212: Lucas Scheidler: Does not include markup
Note on Y212: Lucas Scheidler: EMCOR -misc electrical and plumbing, misc sheet metal, curb - Does not include markup or tax
Note on Z212: Lucas Scheidler: EMCOR - Crane - Does not include markup
Note on AA212: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt, permits, insurance, bond, contingency, warranty - Does not include markup
Note on AC212: Lucas Scheidler: Weighted average of all laborers. Does not include markup
Note on AD212: Lucas Scheidler: Does not include markup
Note on AE212: Lucas Scheidler: EMCOR - small tools / etc- Does not include markup or tax
Note on AF212: Lucas Scheidler: EMCOR - Rigging/crane, - Does not include markup
Note on AG212: Lucas Scheidler: EMCOR - Engineering/survey, project mgmt,warranty - Does not include markup
Note on J213: Lucas Scheidler: Crane rental -
Note on S213: Lucas Scheidler: Crane rental - based on 7.5 ton unit
Note on U213: Lucas Scheidler: RSMeans item 236213. Item number 2374 provides additional estimates for units with heating option and multi-zone + curb - These are for large package dx - assume package HP labor hours and rates are similar
Note on AP213: Lucas Scheidler: National Average - crew Q-5
Note on AP216: Lucas Scheidler: National Average - crew Q-6
Note on K218: Lucas Scheidler: average RSMeans
Note on U218: Lucas Scheidler: RSMeans item 223430
Note on AP218: Lucas Scheidler: National average 1 plumber
Note on K239: Lucas Scheidler: RSMeans average
Note on U239: Lucas Scheidler: RSMeans item 223413
Note on AP239: Lucas Scheidler: National average 1 plumber
Note on T240: Lucas Scheidler: Capacity not specified. Labor costs not broken out by hours or rate.
Note on K250: Lucas Scheidler: default
Note on K261: Lucas Scheidler: RSMeans average
Note on U261: Lucas Scheidler: RSMeans item 223436
Note on AP261: Lucas Scheidler: National average 1 plumber
Note on AP270: Lucas Scheidler: RSMeans National average crew Q-1
Note on K277: Lucas Scheidler: RSMeans average
Note on U277: Lucas Scheidler: MCS contractor survey question: On average, how long does it take to install wall-mounted occupancy sensors in terms of man-hours per sensor? Please include in the time required for: wiring, installation, programming, and commissioning.
Note on U278: Lucas Scheidler: MCS lighting contractor survey question: On average, how long does it take to install ceiling-mounted occupancy sensors in terms of man-hours per sensor? [IF NEEDED: Again, please include in the time required for: wiring, installation, programming, and commissioning.]
Note on U279: Lucas Scheidler: MCS lighting contractor survey question: On average, how long does it take to install fixture-integrated occupancy sensors inside existing fixtures in terms of man-hours per sensor. Please include the time required for: dismantling and re-assembling the fixture, in addition to wiring, installation, programming, and commissioning.
Note on U280: Lucas Scheidler: RSMeans item 260923
Note on AP280: Lucas Scheidler: National Average - 1 electrician
Note on U284: Lucas Scheidler: M4 Scope of Work (SOW): Install 20 Wall Mounted Occupancy Sensors Description: The building presently has manually operated wall switches in rest rooms and conference rooms. The building management has decided to install occupancy sensors in all the rest rooms and conference rooms. Please install Watt-Stopper DSW-100 dual Technology Wall Switch or equivalent. Only 1 sensor per room is required. Each room has between two and six fixtures. Tasks: The following tasks needs to be executed for installing the occupancy sensors Remove existing manually operated switches from rest rooms and conference rooms Provide and Install 20 new wall mounted occupancy sensors Program the sensor to turn on the lights on upon entry of a person into a room, and then turn the lights off from 5 minutes after the room is vacated. Commission the sensor and verify correct operation Dispose the existing manually operated switches Bid: Please provide the following separately with your bid. Specific products that will be used Cost of Materials Hours estimated for removal and installation Hours estimated for preparing items for disposal Total cost of labor Cost for extra equipment needed such as a lift. (Lift is not be required for this measure) Cost of disposal fees that may be required Taxes
Note on V284: Lucas Scheidler: per unit
Note on X284: Lucas Scheidler: per unit
Note on Z284: Lucas Scheidler: per unit disposal
Note on AA284: Lucas Scheidler: per unit taxes
Note on Y287: Lucas Scheidler: unspecified per unit cost
Note on U289: Lucas Scheidler: M5 Scope of Work (SOW): Install 20 Ceiling Mounted Occupancy Sensors Description: The building conference rooms presently do not have occupancy/motion sensors. The ceiling is 9 ft tall and is a dropped ceiling type. Building management has decided install the ceiling mounted occupancy sensors. Please install Watt Stopper CI-205 Passive Infrared Ceiling Sensor and Watt Stopper BZ-50 Universal Voltage Power Pack or equivalent occupancy sensors as a lighting control strategy. The sensors shall be installed on the dropped ceiling. Only one sensor per room will be required. Each room has between two and six fixtures. Tasks: The following tasks needs to be executed for installing the occupancy sensors Identify correct locations for installing the sensors for maximum effectiveness Provide and install 20 new ceiling mounted occupancy sensors. Provide and install 20 new power packs for the sensors. Provide and install all necessary electrical connections. Program the sensor to turn on the lights on upon entry of a person into a room, and then turn the lights off 5 minutes after the room is vacated. Commission the sensors and verify correct operation Bid: Please provide the following separately with your bid. Specific products that will be used Cost of Materials Hours estimated for removal and installation Hours estimated for preparing items for disposal Total cost of labor Cost for extra equipment needed such as a lift. (Ladders are adequate for access) Cost of disposal fees that may be required Taxes
Note on V289: Lucas Scheidler: per unit
Note on X289: Lucas Scheidler: per unit
Note on Y294: Lucas Scheidler: unspecified per unit cost
Note on Z294: Lucas Scheidler: disposal - per unit
Note on U296: Lucas Scheidler: M6 Scope of Work (SOW): Install occupancy sensors on 50 existing electronic ballast lighting fixtures Description: The project site presently has 50, 4ft 2-lamps T8 lighting fixtures with electronic ballasts. These fixtures shall be retrofit with new Watt Stopper FS-155 or equivalent occupancy sensor to turn the individual fixtures off when occupants are not present. The recessed lighting fixtures are mounted on dropped ceilings which are at a height of 9 ft from the floor. The lighting fixtures are distributed across 3 floors of the building. Tasks: The following tasks needs to be executed for this project Remove necessary parts to access mounting location Install Watt Stopper FS-155 Sensor or equivalent on each fixture Provide and install all electrical connections Program the sensor to turn on the lights on upon entry of a person into a room, and then turn the lights off from 5 minutes after the space is vacated. Commission and verify correct operation of all the fixtures. Bid: Please provide the following separately with your bid. Specific products that will be used Cost of Materials Hours estimated for removal and installation Hours estimated for preparing items for disposal Total cost of labor Cost for extra equipment needed such as a lift. (Ladders are adequate for access) Cost of disposal fees that may be required Taxes
Note on V296: Lucas Scheidler: per unit
Note on X296: Lucas Scheidler: per unit
Note on Y300: Lucas Scheidler: per unit - unspecified
Note on Z300: Lucas Scheidler: disposal - per unit